## bhp_uht_inspection
fulcrum_id | created_at | updated_at | created_by | updated_by | system_created_at | system_updated_at | version | status | project | assigned_to | latitude | longitude | geometry | segment_name
8b7848f5-ea70-441e-9cab-b4cf7767517e | 2025-05-27 20:13:19 AEST | 2025-07-31 01:57:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:19 AEST | 2025-09-05 13:43:03 AEST | 31 |  |  |  | -27.4529 | 153.0341 | POINT (153.0340718746927 -27.452870991508025) | Rings 1 - 30
17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 2025-05-27 20:13:20 AEST | 2025-07-31 03:17:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:20 AEST | 2025-09-05 13:43:05 AEST | 21 |  |  |  | -20.3181 | 118.5775 | POINT (118.57745923849077 -20.318057333763953) | Rings 31 - 60
dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 2025-05-27 20:13:20 AEST | 2025-07-31 05:43:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:20 AEST | 2025-09-05 13:43:06 AEST | 20 |  |  |  | -20.318 | 118.5775 | POINT (118.57746150360406 -20.317996019983244) | Rings 61 - 90
f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 2025-05-27 20:13:21 AEST | 2025-07-31 05:54:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:21 AEST | 2025-09-05 13:43:08 AEST | 26 |  |  |  | -20.3218 | 118.5856 | POINT (118.58564459032044 -20.321752911677223) | Rings 91 - 120
a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 2025-05-27 20:13:21 AEST | 2025-07-30 05:57:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:21 AEST | 2025-09-05 13:43:10 AEST | 14 |  |  |  | -20.318 | 118.5774 | POINT (118.5773903 -20.3179548) | Rings 121 - 150
53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 2025-05-27 20:13:22 AEST | 2025-07-31 03:39:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:22 AEST | 2025-09-05 13:43:12 AEST | 23 |  |  |  | -20.3216 | 118.5854 | POINT (118.5854271 -20.3216153) | Rings 151 - 180
6728cd27-078c-421a-b1f4-1acfc77f71f9 | 2025-05-27 20:13:22 AEST | 2025-07-30 02:46:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:22 AEST | 2025-09-05 13:43:13 AEST | 14 |  |  |  | -20.3215 | 118.5854 | POINT (118.58543260078937 -20.32151943230174) | Rings 181 - 210
53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 2025-05-27 20:13:23 AEST | 2025-07-28 06:09:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:23 AEST | 2025-09-05 13:43:15 AEST | 11 |  |  |  | -20.3179 | 118.5774 | POINT (118.5773702 -20.317909) | Rings 211 - 240
0a69fbad-efd1-4d3a-bd86-3e3525881922 | 2025-05-27 20:13:23 AEST | 2025-07-29 23:52:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:23 AEST | 2025-09-05 13:43:16 AEST | 11 |  |  |  | -20.3216 | 118.5853 | POINT (118.5852941 -20.3215889) | Rings 241 - 270
6e355a6c-8469-4ed4-a402-41fb8116b58c | 2025-05-27 20:13:23 AEST | 2025-07-29 23:00:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:23 AEST | 2025-09-05 13:43:18 AEST | 20 |  |  |  | -20.3218 | 118.5856 | POINT (118.5856387 -20.3218143) | Rings 271 - 300
3e5d5385-3a2f-4155-b5a3-772fc267e40f | 2025-05-27 20:13:24 AEST | 2025-07-29 22:59:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:24 AEST | 2025-09-05 13:43:20 AEST | 19 |  |  |  | -20.3217 | 118.5853 | POINT (118.58531728829445 -20.321721393386525) | Rings 301 - 330
11879e43-89b0-4462-b3ed-a822c8a2f994 | 2025-05-27 20:13:24 AEST | 2025-07-29 22:20:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:24 AEST | 2025-09-05 13:43:21 AEST | 22 |  |  |  | -20.3213 | 118.5849 | POINT (118.5849323 -20.3213463) | Rings 331 - 360
9c02e216-6c30-4006-b03f-dcfa367bcdac | 2025-05-27 20:13:25 AEST | 2025-07-29 22:16:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:25 AEST | 2025-09-05 13:43:23 AEST | 24 |  |  |  | -20.3217 | 118.5853 | POINT (118.58528112346737 -20.321663442898803) | Rings 361 - 390
a4ab9852-aae4-4525-a1e0-d027c91a211a | 2025-05-27 20:13:25 AEST | 2025-07-30 05:58:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:25 AEST | 2025-09-05 13:43:24 AEST | 24 |  |  |  | -20.3217 | 118.5854 | POINT (118.5853713 -20.3216525) | Rings 391 - 420
fb048eb7-416c-4027-acd6-08f65efde129 | 2025-05-27 20:13:26 AEST | 2025-07-28 23:53:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:26 AEST | 2025-09-05 13:43:26 AEST | 18 |  |  |  | -20.318 | 118.5773 | POINT (118.5773054169587 -20.318022306224574) | Rings 421 - 450
ee16eb52-4620-4d27-8038-a3c93bf88107 | 2025-05-27 20:13:26 AEST | 2025-07-29 15:23:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:26 AEST | 2025-09-05 13:43:28 AEST | 27 |  |  |  | -20.3216 | 118.5854 | POINT (118.5853743 -20.3216485) | Rings 451 - 480
09309c02-2c9e-4aea-9ab5-b39f583cd12b | 2025-05-27 20:13:27 AEST | 2025-07-31 04:51:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:27 AEST | 2025-09-05 13:43:29 AEST | 28 |  |  |  | -20.3216 | 118.5853 | POINT (118.585267 -20.3216388) | Rings 481 - 510
c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 2025-05-27 20:13:27 AEST | 2025-07-31 00:53:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:27 AEST | 2025-09-05 13:43:31 AEST | 17 | [6 empty] | Rings 511 - 540
3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 2025-05-27 20:13:28 AEST | 2025-07-30 11:27:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:28 AEST | 2025-09-05 13:43:32 AEST | 27 |  |  |  | -20.318 | 118.5773 | POINT (118.57733245416871 -20.317954293147753) | Rings 541 - 570
e5e55a2a-2e7b-480e-9988-a0a945287b37 | 2025-05-27 20:13:28 AEST | 2025-07-30 11:24:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:28 AEST | 2025-09-05 13:43:34 AEST | 24 |  |  |  | -20.3741 | 118.6348 | POINT (118.63480487016331 -20.374131722949524) | Rings 571 - 600
7e727b96-7206-4f43-982f-dc9a2b271ad6 | 2025-05-27 20:13:29 AEST | 2025-07-23 21:56:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:29 AEST | 2025-09-05 13:43:36 AEST | 21 |  |  |  | -20.3149 | 118.5659 | POINT (118.56587422712452 -20.31485430347205) | Rings 601 - 630
de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 2025-05-27 20:13:29 AEST | 2025-07-08 13:41:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:29 AEST | 2025-09-05 13:43:37 AEST | 24 |  |  |  | -20.3742 | 118.6347 | POINT (118.63473109190595 -20.374178832937584) | Rings 631 - 660
7ebe35c8-ed28-4786-ab73-7b881201e02a | 2025-05-27 20:13:30 AEST | 2025-07-31 05:48:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:30 AEST | 2025-09-05 13:43:39 AEST | 17 |  |  |  | -20.3159 | 118.5556 | POINT (118.55561065 -20.31585311) | Rings 661 - 690
f7d03050-0fd5-44cb-af31-a3a632990490 | 2025-05-27 20:13:30 AEST | 2025-06-02 00:21:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:30 AEST | 2025-09-05 13:43:40 AEST | 11 |  |  |  | -20.3738 | 118.6342 | POINT (118.6342477 -20.373784) | Rings 691 - 720
f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 2025-05-27 20:13:30 AEST | 2025-07-31 05:42:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:30 AEST | 2025-09-05 13:43:41 AEST | 14 |  |  |  | -20.3363 | 118.5502 | POINT (118.55023727904296 -20.336329766515888) | Rings 721 - 750
3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 2025-05-27 20:13:31 AEST | 2025-06-02 05:00:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:31 AEST | 2025-09-05 13:43:42 AEST | 15 |  |  |  | -20.31 | 118.559 | POINT (118.55903222154348 -20.309958815630363) | Rings 751 - 780
131c12f8-42fa-4fca-828a-09b38c961c69 | 2025-05-27 20:13:31 AEST | 2025-06-02 08:45:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:31 AEST | 2025-09-05 13:43:43 AEST | 14 |  |  |  | -20.3156 | 118.5668 | POINT (118.5668181577458 -20.3155651) | Rings 781 - 810
b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 2025-05-27 20:13:31 AEST | 2025-06-02 00:46:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:31 AEST | 2025-09-05 13:43:44 AEST | 10 |  |  |  | -20.3156 | 118.5668 | POINT (118.5668181577458 -20.3155651) | Rings 811 - 840
110a175f-a692-4ca9-89a8-2a7da948c4bd | 2025-05-27 20:13:32 AEST | 2025-06-02 00:59:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 2025-05-27 20:13:32 AEST | 2025-09-05 13:43:45 AEST | 13 |  |  |  | -20.3156 | 118.5669 | POINT (118.56687744864736 -20.315565904461025) | Rings 841 - 870
ece4ab2f-3734-4544-9353-cc4ed991e2fa | 2025-07-27 07:55:35 AEST | 2025-07-27 07:55:44 AEST | 30011704-user5@smec.com | james.stone@smec.com | 2025-07-27 07:57:03 AEST | 2025-09-05 13:43:45 AEST | 3 |  |  |  | -20.3214 | 118.5854 | POINT (118.5853767 -20.3213867)
af5cf9d7-2ea4-4457-9557-527081137d3a | 2025-09-16 19:14:54 AEST | 2025-09-16 19:14:54 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 2025-09-16 19:14:54 AEST | 2025-09-16 19:14:54 AEST | 1 | [6 empty] | Sample Defects

## defects
fulcrum_id | fulcrum_parent_id | fulcrum_record_id | version | latitude | longitude | geometry | created_at | updated_at | created_by | updated_by | ring_number | clock_position | component_old | component | component_other | bhp_defect_id | defect_version_details | inspection_id | equipment | area | inspection_standard | location | status | previous_assessment | defect_type | repair_verified_by_inspector | repair_verified_by_competent_supervisor | repair_verified_by_gts_engineer | damage_mechanism_old | damage_mechanism | damage_mechanism_other | condition | condition_other | current_condition_condition | business_impact_type_old | business_impact_type | business_impact_type_other | current_condition_type | type | type_other | consequence_old | consequence | consequence_other | likelihood_old | likelihood | likelihood_other | defect_location_description | component_final_failure_mode_old | component_final_failure_mode | component_final_failure_mode_other | detailed_description_old | detailed_description | detailed_description_other | effect_to_equipment_due_to_component_failure_old | effect_to_equipment_due_to_component_failure | effect_to_equipment_due_to_component_failure_other | default_consequence | current_condition_notes | reason_for_consequence_change | priority | previous_photos | previous_photos_caption | previous_photos_url | corrective_action_summary | work_requirements | monitor | equipment_constraints | isolation_required | access_requirements | permits_required | type_of_work_to_be_completed | inspector | smec_inspection_condition | smec_notes | condition_changed | priority_correct | revised_priority | desktop_update_required | description_of_updates_required | photos | photos_caption | photos_url | review_material | review_element | review_defects | review_status | review_comments
b1982b59-a408-4e84-a0a3-6b76cdaaa108 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 | -20.316 | 118.5814 | POINT (118.5814394 -20.3160279) | 2025-05-27 20:13:17 AEST | 2025-07-30 03:31:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 10 | Steel Channel Bracket | Steel Channel Bracket |  | 85756 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 1, 10 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolts have Level 4 Medium High Corrosion. Steel channel support bracket has Level 4 Major Corrosion up to 40% coverage. |  | Channel anchor bolts have Level 4 Medium High Corrosion. Steel channel support bracket has Level 4 Major Corrosion up to 40% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. 3. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak behind bracket | no | yes |  | no |  | a94807ff-0280-42fd-9f1a-09d02951e350,521e53b8-bc23-4411-bd0e-d7d179c28578 | , | https://web.fulcrumapp.com/photos/view?photos=a94807ff-0280-42fd-9f1a-09d02951e350%2C521e53b8-bc23-4411-bd0e-d7d179c28578 | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks
0e43a454-5936-417b-8411-d5e03c0490d9 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:32:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26869 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 1, 10 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has leak - active at time of inspection. |  | Concrete shell segment at bolted connection penetration has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), upgraded to P2 and included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | Leak is still active | no | yes |  | no |  | c289668f-7805-45c1-9d71-acfe9b9a70c6,a9f93e1a-1b1e-4c5f-8aad-b490cd349b74 | , | https://web.fulcrumapp.com/photos/view?photos=c289668f-7805-45c1-9d71-acfe9b9a70c6%2Ca9f93e1a-1b1e-4c5f-8aad-b490cd349b74 | Concrete | Channel Bracket | Leaks |  | Not reinforcement - Channel Bracket
7a90b69f-a3e6-43a4-8871-ba37454e4ceb | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 09:41:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 2 O’clock | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85753 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 1, 2 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | AA BP |  | No change - Defect still present. Salt buildup | no | no |  | no |  | 3fc54fb9-8ec9-4568-8cc3-ba4e882bab7b,a574f345-3278-44dd-91ea-a35d2e1177c6,e773bb75-0a4b-4742-9711-e10e299e465f,9677d833-72da-4599-b75d-69bc3069dce4 | ,,, | https://web.fulcrumapp.com/photos/view?photos=3fc54fb9-8ec9-4568-8cc3-ba4e882bab7b%2Ca574f345-3278-44dd-91ea-a35d2e1177c6%2Ce773bb75-0a4b-4742-9711-e10e299e465f%2C9677d833-72da-4599-b75d-69bc3069dce4 | Concrete | Radial Joint | Drummy
9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 09:49:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27115 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | 3 O’clock Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion |  | Steel channel support bracket has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | BP AA |  | Channel corroded - Bolts & Nuts corroded, Active leaking an drummy area. Medium risk | no | yes |  | yes | Channel in poor condition | 184463c9-c3a8-4dcd-8f6c-2468000f7d38,8bdf6a6e-8b3b-4785-ac61-d3a621d0b6b6,99ff6f4e-14a5-489a-bad2-efa96a7614de,0dc61c65-86a7-403f-9dfa-f803847a5631,3ff22668-0493-4efe-8d28-06a281f8ab27,52c471c3-3437-4933-bf3d-babb91d96234,b82752d8-2366-4009-ac4b-4b91e8b5b41a,9926ef99-2ba9-4e92-853b-ca00d463cc4c | ,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=184463c9-c3a8-4dcd-8f6c-2468000f7d38%2C8bdf6a6e-8b3b-4785-ac61-d3a621d0b6b6%2C99ff6f4e-14a5-489a-bad2-efa96a7614de%2C0dc61c65-86a7-403f-9dfa-f803847a5631%2C3ff22668-0493-4efe-8d28-06a281f8ab27%2C52c471c3-3437-4933-bf3d-babb91d96234%2Cb82752d8-2366-4009-ac4b-4b91e8b5b41a%2C9926ef99-2ba9-4e92-853b-ca00d463cc4c | Steel | Channel Bracket,Channel Bracket-Bolt | Drummy,Leaks
7f761d96-ac2a-4b92-a637-e996fe372129 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 09:44:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 8 O’clock | Hydrophilic Joint Seal (Radial Joint) | Hydrophilic Joint Seal (Radial Joint) |  | 41368 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 1, 8 o'clock. Hydrophilic Joint Seal (Radial Joint) | Failure to seal joint | Failure to seal joint |  | Grout delamination over an area of 400mm long x 300mm high (Radial Joint). |  | Grout delamination over an area of 400mm long x 300mm high (Radial Joint). | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 300mm. | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Likely Likelihood of failure, resulting in a Priority 3. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | A.Acero |  | Low risk | yes | no |  | no |  | d7c14cf2-81b7-4ba1-b0fd-2454de075748,99067542-2a77-410f-8c36-9d48058a73d0 | , | https://web.fulcrumapp.com/photos/view?photos=d7c14cf2-81b7-4ba1-b0fd-2454de075748%2C99067542-2a77-410f-8c36-9d48058a73d0 | Concrete | Radial Joint | Drummy
968d0d8d-b055-46b7-9db2-78ea73528cef | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 14:10:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41876 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout in two locations of 400mm x 300mm and 200mm x 400mm. |  | Radial joint has Grout Delamination / Drummy Grout in two locations of 400mm x 300mm and 200mm x 400mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), upgraded to P2 and included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AA |  | No Change | no | no |  | no | Stalactites forming next to steel channel | bad9450c-d892-466c-aea1-60e34abd62f3,d3d5e04f-bedb-49f7-8205-03ded8c2d9bb,1b492bf1-dd0d-4053-ac3f-746fc008858e,21c11c36-abbe-43c2-9d7b-869ff8a2a7b3,5e7c4bc4-7559-4e7d-bcda-54ede796c462 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=bad9450c-d892-466c-aea1-60e34abd62f3%2Cd3d5e04f-bedb-49f7-8205-03ded8c2d9bb%2C1b492bf1-dd0d-4053-ac3f-746fc008858e%2C21c11c36-abbe-43c2-9d7b-869ff8a2a7b3%2C5e7c4bc4-7559-4e7d-bcda-54ede796c462 | Concrete,Steel | Radial Joint | Drummy
1f1b4238-2c21-4a9d-88fa-46f015a460bf | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 14:11:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 4 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 69057 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | O’clock concrete Shell Segment. | Failure to seal joint | Failure to seal joint |  | Interface to the tunnel shell concrete annulus and first ring has numerous leaks - Active at time of inspection. |  | Interface to the tunnel shell concrete annulus and first ring has numerous leaks - Active at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | AA |  | No change Drummy concrete.Low risk. | no | yes |  | yes |  | 036b3b3e-c9d7-4df9-8a08-0311de9d705d,f4cffe92-ac14-4ccc-b517-a3092442057e,b8757818-970f-41c4-87ad-6fd20bde8eef | ,, | https://web.fulcrumapp.com/photos/view?photos=036b3b3e-c9d7-4df9-8a08-0311de9d705d%2Cf4cffe92-ac14-4ccc-b517-a3092442057e%2Cb8757818-970f-41c4-87ad-6fd20bde8eef | Concrete | Circular Joint | Drummy,Leaks |  | Not reinforcement
e3a099cc-22d6-4701-a40b-64adffd15e6d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 00:51:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41877 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 1, Full circumference, Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete annular has drummy and spalling concrete all around. |  | Concrete annular has drummy and spalling concrete all around. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | SS |  | Drumminess is from cladding concrete. This is not a structural issue. | no | yes |  | yes | Reduce priority and risk. This defect relates to cladding/shotcrete, not the structural components. | 21276bec-a0b1-49d4-a4f4-8172ae62b33d,8e6f022d-e6ae-4182-af75-87932f19471e,b0c6914d-44a9-4d23-a026-af990b2b8f76,3c57cfa0-dc3f-4401-b704-21b62ba67e3e | ,,, | https://web.fulcrumapp.com/photos/view?photos=21276bec-a0b1-49d4-a4f4-8172ae62b33d%2C8e6f022d-e6ae-4182-af75-87932f19471e%2Cb0c6914d-44a9-4d23-a026-af990b2b8f76%2C3c57cfa0-dc3f-4401-b704-21b62ba67e3e | Concrete | Reinforcement | Drummy,Surface Damage
5608525a-a39b-49d7-989a-da8b981809f4 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:31:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 1 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 41880 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44043.3436 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure, Ring 1, 10 O'Clock, Concrete Element |  |  |  | Grout Delamination / debonding at segment bolted joints over an area of 200mm long x 400mm. |  | Grout Delamination / debonding at segment bolted joints over an area of 200mm long x 400mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | A.Acero |  | No change | no | no |  | no |  | 0174535a-2bc8-4c6c-a5fb-2d7ebe3436f1,0782e471-e902-4320-b2a2-86e4f334a743 | , | https://web.fulcrumapp.com/photos/view?photos=0174535a-2bc8-4c6c-a5fb-2d7ebe3436f1%2C0782e471-e902-4320-b2a2-86e4f334a743 | Concrete | Middle of Panel | Drummy |  | Middle of panel
10d7222e-9782-498b-8b98-404e3995b27b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 13:58:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 3 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 85754 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44874.4864 |  |  | No | Missing | [12 empty] | Severity Level 4 |  |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | O'Clock, Concrete segment |  |  |  | 0.3mm crack at radial segment bolted joint grout patch. |  | 0.3mm crack at radial segment bolted joint grout patch. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | BP |  | Surface patch, small cracks. Low risk | no | no |  | no |  | bc8075f5-eeff-4ed2-9d9f-3a30f236c1c3 |  | https://web.fulcrumapp.com/photos/view?photos=bc8075f5-eeff-4ed2-9d9f-3a30f236c1c3 | Concrete | Radial Joint | Crack |  | Radial Joint
b9abdc46-80b1-4c40-826b-a978b855b310 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:50:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 3 | 8 O’clock drilled holes in segment | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99514 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle segment bolted joint over area of 200mm x 100mm. |  | Grout Delamination / Drummy Grout at circle segment bolted joint over area of 200mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA BP |  | Three drilled test holes. Low risk | no | yes |  | yes |  | 1f64275b-c28e-4041-81f4-fd8439e390a8 |  | https://web.fulcrumapp.com/photos/view?photos=1f64275b-c28e-4041-81f4-fd8439e390a8 | Concrete | Circular Joint | Drummy,Test Hole
b867de59-e937-4dd6-ac99-a4683ecb5fa7 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:44:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 3 | 8- Consider removing duplicate | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 42004 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44046.4738 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 3, 8 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | 8- Consider removing duplicate | [8 empty] | Concrete |  | Test Hole |  | Duplicate - Remove
26de5042-46d4-4a8c-8074-9897bc3c18b1 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:44:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 3 | 8-Consider removing duplicate | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41917 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 3, 8 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout in one location of 300mm x 600mm. |  | Radial joint has Grout Delamination / Drummy Grout in one location of 300mm x 600mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | 8- Consider removing duplicate | [8 empty] | Concrete | Radial Joint,Reinforcement | Drummy |  | Duplicate - Remove
3578efe7-a275-415c-a9be-83a8ccd73fcd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:49:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 4 | 3 O’clock Drummy concrete | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26871 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over two areas of the same size of 200mm x 200mm. |  | Concrete shell segment has drummy concrete over two areas of the same size of 200mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA BP |  | Drummy concrete Circumference edge. Low risk | no | yes |  | no |  | 3f5b084b-5459-4bcb-a31f-68bd2e3f90e8,bc4aab33-d441-4abe-aada-2e42fb3f9249,a751eb4a-4806-4d10-9dfc-2eb62d66c0a6 | ,, | https://web.fulcrumapp.com/photos/view?photos=3f5b084b-5459-4bcb-a31f-68bd2e3f90e8%2Cbc4aab33-d441-4abe-aada-2e42fb3f9249%2Ca751eb4a-4806-4d10-9dfc-2eb62d66c0a6 | Concrete | Circular Joint,Radial Joint | Drummy |  | Radial Joint and Circumferential Joint - Not Reinforcement
fb8a19a9-0eee-4134-bc19-152d4bb867db | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:51:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 5 | 10 | Channel Anchor Bolts | Channel Anchor Bolts |  | 85755 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | O'Clock Concrete segment | Rupture | Rupture |  | Steel channel anchor bolt is missing / loose. |  | Steel channel anchor bolt is missing / loose. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing and loose anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | AA BP |  | Gout hole inactive leak. Low risk | no | yes |  | yes |  | d22245cc-9d72-4e59-8566-cd538ebc7f36 |  | https://web.fulcrumapp.com/photos/view?photos=d22245cc-9d72-4e59-8566-cd538ebc7f36 | Concrete,Steel | Grout Hole | Leaks,Loose,Missing |  | Grout Hole - not bracket
d2ffae24-ec6c-425e-b3e1-4b82c759625c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:14:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 5 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41918 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 200mm x 200mm. |  | Concrete shell segment has drummy concrete over an area of 200mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Defect not noted at time of inspection. If it were present, Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Suggest update priority and risk to low. | e0da654a-cda5-4fe8-a173-75539a430b0e |  | https://web.fulcrumapp.com/photos/view?photos=e0da654a-cda5-4fe8-a173-75539a430b0e | Concrete |  | Drummy
8429f7d8-bc66-438e-af5c-92d90ac90986 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:52:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 7 | 8 O’clock grout hole active leak | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69058 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout delamination / debonding at circle segment bolted joints over an area of 200mm x 200mm. |  | Grout delamination / debonding at circle segment bolted joints over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | A.Acero |  | Leak continues and build up of salt occurs.Medium risk. | no | yes |  | yes |  | a3c43e32-4ed7-420f-8d76-6aef2312a986 |  | https://web.fulcrumapp.com/photos/view?photos=a3c43e32-4ed7-420f-8d76-6aef2312a986 | Concrete | Circular Joint,Grout Hole | Drummy,Leaks
190f23f7-5ffa-43d4-9cd5-7c0d12a1148c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:54:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 7 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41928 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. - Condition Rating 5 |  | Grout injection hole has Leak Active at time of inspection. - Condition Rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor |  |  | Leak continues - Formation of salt in concrete at leak point | no | no |  | no |  | 33f56796-f7f0-490c-88db-6973fd75967d,2650350b-4fc7-4b59-af33-0c85d52e8150,f1c0012b-81c6-4300-9405-f6d6cf190d7d | ,, | https://web.fulcrumapp.com/photos/view?photos=33f56796-f7f0-490c-88db-6973fd75967d%2C2650350b-4fc7-4b59-af33-0c85d52e8150%2Cf1c0012b-81c6-4300-9405-f6d6cf190d7d | Concrete | Grout Hole | Leaks
396e9b60-bd06-4442-ab63-c93f988c5e61 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 15:58:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 8 | 11 | Grout Injection Hole | Grout Injection Hole |  | 85757 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. - Condition Rating 5 |  | Grout injection hole has leak - active at time of inspection. - Condition Rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | BP |  | Continued slow leak water patch, identified previously. Marked at bolt hole | no | yes |  | yes | Active leak with white salt formation | 43cf7236-abfd-40fe-b560-8f8af40cbf4e,b1aff8e7-5c4a-4d09-bcbd-95b2a5561201,c0afe889-8075-4c9c-b0c4-1f818576179b,e6236844-5434-47b6-b04f-bb852078808a | ,,, | https://web.fulcrumapp.com/photos/view?photos=43cf7236-abfd-40fe-b560-8f8af40cbf4e%2Cb1aff8e7-5c4a-4d09-bcbd-95b2a5561201%2Cc0afe889-8075-4c9c-b0c4-1f818576179b%2Ce6236844-5434-47b6-b04f-bb852078808a | Concrete | Grout Hole | Leaks
e27d23f8-7284-40b3-b57a-02331141d626 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:56:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 8 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 85764 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44874.5111 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 8, 2 O'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings |  |  |  | 0.3mm crack at radial segment bolted joint grout patch. |  | 0.3mm crack at radial segment bolted joint grout patch. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | HM |  | Crack is evident. Not repaired at the time of the inspection. This is a low priority defect. | no | yes |  | no |  | 74a9a1ae-ceff-4379-801b-a8b882ed86d8,49b43731-4d22-487c-9489-db6960f6e8a2 | , | https://web.fulcrumapp.com/photos/view?photos=74a9a1ae-ceff-4379-801b-a8b882ed86d8%2C49b43731-4d22-487c-9489-db6960f6e8a2 | Concrete | Radial Joint | Crack |  | Radial Joint
9e35d7e8-e025-4d5f-a828-8f758283bce7 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:06:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 8 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99515 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 8, 4 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area of 100mm x 100mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 388e83b4-8d90-4a28-b3e0-c609483b6c04,f8b7bfc6-75ac-43e5-9713-f8757f19ec1c | , | https://web.fulcrumapp.com/photos/view?photos=388e83b4-8d90-4a28-b3e0-c609483b6c04%2Cf8b7bfc6-75ac-43e5-9713-f8757f19ec1c | Concrete | Circular Joint | Drummy
d8911c4c-47bb-44f1-8c59-c4d3146ed36e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:09:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 9 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 85765 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 9, 2 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Steel channel support bracket has Level 3 Medium Corrosion up to 50% coverage. |  | Steel channel support bracket has Level 3 Medium Corrosion up to 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P3. | Safety | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. 3. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | On-Line | No | Walkway | - | Scheduled Maintenance Competent Supervisor | BP |  | New spot salts 9 O’Clock under steel channel support bracket.Medium risk | yes | yes |  | yes | New leak with spotting salts 50mm diameter | 5d518eba-eefe-489b-b1e9-5a34b235ca76,af909b1d-fb07-4182-8795-bcf506ea0858 | , | https://web.fulcrumapp.com/photos/view?photos=5d518eba-eefe-489b-b1e9-5a34b235ca76%2Caf909b1d-fb07-4182-8795-bcf506ea0858 | Steel | Channel Bracket | Leaks
aa6687f7-0267-4cb4-ab67-ba14e5cf1d33 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 00:12:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 10 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99516 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 10, 4 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area of 150mm x 300mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area of 150mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | BP |  | Inactive leak bolt hole. Low risk | no |  |  | yes |  | c5f7d2c2-3716-4f77-8f0c-156e38f932f4 |  | https://web.fulcrumapp.com/photos/view?photos=c5f7d2c2-3716-4f77-8f0c-156e38f932f4 | Concrete | Grout Hole | Drummy,Leaks |  | grout hole not Circular Joint
43d3fe01-953d-4cac-b04d-4633f8bc6904 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:14:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 11 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27120 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Corrosion Under Buildup |  | Corrosion Under Buildup | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 11, 2 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services. | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Steelwork Remediation Crew. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | BP , AA |  | Surface patch repairs, replace missing bolts corroded. Low risk | no | yes |  | yes |  | dd38181e-1139-46bb-a992-aa254d97a15e,a2ce154c-a40b-4014-aea7-95c7c66ffe28 | , | https://web.fulcrumapp.com/photos/view?photos=dd38181e-1139-46bb-a992-aa254d97a15e%2Ca2ce154c-a40b-4014-aea7-95c7c66ffe28 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
00cda714-0c80-4992-82ee-cc664ce74862 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:16:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 12 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26874 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 12, 8 O'Clock, Concrete Element, New Defect 2017 | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Active Leak Grout Injection Hole |  | Active Leak Grout Injection Hole | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding, Walkway | Working at Heights, Confined Space, Hot Work, Excavation | Scheduled Maintenance Competent Supervisor | AA BP |  | Active leaking continues starting to build up salt. Medium risk | yes | yes |  | yes |  | c14b73e6-af96-4425-9c65-624edb90d645,3465c876-82f9-49f7-9e0d-599143993618 | , | https://web.fulcrumapp.com/photos/view?photos=c14b73e6-af96-4425-9c65-624edb90d645%2C3465c876-82f9-49f7-9e0d-599143993618 | Concrete | Grout Hole | Leaks |  | Not reinforcement
c9e84d13-19b7-4bcf-bde8-07fff10546d7 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:19:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 13 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85895 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | BP |  | Missing anchor bolt.Medium risk | no | yes |  | yes |  | 7c85fb44-2252-47dd-bc5d-dc7f7e566008 |  | https://web.fulcrumapp.com/photos/view?photos=7c85fb44-2252-47dd-bc5d-dc7f7e566008 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
f7dcc05c-efe7-48ac-abc1-3071afb31f0b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:19:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 13 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26787 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 13, 8 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Leak Active at time of inspection. Leak occurs between Ring 13 & 14. |  | Circle joint has Leak Active at time of inspection. Leak occurs between Ring 13 & 14. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | A.Acero |  | No change- active leaking continues | no | no |  | no |  | e59587ee-72aa-4fc6-a657-caa28feb90d1,2158f87d-95c6-4473-bd98-c7d9603f12f1,eb84e8c8-319f-4e2c-8c2f-ab9280e948a1,22ea825b-a6ab-4c94-b634-082714711f3d | ,,, | https://web.fulcrumapp.com/photos/view?photos=e59587ee-72aa-4fc6-a657-caa28feb90d1%2C2158f87d-95c6-4473-bd98-c7d9603f12f1%2Ceb84e8c8-319f-4e2c-8c2f-ab9280e948a1%2C22ea825b-a6ab-4c94-b634-082714711f3d | Concrete | Circular Joint | Leaks |  | Not reinforcement
aa2f6c5a-25cc-4725-adc7-02733d06eb5b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:16:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 14 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41881 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 14, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 200 mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 200 mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | b4462138-0f94-47da-a639-e3401da60364,793b4e49-8a9a-4e2e-adc3-af444eb9f1c0 | , | https://web.fulcrumapp.com/photos/view?photos=b4462138-0f94-47da-a639-e3401da60364%2C793b4e49-8a9a-4e2e-adc3-af444eb9f1c0 | Concrete | Circular Joint | Drummy
665f2a1a-cffe-4f55-bf81-70ca463a5681 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:24:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 15 | 10 O’clock grout hole | Grout Injection Hole |  |  | 85766 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 15, 10 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. - Condition Rating 5 |  | Grout injection hole has leak - active at time of inspection. - Condition Rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | A.A |  | No change. Medium risk | no | yes |  | no |  | afd41dfa-28f0-4631-aa30-0147e16ab012,d4392b5a-281a-429d-b7ea-5c786b5e4358 | , | https://web.fulcrumapp.com/photos/view?photos=afd41dfa-28f0-4631-aa30-0147e16ab012%2Cd4392b5a-281a-429d-b7ea-5c786b5e4358 | Concrete | Grout Hole | Leaks
21caa9db-8e37-4fcf-82b1-d535498059d0 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:41:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 17 | 10 & 1 O’clock | Channel Anchor Bolts | Channel Anchor Bolts |  | 26791 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Concrete Shell Segment | Rupture | Rupture |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | BP |  | Channel anchor bolts corrosion 10 and 1 O’Clock where bracket is corroding due to back seepage, wet, salts formation. Medium Risk | yes | yes |  | yes |  | c42b3328-a4bd-480e-824c-01b7c98e9c69,43301d51-a346-4bd9-81f1-b516be02ce90,86f8d434-03a7-473d-90e0-65e6770e7686 | ,, | https://web.fulcrumapp.com/photos/view?photos=c42b3328-a4bd-480e-824c-01b7c98e9c69%2C43301d51-a346-4bd9-81f1-b516be02ce90%2C86f8d434-03a7-473d-90e0-65e6770e7686 | Concrete | Channel Bracket-Bolt | Leaks
caea08f0-1bf6-4718-ad60-5ac7a68c3951 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 09:29:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 17 | 10 consider removing entry | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85767 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 17, 10 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor |  |  | Consider removing entry-duplicate | [8 empty] | Concrete |  | Leaks |  | Duplicate - Remove
d88ad90e-0f2f-43c7-863c-3ee954d49419 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 09:28:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 17 | 10 Consider removing entry | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41931 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 17, 10 o'clock. Concrete Shell Segment. - Condition Rating 4. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | No | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor |  |  | Consider removing duplicate | [8 empty] | Concrete |  | Leaks |  | Duplicate - Remove
309e7188-8bbd-4207-8b31-586a481af661 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:43:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 17 | 9 O’clock concrete cracks minor | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 41885 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 17, 9 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at segment bolted joints over an area of 350mm x 350mm. |  | Grout Delamination / debonding at segment bolted joints over an area of 350mm x 350mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AA BP |  | Surface cracks. Monitor surface concrete. Low risk | no | yes |  | yes |  | d62748ee-f383-4939-977e-736a77101dbd,12b70aa8-736e-4022-8dd9-2975f0ea89d3 | , | https://web.fulcrumapp.com/photos/view?photos=d62748ee-f383-4939-977e-736a77101dbd%2C12b70aa8-736e-4022-8dd9-2975f0ea89d3 | Concrete | Radial Joint | Crack,Drummy
e57784ec-7102-439d-b632-8599eea2498d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:50:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 18 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99517 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints over an area of 200mm x 200mm. |  | Grout Delamination / debonding at radial segment bolted joints over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AS BP |  | Drummy grout repair. Low priority | no | yes |  | yes |  | 5d6e5a2c-feda-44dc-8d3f-e1b4977a278e,1363b019-8935-4f1a-81da-784e4b71a31a | , | https://web.fulcrumapp.com/photos/view?photos=5d6e5a2c-feda-44dc-8d3f-e1b4977a278e%2C1363b019-8935-4f1a-81da-784e4b71a31a | Concrete | Radial Joint | Drummy
e3fba9d2-5c97-4a90-b4ff-570eb816f623 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 05:40:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 20 | 10 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69059 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/12/2021 |  | 16/02/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety |  | Same defect | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 20, 10 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints |  | Grout Delamination / debonding at radial segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Loss of production and services | - |  | Priority: P3 |  |  |  | Break out grout locally, abrasive blast steelwork, and inspect by competent engineer to develop repair detail. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Supervisor | SS |  | Duplicate |  |  |  | yes | This is a duplicate of the defect at 12 o'clock. Delete |  |  |  | Concrete | Circular Joint | Drummy |  | Duplicate - Remove
89709a5b-3004-44aa-90e3-8e9e2b4a08e5 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 17:18:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 20 | 11 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69060 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 20, 11 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints over an area of 150mm x 150mm. |  | Grout Delamination / debonding at radial segment bolted joints over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), revised recommended action to include repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | AA-BP |  | Drummy concrete.Low risk | no | yes |  | yes |  | 1c55a815-8b5c-4f0a-8afa-f07269dce205 |  | https://web.fulcrumapp.com/photos/view?photos=1c55a815-8b5c-4f0a-8afa-f07269dce205 | Concrete | Radial Joint | Drummy
cc1c9911-1c67-43f6-b97f-484e62651750 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 16:57:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 20 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69061 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 20, 12 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete at segmental concrete wall over an area of 100mm x 100mm |  | Concrete shell segment has drummy concrete at segmental concrete wall over an area of 100mm x 100mm | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Standard Repair Detail Competent Supervisor | AA BP |  | Drummy concrete. Low risk | [5 empty] | a7c35281-8da2-4deb-aab8-5551367e17a1 |  | https://web.fulcrumapp.com/photos/view?photos=a7c35281-8da2-4deb-aab8-5551367e17a1 | Concrete | Reinforcement | Drummy
4c6d4c04-769b-4e7f-89e3-c71edba8f7e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 05:43:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 21 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26881 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 21, 10 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | Leak is still active, corrosion of bracket is result | no | yes |  | no |  | 889bdb70-495a-4ee3-9094-aee88e0020dc,c2f6d6dc-cafa-4244-8fd0-1a1c90b313de,60d9b77c-91ad-4d20-8ae8-7d6c0bf0bfe7,89085428-410d-48ed-80d1-042cbb1d2db9 | ,,, | https://web.fulcrumapp.com/photos/view?photos=889bdb70-495a-4ee3-9094-aee88e0020dc%2Cc2f6d6dc-cafa-4244-8fd0-1a1c90b313de%2C60d9b77c-91ad-4d20-8ae8-7d6c0bf0bfe7%2C89085428-410d-48ed-80d1-042cbb1d2db9 | Concrete | Channel Bracket | Leaks |  | Not reinforcement - Channel Bracket
5f95acb9-9168-4587-bb03-eb7c246c0018 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 17:09:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 21 | 10 O’clock steel channel | Channel Anchor Bolts | Channel Anchor Bolts |  | 26880 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Corrosion Under Buildup |  | Corrosion Under Buildup | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 21, 10 o'clock. Steel Channel Support Bracket | Rupture | Rupture |  | Steel channel support bracket has Level 2 - Minor Corrosion. Anchor bolts have Level 4 - Medium High Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion. Anchor bolts have Level 4 - Medium High Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), revised recommended action to replace corroded anchor bolts only. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services. | Priority: P3 |  |  |  | Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | AA |  | Channel corrosion, salts buildup behind.Medium risk | yes | yes |  | yes |  | 5e25c115-9eaf-476c-a6ea-dd57ea5496fb,b4da837f-ba14-4327-a60f-f8cd8045ae99 | , | https://web.fulcrumapp.com/photos/view?photos=5e25c115-9eaf-476c-a6ea-dd57ea5496fb%2Cb4da837f-ba14-4327-a60f-f8cd8045ae99 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
64e464c3-133d-4749-afe0-1f6604ffce0d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 17:09:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 21 | 3 O’clock Channel bolt | Steel Channel Bracket | Steel Channel Bracket |  | 85896 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 21, 2 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | AA |  | Missing bolt Defect. Low risk | no | yes |  | no |  | 7def633e-56a7-431e-97f0-317202dd404b,e9cf9620-2059-4ef3-b0ab-50c9d0853fa0 | , | https://web.fulcrumapp.com/photos/view?photos=7def633e-56a7-431e-97f0-317202dd404b%2Ce9cf9620-2059-4ef3-b0ab-50c9d0853fa0 | Steel | Channel Bracket-Bolt | Missing |  | Only Bolt
27f72c2e-c932-45e6-ac5b-3323bcd17354 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:21:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 21 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42005 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 21, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has concrete excavation over a 100mm x 100mm areas which has not been repaired. |  | Concrete shell segment has concrete excavation over a 100mm x 100mm areas which has not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Low priority patch | no | yes |  | yes | Priority and risk to be downgraded | b1316c2d-014a-4f16-a2ce-0ab14adc2601,ed0a5bb1-b2a3-4eb1-beba-c529fb825872 | , | https://web.fulcrumapp.com/photos/view?photos=b1316c2d-014a-4f16-a2ce-0ab14adc2601%2Ced0a5bb1-b2a3-4eb1-beba-c529fb825872 | Concrete
e9bb0168-35cf-4dd1-850e-39c762d20d7e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:49:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 23 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85897 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | No delamination detected at this position. | yes | no | 4 | yes | Remove or reduce priority to 4. |  |  |  | Concrete | Circular Joint | Drummy
cb8ab833-88ba-478e-bb56-b954ac7c2dde | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 19:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 23 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41932 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 23, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | BP AA |  | Corroded delaminated channel support, supporting cable trays. Inactive leaks behind channel. Salt buildup. Medium risk | no | yes |  | yes |  | 7657abd2-933d-4f0e-9571-a50cca82e908,dcd4cd89-bce7-46c4-8cee-6e0b30a41cde,f601cac6-3a40-4f1e-84c1-bae86bbbbb4a | ,, | https://web.fulcrumapp.com/photos/view?photos=7657abd2-933d-4f0e-9571-a50cca82e908%2Cdcd4cd89-bce7-46c4-8cee-6e0b30a41cde%2Cf601cac6-3a40-4f1e-84c1-bae86bbbbb4a | Concrete | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Drummy,Leaks
ed209b8e-6b25-4764-b1c2-5e04ec1d01e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:31:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 24 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99518 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 24, 4 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area of 50mm x 50mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area of 50mm x 50mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | yes | no |  | yes | Priority and risk to be downgraded | 5655ae2a-2cec-4d90-b6a4-688d4cff08a3,2576eb06-f883-4e25-944d-4a1f4c1e57fc,11acccef-68fe-4377-a8bd-bb0e49859f3a | ,, | https://web.fulcrumapp.com/photos/view?photos=5655ae2a-2cec-4d90-b6a4-688d4cff08a3%2C2576eb06-f883-4e25-944d-4a1f4c1e57fc%2C11acccef-68fe-4377-a8bd-bb0e49859f3a | Concrete | Circular Joint | Drummy
cb3e1f88-0dcd-4b5b-92de-9f8390deea54 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 09:06:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 25 | 3 O’clock Corroded channel | Channel Anchor Bolts | Channel Anchor Bolts |  | 26888 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 25, 3 o'clock. Bolt, Nut & Washer. | Rupture | Rupture |  | Steel channel support bracket has Level 2 - Minor Corrosion. Anchor bolts have Level 4 - Medium High Corrosion and active leak. |  | Steel channel support bracket has Level 2 - Minor Corrosion. Anchor bolts have Level 4 - Medium High Corrosion and active leak. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), included repair methodology provided by GTS and replacement of corroded anchor bolts. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | 1. Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. 2. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AA |  | Defect still present steel channel supporting 3 cable trays. medium risk | yes | yes |  | no |  | 44771b59-7f54-4111-b860-eb6f9c2596a3,6584974a-639c-4fea-abd5-0cf43e238304,9aa900c1-31d0-4e1c-a238-c1277cc1e0ad | ,, | https://web.fulcrumapp.com/photos/view?photos=44771b59-7f54-4111-b860-eb6f9c2596a3%2C6584974a-639c-4fea-abd5-0cf43e238304%2C9aa900c1-31d0-4e1c-a238-c1277cc1e0ad | Steel | Channel Bracket,Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Corrosion-Surface,Leaks
6bf454ee-f2b0-414b-bcb7-7dbe150c9ce2 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 09:03:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 25 | 3 O’clock steel channel | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26788 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Leak from behind the steel channel bracket Active at time of inspection. |  | Leak from behind the steel channel bracket Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AA |  | Active leak still present.Medium risk | no | yes |  | no |  | a31c0952-da4d-4d29-8e99-813783262cc8,3baca9c7-022d-4a2a-869b-6f8200c77332,c0109a4d-e3e8-4bff-a9f0-e8fba56d214b | ,, | https://web.fulcrumapp.com/photos/view?photos=a31c0952-da4d-4d29-8e99-813783262cc8%2C3baca9c7-022d-4a2a-869b-6f8200c77332%2Cc0109a4d-e3e8-4bff-a9f0-e8fba56d214b | Concrete,Steel | Channel Bracket | Leaks |  | No reinforcement
f2c8edd3-54b8-4298-a633-cc03289de1aa | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:33:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 25 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99519 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 25, 4 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area of 50mm x 50mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area of 50mm x 50mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  |  | no | no | P4 | yes | Priority and risk to be downgraded | cd3d274f-959c-4823-9530-d38dc1fb6c02,fccafe11-9ba1-4f61-bd5c-f7300230d06c,cc272869-3584-4df2-9bc5-e54c144fd94b | ,, | https://web.fulcrumapp.com/photos/view?photos=cd3d274f-959c-4823-9530-d38dc1fb6c02%2Cfccafe11-9ba1-4f61-bd5c-f7300230d06c%2Ccc272869-3584-4df2-9bc5-e54c144fd94b | Concrete | Circular Joint | Drummy
83eeaa50-b694-48c9-a22e-4c85681324d7 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:35:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 25 | 4 | Steel Channel Bracket | Steel Channel Bracket |  | 26882 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 25, 4 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion |  | Steel channel support bracket has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | This is a duplicate of the 3 o'clock issue |  |  |  | yes | Delete this duplicate |  |  |  | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface |  | Duplicate - Remove
91255cb9-8493-4a9b-b6a1-dfb1cad90bbf | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:40:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 25 | 7 O’clock | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26887 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 25, 7 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak is slow, but active with salts buildup | no | no |  | yes | Priority and risk to be downgraded | b9f88f98-91f1-4a99-80dc-0fcc79827c40,ea32ae07-b823-4520-8f26-8196b85ad429 | , | https://web.fulcrumapp.com/photos/view?photos=b9f88f98-91f1-4a99-80dc-0fcc79827c40%2Cea32ae07-b823-4520-8f26-8196b85ad429 | Concrete | Grout Hole | Leaks |  | Not reinforcement
6fa797c6-42f2-431a-9908-185da306164c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 08:57:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 26 | 2 O’clock grout hole inactive leak | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26789 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 26, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | BP |  | Inactive leak. Monitor only. Low risk. | no | no |  |  |  | 5d1dafbf-97e5-4a95-97bb-6463d92e4785 |  | https://web.fulcrumapp.com/photos/view?photos=5d1dafbf-97e5-4a95-97bb-6463d92e4785 | Concrete | Grout Hole | Leaks |  | Not reinforcement
47231d0c-cc6c-4d84-8f5a-908503133a3e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:45:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 26 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99520 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Remove entry Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area of 100mm x 100mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | yes | no |  | yes | Priority and risk to be downgraded | 062632a3-779b-49d9-8896-e426de0a7d1f,3ca9c28b-a84f-4630-9b4f-02465cf46de9,aaf3dbfb-0acd-419e-92a9-42309929fc1f,f24fb635-4a88-4f79-9dd6-b81d81d5f6d8 | ,,, | https://web.fulcrumapp.com/photos/view?photos=062632a3-779b-49d9-8896-e426de0a7d1f%2C3ca9c28b-a84f-4630-9b4f-02465cf46de9%2Caaf3dbfb-0acd-419e-92a9-42309929fc1f%2Cf24fb635-4a88-4f79-9dd6-b81d81d5f6d8 | Concrete | Circular Joint | Drummy
53d6b10b-086e-4381-8b15-cecc73860404 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:52:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 27 | 7 Consider removing entry | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26889 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Structure,Ring 027,7 O'Clock,Concrete Element,New Defect 2017 | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Active Leak Shell Segment Interface |  | Active Leak Shell Segment Interface | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak at interface of shell segments. Carry out leak seal in accordance with approved remediation work scope. | Engineering repair method and specification required. Concrete remediation crew. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | Cannot locate defect | no | no |  | no |  | f856f1d7-a692-47dc-a0bb-a21a0aecbd23 |  | https://web.fulcrumapp.com/photos/view?photos=f856f1d7-a692-47dc-a0bb-a21a0aecbd23 | Concrete | Reinforcement | Leaks
ec43b587-91b0-45c3-a467-8d7325623ce3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:32:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 28 | 2 O’clock grout hole active leak | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26790 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | O’Clock Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Social / Cultural Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | BP |  | Active leak chlorides affecting concrete segments. Medium risk. The leak seems to be happening at radial joint at 3 o' clock | yes | yes |  | yes |  | 3a6b8936-d794-4de5-a4ad-94d2d0d1f2b8,8c7a7c0b-7e1c-4887-bd6b-250b2ed306e2,291277bb-9d78-4540-a02d-c015234cb742,4f130d79-ccf9-49cd-a811-01fb7df13452,c2f95db6-cfad-4990-a4a0-2f615f3ae1dd | ,,,, | https://web.fulcrumapp.com/photos/view?photos=3a6b8936-d794-4de5-a4ad-94d2d0d1f2b8%2C8c7a7c0b-7e1c-4887-bd6b-250b2ed306e2%2C291277bb-9d78-4540-a02d-c015234cb742%2C4f130d79-ccf9-49cd-a811-01fb7df13452%2Cc2f95db6-cfad-4990-a4a0-2f615f3ae1dd | Concrete | Grout Hole,Radial Joint | Leaks |  | Not reinforcement
ce66b86b-d6d7-4841-9508-fda6159a4479 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:29:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 28 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41934 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 28, 2 o'clock. Concrete Shell Segment Bolted Joint (Circle Joint) | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. Note leak is located at bolted joint grouting. |  | Joint seal (Circle joint) has Leak Active at time of inspection. Note leak is located at bolted joint grouting. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | HM |  | Grout hole leak is active at the time of inspection. | no | yes |  | no |  | c29b5e9d-be15-414c-8f36-ec511d85470f,866c2bcd-2b87-46fe-8ce8-5280ed8151cf | , | https://web.fulcrumapp.com/photos/view?photos=c29b5e9d-be15-414c-8f36-ec511d85470f%2C866c2bcd-2b87-46fe-8ce8-5280ed8151cf | Concrete | Grout Hole | Leaks |  | Not Circular JOint
c7246497-e015-445d-9194-a766b87aa3f8 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:55:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 28 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26891 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 28, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | SS |  | Not visible at time of inspection. Possibly buried. | no | no |  | no |  | bf3b5ea7-ca69-45b5-ad4d-998cc54127df,9437d88a-97b7-40bd-8de8-48d754bf5b53,015fa61f-b7ac-4bb1-bba1-81e56f27e289 | ,, | https://web.fulcrumapp.com/photos/view?photos=bf3b5ea7-ca69-45b5-ad4d-998cc54127df%2C9437d88a-97b7-40bd-8de8-48d754bf5b53%2C015fa61f-b7ac-4bb1-bba1-81e56f27e289 | Concrete | Grout Hole | Leaks |  | Not reinforcement
f1740844-b413-4d1b-96cf-aecd4220af76 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 31 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 08:48:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 29 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 85898 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 29, 2 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | AA |  | Missing bolt priority low | no | yes |  | no |  | 56bb517f-5714-4e34-a7e5-9cd72cb20e4b,07ef5408-fed4-481d-8378-083e3d230d6c | , | https://web.fulcrumapp.com/photos/view?photos=56bb517f-5714-4e34-a7e5-9cd72cb20e4b%2C07ef5408-fed4-481d-8378-083e3d230d6c | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
5d16ced9-2080-44c0-8a39-84ba43464e74 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 24 |  |  |  | 2025-07-24 10:42:49 AEST | 2025-07-28 08:48:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 3 | 9 to 10 O’clock | [34 empty] | Drummy concrete | [24 empty] | A.Acero |  | Drumming in concrete. Sprayed out. But not documented in fulcrum locations at edge od 2-3 ring and 3-4 ring. Low risk |  | no |  | no |  | 3b248b83-03f5-4872-9a87-45f418f0c28e,19957fec-eb50-4ab0-803b-70d371148e85,e7d12f43-43c0-43ac-975c-250179517e91,545a2d48-efdd-4fcf-aca2-8f26a242cf3b | ,,, | https://web.fulcrumapp.com/photos/view?photos=3b248b83-03f5-4872-9a87-45f418f0c28e%2C19957fec-eb50-4ab0-803b-70d371148e85%2Ce7d12f43-43c0-43ac-975c-250179517e91%2C545a2d48-efdd-4fcf-aca2-8f26a242cf3b | Concrete | Circular Joint | Drummy |  | Circular Joint
52835ce1-9f6b-478a-bfc2-ea0fb49314d6 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 24 |  |  |  | 2025-07-24 11:39:50 AEST | 2025-07-28 08:48:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 11 | 8 | [34 empty] | O’Clock position, injection grout hole | [24 empty] | AA |  | Minor leaking starting to appear and build up of salts.Low risk |  | yes |  | yes |  | 097396cd-71fa-4f50-b93b-09c5ae69795d,01dc7d8c-a8cf-4706-a26b-35492e80a333 | , | https://web.fulcrumapp.com/photos/view?photos=097396cd-71fa-4f50-b93b-09c5ae69795d%2C01dc7d8c-a8cf-4706-a26b-35492e80a333 | Concrete | Grout Hole | Leaks
24b0f38f-edf9-4e95-a8ef-0008d5c0f173 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 24 |  |  |  | 2025-07-24 12:49:48 AEST | 2025-07-28 08:48:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 27 | 10 | [34 empty] | Slow damp leak sign at grout hole |  |  |  |  | Grout injection hole has Leak - Inactive at time of inspection. | [13 empty] | Yes | [5 empty] | A.Acero |  | Wet surface starting to appear at grout hole. Low risk |  | no |  | no |  | 60094446-53aa-4d21-b4d1-3a7059b51c81 |  | https://web.fulcrumapp.com/photos/view?photos=60094446-53aa-4d21-b4d1-3a7059b51c81 | Concrete | Grout Hole | Leaks
52f9cb96-c662-4449-a6ce-637c1a458c96 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 25 | -20.3213 | 118.586 | POINT (118.5859687865392 -20.32134596715089) | 2025-07-24 19:04:25 AEST | 2025-07-28 08:48:00 AEST | 30011704-user5@smec.com | james.stone@smec.com | 11 | 6 O’clock Support Conveyor and Walkway |  |  | Support Conveyor and walkway base plate | [14 empty] | Corrosion - Connection |  | 2 | [14 empty] | Nut and bolt corrosion, delaminating steel | [16 empty] | Monitor | Treat corrosion | Yes | [5 empty] | AC BP |  | Support Beam walkway and Conveyor base plate, steel Delamination. Medium risk |  | yes |  | yes |  | 38d411ad-5a15-4b9a-8ae8-496a16ff8ffe,946dcbdc-530c-4f50-a7dd-3cafa3cb8a9f | , | https://web.fulcrumapp.com/photos/view?photos=38d411ad-5a15-4b9a-8ae8-496a16ff8ffe%2C946dcbdc-530c-4f50-a7dd-3cafa3cb8a9f | Steel | Centre Support | Drummy
0ecdf409-1778-42fa-b048-874adec21c74 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 25 |  |  |  | 2025-07-24 19:10:54 AEST | 2025-07-28 08:44:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 15 | 6 |  |  | Conveyor and walkway support beam | [14 empty] | Corrosion - Connection |  | 2 | [14 empty] | Conveyor and walkway support beam base corrosion | [18 empty] | Monitor with painting | [5 empty] | AA BP |  | Support Conveyor and walkway base plate corroded/ delaminating . Medium risk |  | yes |  | yes |  | 527a5ddf-e4a9-4030-9010-738548f1dfc2,93427d72-c697-426e-b5d2-b1ee4778fcde | , | https://web.fulcrumapp.com/photos/view?photos=527a5ddf-e4a9-4030-9010-738548f1dfc2%2C93427d72-c697-426e-b5d2-b1ee4778fcde | Steel | Walkway Support | Drummy
99211911-a794-4510-a35e-fc79b29c502f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 25 | -20.3173 | 118.5811 | POINT (118.5811253255184 -20.31727224642713) | 2025-07-24 19:17:00 AEST | 2025-07-28 08:30:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 19 | 5 |  | Steel Channel Bracket | [15 empty] | Corrosion - Connection |  | 2 | [14 empty] | O’Clock Circular Walkways support end bolt nut Corrosion |  |  | Corrosion | [21 empty] | AA BP |  | Circular Walkways support end bolt nut Corrosion .Medium risk |  | yes |  | yes |  | 4e267ca7-3736-4a38-b995-554c26934a28 |  | https://web.fulcrumapp.com/photos/view?photos=4e267ca7-3736-4a38-b995-554c26934a28 | Steel | Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support and Walkway Bolt
8b5e9d67-7734-4262-80b6-cb54eb0c2648 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 25 |  |  |  | 2025-07-24 19:21:23 AEST | 2025-07-28 08:28:54 AEST | 30011704-user5@smec.com | james.stone@smec.com | 27 | 5 and 6 |  |  | Conveyor and walkway support beam | [14 empty] | Corrosion - Connection |  | 2 | [14 empty] | O’Clock Support Conveyor and walkway base plate, and Circular support | [24 empty] | AC BP |  | Support Conveyor and walkway base plate, Circular support .Medium risk |  | yes |  | yes |  | 4d13a672-0665-438b-bd37-735376a21758,a54b2046-7cb0-407e-9aa8-6c6e025b8f18,9b760a84-758f-47b4-8d70-1c62e770f717 | ,, | https://web.fulcrumapp.com/photos/view?photos=4d13a672-0665-438b-bd37-735376a21758%2Ca54b2046-7cb0-407e-9aa8-6c6e025b8f18%2C9b760a84-758f-47b4-8d70-1c62e770f717 | Steel | Walkway Support
67758db5-619b-49af-af62-edd0d63537ff | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 19 |  |  |  | 2025-07-27 09:59:32 AEST | 2025-07-28 08:32:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | 5 | 1 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [15 empty] | Concrete Damage due to Cast- In |  | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods | [7 empty] | O’clock , Drummy concrete patch |  | Failure of shell segment in compression or tension leading to single ring failure. | [22 empty] | AA |  | Drummy patched concrete with inactive leak - monitor. Low Risk |  | yes |  | yes |  | c0891d8f-55b5-4144-8230-1817a279f730 |  | https://web.fulcrumapp.com/photos/view?photos=c0891d8f-55b5-4144-8230-1817a279f730 | Concrete |  | Drummy,Leaks
db6b7a25-e866-4c8e-8ed7-ade0c3d19641 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 19 |  |  |  | 2025-07-27 10:02:46 AEST | 2025-07-28 08:42:00 AEST | 30011704-user5@smec.com | james.stone@smec.com | 5 | 3 O’clock Inactive leak - patched area |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | AA |  | Inactive leak - patched area | [5 empty] | 23d8fa15-6854-4614-9185-e2d19f21864b,c2783fad-1161-49d5-a994-a6489035b305,76509de0-ec14-4698-b747-9a50c20cce57 | ,, | https://web.fulcrumapp.com/photos/view?photos=23d8fa15-6854-4614-9185-e2d19f21864b%2Cc2783fad-1161-49d5-a994-a6489035b305%2C76509de0-ec14-4698-b747-9a50c20cce57 | Concrete |  | Leaks
e016950b-fc3b-46f1-8ec5-25de4831dad6 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 19 |  |  |  | 2025-07-27 10:09:03 AEST | 2025-07-28 08:41:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 9 | 2 O’clock Corrosion channel bracket bolts |  | Steel Channel Bracket | [15 empty] | Corrosion - Connection |  | 3 | [39 empty] | AA |  | Corrosion present in channel bracket and bolts. Low Risk | [5 empty] | 48cd6ed3-edf9-4907-a1b2-322d8c963320,6e781fc1-0ebc-4f25-b6ba-c3373bec7671,47773162-ebe4-4f16-a7ca-63a87a981db4 | ,, | https://web.fulcrumapp.com/photos/view?photos=48cd6ed3-edf9-4907-a1b2-322d8c963320%2C6e781fc1-0ebc-4f25-b6ba-c3373bec7671%2C47773162-ebe4-4f16-a7ca-63a87a981db4 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
145e8573-63b1-43d4-adac-d27f236808fd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 19 |  |  |  | 2025-07-27 10:15:17 AEST | 2025-07-28 08:42:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 16 | 3 O’clock Grout hole Inactive leak |  | Grout Injection Hole | [15 empty] | Concrete Damage due to Cast- In |  | 1 |  |  |  | Health & Safety |  |  | Poor Construction Methods | [32 empty] | AA |  | Salt build up - inactive leaking. Priority 1 and monitor.Low risk |  | no |  | no |  | 98ffc14d-42e5-4b7a-b490-e2322fc19524,4d3e5032-d9be-4889-9941-1f97a1de8915,04c13aec-2179-47f4-80be-f0d91377866a,8fba2f53-10af-486d-b8d7-bc8dc28df1ad | ,,, | https://web.fulcrumapp.com/photos/view?photos=98ffc14d-42e5-4b7a-b490-e2322fc19524%2C4d3e5032-d9be-4889-9941-1f97a1de8915%2C04c13aec-2179-47f4-80be-f0d91377866a%2C8fba2f53-10af-486d-b8d7-bc8dc28df1ad | Concrete | Grout Hole | Leaks
261a1084-9b65-4201-ac6b-0c0758f128f2 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 19 |  |  |  | 2025-07-27 10:21:16 AEST | 2025-07-28 08:42:39 AEST | 30011704-user5@smec.com | james.stone@smec.com | 18 | 1 O’clock Grout hole inactive leak |  | Grout Injection Hole | [17 empty] | 1 |  |  |  | Health & Safety |  |  | Additional Components | [32 empty] | AA |  | Build up Salt in grout hole. Inactive leak. Low risk | [5 empty] | 91793c2b-ea31-49a9-8b04-a58e60f9e7cf,959982cc-234d-47a9-8451-03f9506ab7ef | , | https://web.fulcrumapp.com/photos/view?photos=91793c2b-ea31-49a9-8b04-a58e60f9e7cf%2C959982cc-234d-47a9-8451-03f9506ab7ef | Concrete | Grout Hole | Leaks
f2090ec0-b174-450f-9862-d007dc996b66 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 19 |  |  |  | 2025-07-27 10:45:18 AEST | 2025-07-28 08:44:16 AEST | 30011704-user5@smec.com | james.stone@smec.com | 25 | 4 O’clock Active leak grout hole | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26788 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | 3 |  | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Severity Level 3 |  | Likely (Failure within 2 Years) | Possible (Failure within 5 Years) |  | Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Leak from behind the steel channel bracket Active at time of inspection. |  | Leak from behind the steel channel bracket Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AA |  | Active leak from 25 - 3 O’clock espreading down to 4 O’clock. Medium risk | no | yes |  | no |  | a2828155-9c62-4c55-bb7f-6b48e0ac0ed4,2a529fe5-b4f4-48bb-a035-20f815b06974 | , | https://web.fulcrumapp.com/photos/view?photos=a2828155-9c62-4c55-bb7f-6b48e0ac0ed4%2C2a529fe5-b4f4-48bb-a035-20f815b06974 | Concrete,Steel | Channel Bracket,Grout Hole,Reinforcement | Leaks
a795ab06-9bb5-42eb-a3fb-d27a7627965c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 19 |  |  |  | 2025-07-27 10:51:48 AEST | 2025-07-28 08:24:50 AEST | 30011704-user5@smec.com | james.stone@smec.com | 28 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41934 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 28, 3 o'clock. Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. Note leak is located at bolted joint grouting. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | AA |  | Active leak priority medium | yes | yes |  | no |  | e502f0bf-53c2-4cb1-a50b-77dc4cb59cbb,f75d2e9a-b41e-4754-a71a-d8200d9b0ebe,844078b0-8358-4377-971f-ac0836610139 | ,, | https://web.fulcrumapp.com/photos/view?photos=e502f0bf-53c2-4cb1-a50b-77dc4cb59cbb%2Cf75d2e9a-b41e-4754-a71a-d8200d9b0ebe%2C844078b0-8358-4377-971f-ac0836610139 | Concrete | Grout Hole,Radial Joint | Leaks |  | Grout hole and Radial Joint
e94d5682-40db-4bbd-b8af-25897f458f62 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 21 | -20.3155 | 118.5805 | POINT (118.5805099258431 -20.31553469455771) | 2025-07-27 10:00:26 AEST | 2025-07-30 00:13:08 AEST | 30011704-user5@smec.com | james.stone@smec.com | 3 | 3 O’Clock position |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete drilled hole , to patch grout | [24 empty] | BP |  | Drill hole concrete chloride test hole I. July 2025 To patch with grout. |  | no |  | yes | To fill 20 mm hole with grout | e10cf5c7-dc80-44c0-88b7-84733e33947e |  | https://web.fulcrumapp.com/photos/view?photos=e10cf5c7-dc80-44c0-88b7-84733e33947e | Concrete |  | Test Hole
7fbfc3d9-efaf-4b5d-9b73-03d86c53982b | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 05:48:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 31 | 11 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 69063 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.3805 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 31, 11 o'clock. Concrete Shell Segment. |  |  |  | Circle joint has Grout Repair Crack - Shrinkage Crack. |  | Circle joint has Grout Repair Crack - Shrinkage Crack. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Cracks such as this in location anchor grout pads are not considered a significant defect | no | yes |  | no |  | 17ecac67-9f2c-4626-8312-fe2b1ca3961f,216c1312-6328-4933-8e87-de87eee37aaf | , | https://web.fulcrumapp.com/photos/view?photos=17ecac67-9f2c-4626-8312-fe2b1ca3961f%2C216c1312-6328-4933-8e87-de87eee37aaf | Concrete | Circular Joint | Crack
1710c6d4-61e0-4c8a-a7ed-19479dfba14e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:02:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 31 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85840 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 31, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no | P3 | yes | Priority and risk to be downgraded | 567a6403-454e-4860-ad56-d42c98f8c972,594689d4-5983-44c1-8d1c-7f6d0d07aa1e | , | https://web.fulcrumapp.com/photos/view?photos=567a6403-454e-4860-ad56-d42c98f8c972%2C594689d4-5983-44c1-8d1c-7f6d0d07aa1e | Concrete | Circular Joint | Drummy
42f1d22b-f753-4f54-8291-c5813db7c249 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 11:46:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 32 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26794 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 32, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | BP |  | Circumference seam sealed joint has salt build up.Low risk | no | yes |  | yes |  | 147dbef6-359c-43c4-badd-5812b8d2dabb,3f42379c-0473-47ed-99d9-2ee726575e3b | , | https://web.fulcrumapp.com/photos/view?photos=147dbef6-359c-43c4-badd-5812b8d2dabb%2C3f42379c-0473-47ed-99d9-2ee726575e3b | Concrete | Circular Joint | Leaks |  | Not reinforcement
32e472ef-d0fe-4665-a056-a1128d2c943e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:08:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 34 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27133 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 34, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment drummy concrete over an area of 250mm x 250mm. |  | Concrete shell segment drummy concrete over an area of 250mm x 250mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Break out loose and damaged concrete. Engineer to assess damage to reinforcement and remediation required. All areas of damaged concrete shall be replaced with high strength concrete patch repairs including embedment of galvanic Cathodic Protection (CP) anodes. Corroded reinforcement that has not been removed shall be thoroughly cleaned of all corroded material. Where corroded reinforcement has been removed it should be replaced by welding a new length of N grade reinforcement of the same diameter to the remaining undamaged reinforcing bar. Or replacing the damaged bar with a new N grade bar of the same diameter as the removed bar. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no | P4 | yes | Priority and risk to be downgraded | a4e79f0f-a22d-432c-8aca-41b9f9b5e44e,b9161e4d-aa96-47a5-b175-7a23b85150c5 | , | https://web.fulcrumapp.com/photos/view?photos=a4e79f0f-a22d-432c-8aca-41b9f9b5e44e%2Cb9161e4d-aa96-47a5-b175-7a23b85150c5 | Concrete | Circular Joint | Drummy |  | Circular Joint - Not reinforcement
e0d42ab3-f475-4964-a511-03c62b182c63 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 11:45:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 35 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85842 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 35, 4 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | 50mm diameter hole on concrete shell segment. |  | 50mm diameter hole on concrete shell segment. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor - no further deterioration noticed from last inspection. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | AA BP |  | Previous hole in concrete surface | no | yes |  | no |  | b68f5104-6016-4a87-8373-da558181fe70,5e1e81b1-0573-4855-91b6-dda82f664aa8 | , | https://web.fulcrumapp.com/photos/view?photos=b68f5104-6016-4a87-8373-da558181fe70%2C5e1e81b1-0573-4855-91b6-dda82f664aa8 | Concrete
d3186fe8-24a0-4760-8484-dbb066413850 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 11:51:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 36 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26795 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 36, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | Working at Heights | Scheduled Maintenance Competent Supervisor | AA |  | Active leaking still present priority medium | yes | yes |  | no |  | 0ceadfff-8b82-45ba-90eb-6ca6982cbb15,d0090442-116a-45e1-8de5-394873aab1b8,08aae027-4327-4a4c-9201-f348976270e5 | ,, | https://web.fulcrumapp.com/photos/view?photos=0ceadfff-8b82-45ba-90eb-6ca6982cbb15%2Cd0090442-116a-45e1-8de5-394873aab1b8%2C08aae027-4327-4a4c-9201-f348976270e5 | Concrete | Grout Hole | Leaks |  | Not reinforcement
96b06505-3f42-4a94-94be-8eae1678b3de | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:13:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 36 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27137 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 36, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment drummy concrete over an area of 800mm x 500mm and grouting drummy over an area of 800mm x 550mm. |  | Concrete shell segment drummy concrete over an area of 800mm x 500mm and grouting drummy over an area of 800mm x 550mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Spall to be treated | no | yes |  | no |  | c17e1768-1cd2-4586-a6c0-cab8388ffa43,90e45305-359a-446e-8165-b03d791c811a | , | https://web.fulcrumapp.com/photos/view?photos=c17e1768-1cd2-4586-a6c0-cab8388ffa43%2C90e45305-359a-446e-8165-b03d791c811a | Concrete | Radial Joint | Drummy,Surface Damage |  | Not reinforcement - Radial Joint
f2261ef7-ab7b-4cb7-b6ed-3be2136d7242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 11:58:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 37 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41937 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 37, 7 o'clock. Chloride ingress Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | A.Acero BP |  | This defect appears to come from 37-9 O’Clock. Active leak salt buildup. Medium risk. | no | yes |  | no |  | 2ed79450-3592-46c3-b109-d5fd5d509b48,bfc851af-aeb5-4ae3-9090-4a6ac9bd3d07 | , | https://web.fulcrumapp.com/photos/view?photos=2ed79450-3592-46c3-b109-d5fd5d509b48%2Cbfc851af-aeb5-4ae3-9090-4a6ac9bd3d07 | Concrete | Grout Hole | Leaks
a84fe528-8a52-4fb2-8cdc-a7c2ab1579c8 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:14:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 37 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41936 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 37, 9 o'clock. Chloride ingress inside concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. - Condition rating 5. |  | Grout injection hole has Leak Active at time of inspection. - Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | A.Acero BP |  | No change leak still active. Medium risk | no | yes |  | yes |  | e09099f4-96af-4e21-b13e-ccd619954aa0,980af16f-ffb4-4903-b932-f4973a1052fe | , | https://web.fulcrumapp.com/photos/view?photos=e09099f4-96af-4e21-b13e-ccd619954aa0%2C980af16f-ffb4-4903-b932-f4973a1052fe | Concrete | Grout Hole | Leaks
944aa3dc-3761-4f16-8bdf-36e9299ced31 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:16:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 38 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41938 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 38, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Inactive at time of inspection. |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | Defect not visible, suggest inactive and obscured by dirt | no | yes |  | no |  | 3fe707fe-b895-42fb-813c-23c54f349cc2,009e8891-71a2-4c2d-9057-cece436eab37,4bdc9ec1-04ce-464a-b4d1-13801d8ad6fe,aa695c81-7d5d-4684-b584-83ad4a01cd09 | ,,, | https://web.fulcrumapp.com/photos/view?photos=3fe707fe-b895-42fb-813c-23c54f349cc2%2C009e8891-71a2-4c2d-9057-cece436eab37%2C4bdc9ec1-04ce-464a-b4d1-13801d8ad6fe%2Caa695c81-7d5d-4684-b584-83ad4a01cd09 | Concrete | Grout Hole | Leaks |  | Grout Hole note Circular Joint
d926d0e6-cf18-4e37-99ed-76a3a87ff7dd | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:23:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 39 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27142 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 39, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment drummy concrete over an area of 500mm x 250mm and localised concrete spalling of size 100mm x 200mm. |  | Concrete shell segment drummy concrete over an area of 500mm x 250mm and localised concrete spalling of size 100mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | A.Acero |  | No Change | no | no |  | no |  | 851cf4cb-b0e6-404a-865e-c41583d71788,c759d1e6-5767-449f-85ab-6ae795f47275 | , | https://web.fulcrumapp.com/photos/view?photos=851cf4cb-b0e6-404a-865e-c41583d71788%2Cc759d1e6-5767-449f-85ab-6ae795f47275 | Concrete | Circular Joint | Drummy,Surface Damage |  | Circular Joint - Not reinforcement
d2a3b978-447c-44da-89d8-cc861c987adb | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:56:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 39 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41886 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 39, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350 mm x 150 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350 mm x 150 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS | [5 empty] | yes | This is a duplicate defect entry, to be deleted |  |  |  | Concrete | Circular Joint | Drummy
ff91313f-39b8-4589-9a7a-ed54db9a9db9 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 05:50:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 41 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69066 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 41, 1 o'clock. Concrete Shell Segment - Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | AA |  | Grout injection hole still present | no | yes |  | no |  | 51bd2c66-7b34-47f5-aafd-0bd7ff2237e3,08e3cf9c-feb2-463d-8a40-3c32a9f838e8 | , | https://web.fulcrumapp.com/photos/view?photos=51bd2c66-7b34-47f5-aafd-0bd7ff2237e3%2C08e3cf9c-feb2-463d-8a40-3c32a9f838e8 | Concrete | Grout Hole | Leaks |  | Not reinforcement
16753271-57e9-4d5c-8f31-9edca63f0118 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:30:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 41 | 10 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69064 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 41, 10 o'clock. Concrete Shell Segment. - Hydrophyllic Joint Seal - Circle Joint | Shear failure of bolt | Shear failure of bolt |  | Joint seal (Circle joint) has Leak - Active at time of inspection. |  | Joint seal (Circle joint) has Leak - Active at time of inspection. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | A.Acero |  | No change - stalatile building u. Sample collected risk medium | no | no |  | no |  | 8883205d-1ea2-4640-956d-0b703a792b81,6f7afc6d-77f4-4ab0-814d-2ee08a3a2003 | , | https://web.fulcrumapp.com/photos/view?photos=8883205d-1ea2-4640-956d-0b703a792b81%2C6f7afc6d-77f4-4ab0-814d-2ee08a3a2003 | Concrete | Circular Joint | Leaks |  | Not reinforcement
115b0a2b-d1fb-4d9f-84e9-499d97f8f539 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:26:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 41 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69077 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 41, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has Cracking - up to 0.5 mm in width at corner of shell segment. Spalling occurring at crack location. |  | Concrete shell segment has Cracking - up to 0.5 mm in width at corner of shell segment. Spalling occurring at crack location. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA |  | Micro crack present priority low | [5 empty] | c69ac7e5-4fe6-4eb5-bf39-13564b5d3e17 |  | https://web.fulcrumapp.com/photos/view?photos=c69ac7e5-4fe6-4eb5-bf39-13564b5d3e17 | Concrete | Corner | Crack,Surface Damage
bc04c14e-29c7-4203-88ba-7ed1b83884cd | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:21:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 41 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85845 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 41, 7 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 250mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | yes | yes |  | yes | Priority and risk to be downgraded | 66013d1d-477b-4f76-80ba-3a1e2ec79552,c2d1521f-3322-4387-aa63-52addeb30542 | , | https://web.fulcrumapp.com/photos/view?photos=66013d1d-477b-4f76-80ba-3a1e2ec79552%2Cc2d1521f-3322-4387-aa63-52addeb30542 | Concrete | Circular Joint | Drummy
a3b1601f-0f5a-48de-b90b-0d84fce6e195 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 05:54:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 41 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26796 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 41, 9 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | A.Acero |  | Stalactite building up . Continuation of deffect 41-10 risk - medium | no | no |  | no |  | 45b2a4da-8c19-4ff4-933e-999a7999a018,c17e32ff-ea48-45bc-9b0d-4215c49d8733 | , | https://web.fulcrumapp.com/photos/view?photos=45b2a4da-8c19-4ff4-933e-999a7999a018%2Cc17e32ff-ea48-45bc-9b0d-4215c49d8733 | Concrete | Circular Joint | Leaks |  | Not reinforcement
af2c465b-8e65-446d-9137-5e7bb38ac640 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:24:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 44 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26797 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 44, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 83d13c09-ab64-4b15-872b-e84fe58a08fe,18756f34-5407-4618-9db1-6ba735354a39,4c9e4591-108b-4bd4-812b-59afd1d10b36 | ,, | https://web.fulcrumapp.com/photos/view?photos=83d13c09-ab64-4b15-872b-e84fe58a08fe%2C18756f34-5407-4618-9db1-6ba735354a39%2C4c9e4591-108b-4bd4-812b-59afd1d10b36 | Concrete | Reinforcement | Drummy,Leaks |  | Not reinforcement
143f5c06-9626-434c-9cd9-3e1f660d8373 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:36:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 46 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26798 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 46, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | BP |  | Existing condition, inactive leak behind channel behind steel support bracket. Low risk | no | yes |  | yes |  | 6b179a76-c691-4fd5-b800-5ad76e7b1598 |  | https://web.fulcrumapp.com/photos/view?photos=6b179a76-c691-4fd5-b800-5ad76e7b1598 | Concrete,Steel | Reinforcement | Leaks |  | Not reinforcement
0fe2650e-2584-4b90-a5e3-1cf57fe70c8f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 10:33:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 47 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41895 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 47, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | remediate as per BHP concrete procedure | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | AC BP |  | Joint Circumferential joint 47, 48 deeper alignment. Grout covered | no | yes |  | no |  | efd1e213-2e9d-46a2-9cc4-f69f9cfa3c66,181de8d8-c7eb-4fc4-8a37-1cb1094858de,5d0a197c-4aa0-40db-b3db-d0eb05ba8de1,4d30c096-b648-428d-8d62-e08d740f278c | ,,, | https://web.fulcrumapp.com/photos/view?photos=efd1e213-2e9d-46a2-9cc4-f69f9cfa3c66%2C181de8d8-c7eb-4fc4-8a37-1cb1094858de%2C5d0a197c-4aa0-40db-b3db-d0eb05ba8de1%2C4d30c096-b648-428d-8d62-e08d740f278c | Concrete | Circular Connection,Circular Joint | Drummy
28316751-8de6-4c86-91c9-bd4e7c968072 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:34:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 47 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99523 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 47, 9 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 200 mm x 200 mm |  | Grout Delamination / Drummy Grout at circle joint over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | A.Acero |  | No change. Issue continues risk low | no | no |  | no |  | a2eac470-bcce-4779-bb14-2ec8b1ddfa48 |  | https://web.fulcrumapp.com/photos/view?photos=a2eac470-bcce-4779-bb14-2ec8b1ddfa48 | Concrete | Circular Joint | Drummy
d36b435e-176a-4318-afe2-704509881880 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:31:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 48 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27395 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 48, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 600mm x 600mm. |  | Concrete shell segment has drummy concrete over an area of 600mm x 600mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AC BP |  | Spalling is larger than typical delam grout pad. Parent concrete is affected. This should be treated. | no | yes |  | no |  | d24ab333-0cff-43b8-973a-bfa16a23bb97,bb2122d9-92e7-4ccb-b7d0-9943ea437e2a,c1766210-0a1e-4109-ae1d-df32805cfeda,642c2038-d25a-4b63-b6a9-0ec6b991e8cd | ,,, | https://web.fulcrumapp.com/photos/view?photos=d24ab333-0cff-43b8-973a-bfa16a23bb97%2Cbb2122d9-92e7-4ccb-b7d0-9943ea437e2a%2Cc1766210-0a1e-4109-ae1d-df32805cfeda%2C642c2038-d25a-4b63-b6a9-0ec6b991e8cd | Concrete | Circular Joint | Drummy,Surface Damage |  | Circular Joint - Not reinforcement
ca0be67e-038b-483c-8e0a-22b9064ac50d | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:08:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 48 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99524 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 48, 8 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 150 mm x 150 mm |  | Grout Delamination / Drummy Grout at circle joint over an area of 150 mm x 150 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Reduce priority to P4 | 197380bb-f5cc-46ed-8db3-41c07e41a919,ce4f9743-107d-47d5-9a27-25593b68de39 | , | https://web.fulcrumapp.com/photos/view?photos=197380bb-f5cc-46ed-8db3-41c07e41a919%2Cce4f9743-107d-47d5-9a27-25593b68de39 | Concrete | Circular Joint | Drummy
5de6de83-5739-4813-ad7d-fb2cf157b92b | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:41:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 48 | 8 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 69078 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.5065 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 48, 8 o'clock. Concrete Shell Segment. |  |  |  | Grout Delamination / debonding at radial segment bolted joints |  | Grout Delamination / debonding at radial segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This is a duplicate |  | no |  | yes | Delete duplicate |  |  |  | Concrete | Circular Joint | Drummy |  | Duplicate - Remove
d9c7e13e-6abd-42ba-9105-ab1c7b8a66eb | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:43:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 48 | 8 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 69079 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.508 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 48, 8 o'clock. Concrete Shell Segment. |  |  |  | Grout Delamination / debonding at radial segment bolted joints |  | Grout Delamination / debonding at radial segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No defect noted here. | no | no |  | yes | Defect not found. Consider deleting. |  |  |  | Concrete | Circular Joint | Drummy
615b9232-d5a9-46c0-bb03-35440f368438 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 05:59:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 49 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42489 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 49, 11 o'clock. Concrete Shell Segment. Circle Joint | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at circle seal joint has Leak - Active at time of inspection. Condition rating 5. |  | Concrete shell segment at circle seal joint has Leak - Active at time of inspection. Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | Leak through circle and Radial joint | no | yes |  | no |  | d391c50f-1aef-4bd0-9c5f-45ed2b40fb78,b92e3758-2851-4fab-9ba7-accdf753165c | , | https://web.fulcrumapp.com/photos/view?photos=d391c50f-1aef-4bd0-9c5f-45ed2b40fb78%2Cb92e3758-2851-4fab-9ba7-accdf753165c | Concrete | Circular Joint,Radial Joint | Leaks
1879fef6-78c2-4a05-9d19-abdc343b9c25 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:42:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 49 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99525 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 49, 12 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 300 mm x 200 mm |  | Grout Delamination / Drummy Grout at radial joint over an area of 300 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | BP |  | Patch grouting drummy. Low risk | [5 empty] | 02ddb68a-93ad-44e9-95c2-ae5f12a59c44,1035e897-6b73-435b-a916-8cc335ee600f | , | https://web.fulcrumapp.com/photos/view?photos=02ddb68a-93ad-44e9-95c2-ae5f12a59c44%2C1035e897-6b73-435b-a916-8cc335ee600f | Concrete | Radial Joint | Drummy
3b4147b3-654f-4372-8e6e-da43f89584a7 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:52:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 49 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27396 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 49, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 300mm x 150mm. |  | Concrete shell segment has drummy concrete over an area of 300mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Spalling on adjacent segment has expanded to this one. This is nk longer drummy and is an active spall. This should be treated. | no | yes |  | no |  | ae678730-1ae3-4224-a520-202bbc72ec60,da5e99ee-6cab-47e7-80b9-9d7e1d19ba09,e07a30fc-3e05-44b1-893f-64c285db46c5 | ,, | https://web.fulcrumapp.com/photos/view?photos=ae678730-1ae3-4224-a520-202bbc72ec60%2Cda5e99ee-6cab-47e7-80b9-9d7e1d19ba09%2Ce07a30fc-3e05-44b1-893f-64c285db46c5 | Concrete | Circular Joint | Drummy,Surface Damage |  | Circular Joint - Not reinforcement
dbb410b4-4a19-44e5-b3ba-2a6d39793e3f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:48:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 49 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41896 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 49, 8 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | remediate as per BHP concrete procedure | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | A.Acero |  | Defect is located on ring 50, not 49. Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Change ring number to 50 | 389062cf-68e8-4422-b641-1f4bac9222cb,172c90a0-6ce5-453b-8d26-4fe14492efce | , | https://web.fulcrumapp.com/photos/view?photos=389062cf-68e8-4422-b641-1f4bac9222cb%2C172c90a0-6ce5-453b-8d26-4fe14492efce | Concrete | Circular Joint | Drummy
88db7b21-6975-4182-b85a-a687d013620a | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 06:02:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 50 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85847 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 50, 10 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - active at time of inspection. - Condition rating 5 |  | Concrete shell segment at bolted connection penetration has Leak - active at time of inspection. - Condition rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak is active through Radial and circle joint | no | yes |  | no |  | b63ddcf9-d835-4d21-a5a3-47001ac7b236,6be264c3-869b-4c1f-919f-2fea14a4064f | , | https://web.fulcrumapp.com/photos/view?photos=b63ddcf9-d835-4d21-a5a3-47001ac7b236%2C6be264c3-869b-4c1f-919f-2fea14a4064f | Concrete | Circular Joint | Leaks
0487282e-bf88-4339-8fc5-19b893d61a30 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:01:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 50 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85848 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 50, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout and drummy concrete over an area of 500mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout and drummy concrete over an area of 500mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Dr |  | Area of drummy concrete has not changed. | yes | yes |  | no |  | 5287e053-161c-48c1-b58f-7ecfefe8f097,b02c9e11-506e-40b6-bf31-a397ba75f97f,6cf73877-517a-4d7a-b230-fd10f522a7d5 | ,, | https://web.fulcrumapp.com/photos/view?photos=5287e053-161c-48c1-b58f-7ecfefe8f097%2Cb02c9e11-506e-40b6-bf31-a397ba75f97f%2C6cf73877-517a-4d7a-b230-fd10f522a7d5 | Concrete | Circular Joint | Drummy
c657af51-ae9f-4877-bc6b-f30f9f77ec4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 06:05:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 50 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 85850 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 50, 12 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolts have Level 4 Medium High Corrosion. Steel channel support bracket has Level 4 Major Corrosion up to 50% coverage. |  | Channel anchor bolts have Level 4 Medium High Corrosion. Steel channel support bracket has Level 4 Major Corrosion up to 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. 3. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak behind bracket is causing corrosion | no | yes |  | no |  | 4347583f-11eb-4884-8a00-767f5baa24a6,c48f76c1-7ef6-4e9a-b1e8-321d23ade35c,505a4432-210f-462f-a497-8510d2c59145,b1d80fb0-f43b-4a13-8cf8-998046819e71 | ,,, | https://web.fulcrumapp.com/photos/view?photos=4347583f-11eb-4884-8a00-767f5baa24a6%2Cc48f76c1-7ef6-4e9a-b1e8-321d23ade35c%2C505a4432-210f-462f-a497-8510d2c59145%2Cb1d80fb0-f43b-4a13-8cf8-998046819e71 | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks
1dc02521-fc42-4fb5-b212-f62ae80aad1a | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:48:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 50 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41939 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Structure, Ring 50, 7 O'Clock, Concrete Element | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Active Leak Shell Segment Penetration behind bracelet. - Condition Rating 5. |  | Active Leak Shell Segment Penetration behind bracelet. - Condition Rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | AC BP |  | No defect , consider removing entry | no | no |  | yes | Defect not seen, consider deleting | aa239e71-34f0-4977-9c77-3572d4876692 |  | https://web.fulcrumapp.com/photos/view?photos=aa239e71-34f0-4977-9c77-3572d4876692 | Concrete |  | Leaks
1d491ce6-3b3f-46f2-88ea-8358a606337a | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:41:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 52 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27400 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 52, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 250mm x 250mm. |  | Concrete shell segment has drummy concrete over an area of 250mm x 250mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | AA |  | Drummy concrete risk low | [5 empty] | 030c2f33-bfac-431b-bec6-281f2f9cca8f,cf242fb2-0cee-47b6-b9b1-06311aa9a4d6 | , | https://web.fulcrumapp.com/photos/view?photos=030c2f33-bfac-431b-bec6-281f2f9cca8f%2Ccf242fb2-0cee-47b6-b9b1-06311aa9a4d6 | Concrete | Circular Joint | Drummy |  | Circular Joint Not reinforcement
8b323d24-707d-4a58-905b-753f200f867f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:41:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 52 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27398 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 52, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 250mm x 250mm. |  | Concrete shell segment has drummy concrete over an area of 250mm x 250mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA |  | Drummy concrete risk low | [5 empty] | 408fc1e5-abe7-478d-ad25-d28f2594d622,bd11729b-be76-4cfb-8515-568ef53ffa10 | , | https://web.fulcrumapp.com/photos/view?photos=408fc1e5-abe7-478d-ad25-d28f2594d622%2Cbd11729b-be76-4cfb-8515-568ef53ffa10 | Concrete | Circular Joint,Radial Joint | Drummy |  | Circular and Radial Joint Not reinforcement
7bbdcf2a-3e3c-4288-8d7a-cccc48a0968e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 06:20:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 53 | 10 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99526 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 53, 10 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 200 mm x 200 mm. |  | Grout Delamination / Drummy Grout at radial joint over an area of 200 mm x 200 mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | A.Acero |  | No change | no | yes |  | no |  | 2bf42020-8525-40ce-b728-01a22d75952c |  | https://web.fulcrumapp.com/photos/view?photos=2bf42020-8525-40ce-b728-01a22d75952c | Concrete | Radial Joint | Drummy
fc6cb12c-3abf-42fb-84fe-e169992ac18f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 06:25:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 54 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26801 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 54, 1 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | Leak is active, behind bracket, causing corrosion. This should be treated | no | yes |  | no |  | b3d75579-8b4c-4cc2-a290-1ea68e35df4d,53ea838f-1b3e-46a4-a54d-04ebbdd27ea2,4b6ed047-8f2d-4842-b554-1a467d3c9be7 | ,, | https://web.fulcrumapp.com/photos/view?photos=b3d75579-8b4c-4cc2-a290-1ea68e35df4d%2C53ea838f-1b3e-46a4-a54d-04ebbdd27ea2%2C4b6ed047-8f2d-4842-b554-1a467d3c9be7 | Concrete | Grout Hole,Reinforcement | Leaks
4ed6c3fb-51b0-4889-87c4-866c20047c14 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:47:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 54 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 69080 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 54, 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel bracket has Level 3 - Medium Corrosion up to 25% coverage. |  | Steel channel bracket has Level 3 - Medium Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P3. | injury risk | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | AA |  | Corrosion pf channel bracket present risk medium | no | yes |  | no |  | 1f383807-dda2-44bf-990e-70fe2d5a1c16,e087ab60-0124-496c-b357-fc17ccfe3b5c | , | https://web.fulcrumapp.com/photos/view?photos=1f383807-dda2-44bf-990e-70fe2d5a1c16%2Ce087ab60-0124-496c-b357-fc17ccfe3b5c | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
b6b04f72-f84b-404c-b7d4-9fb2c0fdd347 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 06:26:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 54 | 10 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69081 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 54, 10 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | risk of injury or structure breakdown | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Steelwork Remediation Crew. | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor | SS |  | No change | no | yes |  | no |  | 51ddb580-d73d-4656-9add-5d590c8ce026,6ce506eb-d1bd-466f-adf0-ba47322aa89a | , | https://web.fulcrumapp.com/photos/view?photos=51ddb580-d73d-4656-9add-5d590c8ce026%2C6ce506eb-d1bd-466f-adf0-ba47322aa89a | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
2a1a4c83-8ea4-4dd0-842e-5c33ce02a242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:48:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 54 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27402 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 54, 8 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 500mm x 600mm. |  | Concrete shell segment has drummy concrete over an area of 500mm x 600mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Remediate as per BHP concrete procedure | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | A.Acero |  | No change . Condition of deffect getting worse risk low | no | no |  | no |  | 77eb2c02-36e8-4795-bd3f-e870c948599d,0991c975-a5f4-4f7d-b4b3-a3bae0fcbbb1,034376b1-2ac6-4e8f-b9f6-c8f5a054efae,7e194fef-3452-4d52-b3e8-5c35d4a5c19a,7f8326c3-a552-43e0-aeac-9825c5f8d662 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=77eb2c02-36e8-4795-bd3f-e870c948599d%2C0991c975-a5f4-4f7d-b4b3-a3bae0fcbbb1%2C034376b1-2ac6-4e8f-b9f6-c8f5a054efae%2C7e194fef-3452-4d52-b3e8-5c35d4a5c19a%2C7f8326c3-a552-43e0-aeac-9825c5f8d662 | Concrete | Radial Joint | Drummy |  | RAdial Joint Not reinforcement
dc42b6e6-d96c-47fa-9872-69dd8e367d1d | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:44:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 55 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27404 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 55, 1 & 2 o'clock. Concrete Shell Segment - Radial Joint | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of same size 200mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of same size 200mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | HM |  | Delamination is still present at 1 and 2 o' clock positions. | no | yes |  | no |  | 054fe918-8bcf-4ace-8091-9d3fa2321c85,15598619-cfe3-4def-a8a6-b39c79736847 | , | https://web.fulcrumapp.com/photos/view?photos=054fe918-8bcf-4ace-8091-9d3fa2321c85%2C15598619-cfe3-4def-a8a6-b39c79736847 | Concrete | Radial Joint | Drummy |  | Not reinforcement
fb38130e-79ad-4e0c-9634-5c5416702491 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:18:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 55 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26802 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 55, 2 &3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Inactive at time of inspection. |  | Joint seal (Circle joint) has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | Leak is inactive at the time of inspection. | no | yes |  | yes | This should be at position 3 o' clock | 68ff2951-be1c-4b47-90c3-43af9ae5d261,fcecca29-1e4d-4756-9b98-fb4c04f0ed8f,7c684ccd-1e9e-45bd-9da8-86f28806cbb3,f6b4bdae-9826-4a64-9953-1d527b2547f9 | ,,, | https://web.fulcrumapp.com/photos/view?photos=68ff2951-be1c-4b47-90c3-43af9ae5d261%2Cfcecca29-1e4d-4756-9b98-fb4c04f0ed8f%2C7c684ccd-1e9e-45bd-9da8-86f28806cbb3%2Cf6b4bdae-9826-4a64-9953-1d527b2547f9 | Concrete | Circular Joint | Leaks |  | Not reinforcement
7c684d64-27c3-45fe-8055-604ab7d0efad | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 12:55:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 55 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 42006 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44046.4781 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 55, 2 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | BP |  | Some minor cracks .Low risk | no | yes |  |  |  | 362e8b67-3148-4797-9922-a8df70b20429 |  | https://web.fulcrumapp.com/photos/view?photos=362e8b67-3148-4797-9922-a8df70b20429 | Concrete | Circular Joint | Crack |  | Circular Joint
81fa51db-e471-48a1-b849-ddb41b2dde63 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:15:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 56 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26904 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Structure, Ring 056,7 O'Clock, Concrete Element, New Defect 2017 | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Inactive Leak Shell Segment Interface |  | Inactive Leak Shell Segment Interface | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak at interface of shell segments. Carry out leak seal in accordance with approved remediation work scope. | Engineering repair method and specification required. Concrete remediation crew. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | AC BP |  | Defect not visible, suggest still inactive and obscured by dirt | no | no |  | yes | Priority and risk to be downgraded | f27f1438-08c6-4c9c-a4cf-88a659f63301,bc6fc61f-e969-45a5-98d9-e6966a6cb02a,d0640ba1-4fc0-48ff-835c-2b436768794b | ,, | https://web.fulcrumapp.com/photos/view?photos=f27f1438-08c6-4c9c-a4cf-88a659f63301%2Cbc6fc61f-e969-45a5-98d9-e6966a6cb02a%2Cd0640ba1-4fc0-48ff-835c-2b436768794b | Concrete | Radial Joint | Leaks |  | Radial Joint Not reinforcement
8473e6e7-a930-43d7-9eda-59a2181c7150 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:17:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 57 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85852 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 57, 7 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | AC BP |  | Defect not sighted at time of inspection | [5 empty] | 5dfd43a5-a7c9-4a8a-8edc-a6a9644438df |  | https://web.fulcrumapp.com/photos/view?photos=5dfd43a5-a7c9-4a8a-8edc-a6a9644438df | Concrete | Circular Joint | Drummy
8b35cc0f-b2c2-455e-97f2-4a3e3872e4d2 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:42:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 58 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 85899 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 58, 2 & 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Two channel anchor bolts are missing. |  | Two channel anchor bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | HM |  | Anchor bolts still missing | no | yes |  | no |  | 94baee6d-104e-4d9e-9fc5-0de7dbabf30b,538018ee-16c0-4b90-af69-28df727d3cb8 | , | https://web.fulcrumapp.com/photos/view?photos=94baee6d-104e-4d9e-9fc5-0de7dbabf30b%2C538018ee-16c0-4b90-af69-28df727d3cb8 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
ea55fece-29e8-49ff-a09f-2d07fd6e8093 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 11:34:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 59 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85853 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 59, 7 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 400mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 400mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | AC BP |  | Defect remain unchanged | no | yes |  | no |  | 13b28973-ea6e-4042-9151-a10477849ec8,8dc9cf0d-e027-4e15-9410-5dd6b56b2762 | , | https://web.fulcrumapp.com/photos/view?photos=13b28973-ea6e-4042-9151-a10477849ec8%2C8dc9cf0d-e027-4e15-9410-5dd6b56b2762 | Concrete | Circular Joint | Drummy
cc192bcb-d96b-426e-93f1-c7aec99b401b | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 21 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 13:03:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 60 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26803 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | o'clock. Concrete Shell Segment. And active leaking | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint seal has Leak Inactive at time of inspection. |  | Radial joint seal has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | AA |  | Drummy concrete and active leaking present spreading down towards 3 o’clock | [5 empty] | 27180985-7d73-4a4f-bbbf-b18964caf6f3,0814d7ca-1173-43b5-838e-9e49ff0fe9f9 | , | https://web.fulcrumapp.com/photos/view?photos=27180985-7d73-4a4f-bbbf-b18964caf6f3%2C0814d7ca-1173-43b5-838e-9e49ff0fe9f9 | Concrete | Radial Joint | Drummy,Leaks |  | Not reinforcement
e39fbf86-3347-460e-9cad-7bf875633957 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17 |  |  |  | 2025-07-24 14:47:13 AEST | 2025-07-27 13:14:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 33 | 8 | [17 empty] | Corrosion - Connection | [16 empty] | O’ Clock Active leaking | [18 empty] | Yes | [5 empty] | AA |  | Wetness and salt building up. May eventually cause leaking risk low |  | yes |  | yes |  | 9b3e4028-918c-41ff-97d8-854fa8686f63,d6a01c22-aa13-49e1-afe7-0763ddbb3450 | , | https://web.fulcrumapp.com/photos/view?photos=9b3e4028-918c-41ff-97d8-854fa8686f63%2Cd6a01c22-aa13-49e1-afe7-0763ddbb3450 | Concrete | Grout Hole | Leaks |  | Grout Hole
69848ba7-5067-473c-a0a6-aabde7f63f4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 16 |  |  |  | 2025-07-25 09:35:00 AEST | 2025-07-27 13:07:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 31 | 6 O’Clock Conveyor support base |  |  | Conveyor -walkway support base | [14 empty] | Corrosion - Connection |  |  | Medium | [30 empty] | Maintenance re coating |  | Yes |  | No |  |  |  | AC BP |  | Low risk, heavy corrosion base plate and fixings. Delaminated beam base. |  |  |  | yes |  | a8c7fefb-76f0-4161-8aca-e68eb5749111,7a214d0c-f375-48d8-bc5a-ac29dd2f9e7e | , | https://web.fulcrumapp.com/photos/view?photos=a8c7fefb-76f0-4161-8aca-e68eb5749111%2C7a214d0c-f375-48d8-bc5a-ac29dd2f9e7e | Steel | Walkway Support | Corrosion-Heavy,Drummy
eb004917-0346-4551-bfbc-d374593080f4 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 16 |  |  |  | 2025-07-25 09:53:45 AEST | 2025-07-25 09:57:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 35 | 7 O’Clock Drummy concrete 200mm X 200mm | [19 empty] | 2 | [33 empty] | Yes | [5 empty] | AC BP |  | Drummy concrete surface | [5 empty] | 77b1a188-ea20-4d55-90d8-19873545b021,7d84c3e0-f369-4ecf-971d-bf55b96ff3de | , | https://web.fulcrumapp.com/photos/view?photos=77b1a188-ea20-4d55-90d8-19873545b021%2C7d84c3e0-f369-4ecf-971d-bf55b96ff3de | Concrete | Radial Joint | Drummy |  | Radial Joint
77df86a5-4baf-4488-a554-e60750e3e57c | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 16 |  |  |  | 2025-07-25 10:01:30 AEST | 2025-07-25 10:08:17 AEST | 30011704-user5@smec.com | james.stone@smec.com | 39 | 5 O’Clock Steel walkway circular support frame end | [19 empty] | 3 | [31 empty] | Remedial action decorating and replace bolt nut |  | Yes | [5 empty] | AC BP |  | Corroded end part of circular bracket walkway |  | yes |  | yes |  | 96a34f6b-d623-4bed-9ece-902cb40af92b,bdfb55ee-93b0-4296-8822-4218600a001e,5d6add77-90a8-4780-bf44-bcacb468db92 | ,, | https://web.fulcrumapp.com/photos/view?photos=96a34f6b-d623-4bed-9ece-902cb40af92b%2Cbdfb55ee-93b0-4296-8822-4218600a001e%2C5d6add77-90a8-4780-bf44-bcacb468db92 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support
a0f66257-212e-40cf-9beb-1edc3c3a43f0 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 16 |  |  |  | 2025-07-25 11:17:12 AEST | 2025-07-25 11:23:45 AEST | 30011704-user5@smec.com | james.stone@smec.com | 56 | 6 O’Clock conveyor & walkway support base |  |  | Base Plate beam thinning | [14 empty] | Corrosion - Connection |  | 4 | [31 empty] | Remove corrosion and remediste steel loss | Weld new plate, blast & recoat epoxy | [6 empty] | AC BP |  | Metal thinning, section loss |  | yes |  | yes |  | d4ae3a4e-8c26-4106-9dc5-890fa085df98 |  | https://web.fulcrumapp.com/photos/view?photos=d4ae3a4e-8c26-4106-9dc5-890fa085df98 | Steel | Walkway Support | Corrosion-Heavy
5ab12c32-9958-4b96-adad-45aeb42722da | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 16 |  |  |  | 2025-07-25 11:41:36 AEST | 2025-07-25 11:50:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 64 | 6 O’Clock, Conveyor and walkway support beam |  |  | Conveyor and Walkway support beam | [16 empty] | 3 | [39 empty] | AC BP |  | Delamination of beam, section loss. Cracked concrete Crete base |  | yes |  | yes |  | 42b3e9ab-005a-470e-b470-2247ba4baae1,b6c5d5e7-3f85-4ac7-bd98-f783c67075b5,81bbac93-4a1a-455b-ad29-2fd0372dd571,c2781dea-f321-4bf1-8d5f-b00e75ffe143 | ,,, | https://web.fulcrumapp.com/photos/view?photos=42b3e9ab-005a-470e-b470-2247ba4baae1%2Cb6c5d5e7-3f85-4ac7-bd98-f783c67075b5%2C81bbac93-4a1a-455b-ad29-2fd0372dd571%2Cc2781dea-f321-4bf1-8d5f-b00e75ffe143 | Concrete | Walkway Support | Corrosion-Heavy,Crack |  | not drummy
ba77adb3-6653-4e15-b56e-d41422bdd498 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 13 |  |  |  | 2025-07-27 11:51:42 AEST | 2025-07-27 11:58:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 36 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26795 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  |  | Other | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Severity Level 1 |  | Likely (Failure within 2 Years) | Possible (Failure within 5 Years) |  | Segment getting Active leaking | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 | [5 empty] | No | Off-Line | Yes | Walkway |  |  | AA |  | Active leaking still present priority medium | yes | yes |  | no |  | 37349411-f718-4e21-b757-b97b1eec81c2,d607b358-ec33-4f3e-bc14-58e56a689996 | , | https://web.fulcrumapp.com/photos/view?photos=37349411-f718-4e21-b757-b97b1eec81c2%2Cd607b358-ec33-4f3e-bc14-58e56a689996 | Concrete | Radial Joint | Leaks |  | Radial Joint - Not reinforcement
c0fd50df-219d-4d7c-8425-89746419eb7c | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 13 |  |  |  | 2025-07-27 12:34:57 AEST | 2025-07-27 12:36:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 48 | 1 | [34 empty] | Non Active leaking at grout hole | [24 empty] | AA |  | Non Active leaking at grout hole | [5 empty] | b6e34c9a-8871-4772-9aed-013e3a8ef475,01c35591-18c0-44be-9023-e3946953064d | , | https://web.fulcrumapp.com/photos/view?photos=b6e34c9a-8871-4772-9aed-013e3a8ef475%2C01c35591-18c0-44be-9023-e3946953064d | Concrete | Grout Hole | Leaks
63bed447-87fe-41b6-a9fd-208ffd627a4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 13 |  |  |  | 2025-07-27 12:53:19 AEST | 2025-07-27 12:55:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 58 | 3 | [34 empty] | O ‘clock missing bolt | [24 empty] | AA |  | Missing bolt beam supports 3 runs pf cable ladder reticulation risk low | [5 empty] | 257fd7cc-a7bd-4107-b777-34e83de675d8,fbb6f71b-f1ab-403b-8f9b-b5535db1b5ec,4670f672-a78b-4f87-a363-99c9199daf73 | ,, | https://web.fulcrumapp.com/photos/view?photos=257fd7cc-a7bd-4107-b777-34e83de675d8%2Cfbb6f71b-f1ab-403b-8f9b-b5535db1b5ec%2C4670f672-a78b-4f87-a363-99c9199daf73 | Steel | Channel Bracket-Bolt | Missing |  | Channel Bracket - Bolt
b717d79f-a2a2-492f-8c6f-df933bde5096 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 14 | -20.3168 | 118.5821 | POINT (118.5821066301295 -20.31681321804971) | 2025-07-27 12:25:17 AEST | 2025-07-27 12:28:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 38 | 2 |  | Hydrophilic Joint Seal (Circle Joint) | [16 empty] | Edge msurface cracks | [20 empty] | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | [19 empty] | BP |  | Patch repair grout over cracks. Low risk |  | yes |  | yes |  | 98b7576d-ff49-4b59-8b32-95549e6cf4a5 |  | https://web.fulcrumapp.com/photos/view?photos=98b7576d-ff49-4b59-8b32-95549e6cf4a5 | Concrete | Circular Joint | Crack,Drummy
be4b2b48-d06e-479b-a1d2-7fb7b0058785 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 14 | -20.3169 | 118.5822 | POINT (118.5821744436695 -20.31686114122444) | 2025-07-27 12:55:37 AEST | 2025-07-27 12:58:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 55 | 3 O’Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [15 empty] | Concrete Damage due to Cast- In | [41 empty] | BP |  | Drummy repair grout at circumferencial seam. Low risk |  | yes |  | yes |  | fa62baac-6192-4964-8099-c5b35728e9e7,767fc84c-ecad-4ac0-a45d-33d8cb502346 | , | https://web.fulcrumapp.com/photos/view?photos=fa62baac-6192-4964-8099-c5b35728e9e7%2C767fc84c-ecad-4ac0-a45d-33d8cb502346 | Concrete | Circular Joint | Drummy |  | Circualr JHoint
b354854a-efe7-4519-be31-f153b68d4f62 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 6 |  |  |  | 2025-07-30 06:05:38 AEST | 2025-07-30 06:07:24 AEST | 30011704-user5@smec.com | james.stone@smec.com | 50 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85847 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 50, 11 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - active at time of inspection. - Condition rating 5 |  | Concrete shell segment at bolted connection penetration has Leak - active at time of inspection. - Condition rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Separate leak defect from the 10 o'clock one, created to address the leak behind the bracket. | no | yes |  | no |  | e53136b1-bb5f-4bce-9dc3-02e1b4a87c2b,46569f63-4078-4a43-bdda-cef44db6f9ae,a011678b-7c1d-46f6-87ce-c42555051c5c,cec2a071-4cd0-4066-9dec-f48a8efb52de | ,,, | https://web.fulcrumapp.com/photos/view?photos=e53136b1-bb5f-4bce-9dc3-02e1b4a87c2b%2C46569f63-4078-4a43-bdda-cef44db6f9ae%2Ca011678b-7c1d-46f6-87ce-c42555051c5c%2Ccec2a071-4cd0-4066-9dec-f48a8efb52de | Concrete | Circular Joint,Radial Joint,Channel Bracket | Leaks |  | Circular Joint. Radial Joint. Steel Channel Bracket
3614605b-06e6-4abf-a23d-107639bf00dc | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:28:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 61 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26805 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 61, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | Grout hole leak is inactive at the time of inspection. It is possible leak is fixed. | no | yes |  | no |  | a17b6967-5c44-48fd-8071-24df65b5dee9,b1e0b785-e055-446d-b2e1-cc6fd45e9da4 | , | https://web.fulcrumapp.com/photos/view?photos=a17b6967-5c44-48fd-8071-24df65b5dee9%2Cb1e0b785-e055-446d-b2e1-cc6fd45e9da4 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
9590f0e5-2a88-466a-96b6-49c1cc334fc3 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:25:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 62 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85900 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 62, 1 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | HM |  | Concrete has cracked heavily where delamination is present. | yes | yes |  | yes | Priority to be discussed. Possible priority 1. | 94a2063b-9289-4925-b635-6018c1b7b674,77154d75-8f3b-4f51-9466-537520b4ff79 | , | https://web.fulcrumapp.com/photos/view?photos=94a2063b-9289-4925-b635-6018c1b7b674%2C77154d75-8f3b-4f51-9466-537520b4ff79 | Concrete | Circular Joint | Crack,Drummy
5ab0ed21-50c8-4fc2-8234-b6df798bb7a4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:22:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 63 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26807 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 63, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | HM |  | Grout hole leak is inactive at the time of inspection. It is possible leak has been fixed. | no | yes |  | no |  | 3a5d6bf9-646f-4be6-8e5b-417581d0fed6,2f071e7c-afde-4362-80ad-d761f2d4d373 | , | https://web.fulcrumapp.com/photos/view?photos=3a5d6bf9-646f-4be6-8e5b-417581d0fed6%2C2f071e7c-afde-4362-80ad-d761f2d4d373 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
77b78753-0980-44c7-a372-e275a87c8c75 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:21:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 63 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26808 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 63, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel bracket has been removed. |  | Steel channel bracket has been removed. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | HM |  | This defect is incorrect. No steel anchor bracket at this location. | no | yes |  | no |  | 7c964bc2-fcbc-4940-a124-a9a3162fb133 |  | https://web.fulcrumapp.com/photos/view?photos=7c964bc2-fcbc-4940-a124-a9a3162fb133 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
b7f279d0-68d9-4d1b-847f-e57a109679f2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:41:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 66 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26909 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 66, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | Dr |  | Leak is still active at time of inspection. Has caused severe corrosion to steel channel bracket and anchor bolts. Spalling around steel bracket. High priority | yes | no | High | no |  | 316909f7-4fcf-4713-94d2-b18f34dbc0c7,80a0e5d1-407f-4028-a98c-4598d53261e3,3654a9b3-f661-4d8a-b526-3a31756d6b2f | ,, | https://web.fulcrumapp.com/photos/view?photos=316909f7-4fcf-4713-94d2-b18f34dbc0c7%2C80a0e5d1-407f-4028-a98c-4598d53261e3%2C3654a9b3-f661-4d8a-b526-3a31756d6b2f | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Leaks,Surface Damage |  | Not Reinforcement
3b68fd28-61e9-43d5-bc1c-6f23fd9c3d88 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:42:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 66 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 26910 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 66, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - High Corrosion (Severe) up to 5% coverage. Channel anchor bolts have Level 2 Corrosion. |  | Steel channel support bracket has Level 2 - High Corrosion (Severe) up to 5% coverage. Channel anchor bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Corrosion has advanced. Severe corrosion. High priority | yes | no | High |  |  | 981e88ee-fe34-40b5-b40c-3d38a2309f69,f3101b5f-417a-4003-8751-3ea45124ccdf,2bc8a569-7846-468c-a8ec-f6f1d06cb0f5 | ,, | https://web.fulcrumapp.com/photos/view?photos=981e88ee-fe34-40b5-b40c-3d38a2309f69%2Cf3101b5f-417a-4003-8751-3ea45124ccdf%2C2bc8a569-7846-468c-a8ec-f6f1d06cb0f5 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
f5a381ff-a308-4462-beb9-4e508b2d0b44 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 00:10:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 66 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 85854 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 66, 12 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | AA |  | Missing bolt for support Beam. Priority low consider replace missing bols as it supports 3 runs of cable ltray | [5 empty] | d8707eed-2adc-4f8b-bee9-8dc7542c648b,44a188c4-c34e-4219-9031-ff5fe8fa5c28 | , | https://web.fulcrumapp.com/photos/view?photos=d8707eed-2adc-4f8b-bee9-8dc7542c648b%2C44a188c4-c34e-4219-9031-ff5fe8fa5c28 | Steel | Channel Bracket-Bolt | Missing |  | Only bolt
00003620-32b7-4ab2-a9b1-77e071e2f41b | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:16:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 66 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85901 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | HM |  | Bolt still missing. | no | no | 4 | yes | Priority to be downgraded | 330c65c2-79d1-479f-a87b-786517480fea |  | https://web.fulcrumapp.com/photos/view?photos=330c65c2-79d1-479f-a87b-786517480fea | Steel | Channel Bracket-Bolt | Missing |  | only bolt
30554ac0-3f76-4124-8d01-51361082bc64 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:46:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 68 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41941 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 68, 10 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak active at time of inspection Condition rating 5 |  | Grout injection hole has Leak active at time of inspection Condition rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | Dr |  | Repeated twice. | no | no |  | yes | To be removed. Repeated twice. |  |  |  | Concrete | Grout Hole | Leaks
4d28d489-954d-4658-a12d-8478861e2d0d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:45:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 68 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69083 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 68, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete at corner of concrete wall panel over an area of 200mm x 150mm |  | Concrete shell segment has drummy concrete at corner of concrete wall panel over an area of 200mm x 150mm | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | Dr |  | No change. Area of drummy concrete is the same. | no | yes |  |  |  | 76cf9420-1481-46e2-ab2c-0d1f59e71c16,27af9173-6fcb-4dac-88bc-16c48d9d20ce | , | https://web.fulcrumapp.com/photos/view?photos=76cf9420-1481-46e2-ab2c-0d1f59e71c16%2C27af9173-6fcb-4dac-88bc-16c48d9d20ce | Concrete | Corner | Drummy |  | Not reinforcement
e4a6536d-d9d1-4016-bcdb-adae304d3241 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:44:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 68 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26911 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 68, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Supervisor | Dr |  | Leak is still inactive at time of inspection. Ko change. | no | yes |  |  |  | 5b5a73ea-c583-416e-9d6d-b02e67debeb3 |  | https://web.fulcrumapp.com/photos/view?photos=5b5a73ea-c583-416e-9d6d-b02e67debeb3 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
005e5ec3-2f94-4a7b-922e-1e465fb8555d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 11:57:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 68 | 7 O’Clock Position Circumferential seam | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69082 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 68, 8 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | A.Acero BP |  | Stalactite building up circumference seam | yes | no |  | no |  | bddcb216-fade-49f5-a827-308b8df71126,d4a2e6e5-9b55-4bf9-b98e-6f20b83c1f75 | , | https://web.fulcrumapp.com/photos/view?photos=bddcb216-fade-49f5-a827-308b8df71126%2Cd4a2e6e5-9b55-4bf9-b98e-6f20b83c1f75 | Concrete | Circular Connection,Circular Joint | Leaks
5bb7cd8b-5db7-4e59-b416-ee4807339fb5 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:48:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 69 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85860 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 69, 12 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Active leak at grout patch at segment bolted circle joint. |  | Active leak at grout patch at segment bolted circle joint. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak remains active. High priority defect. | no | no |  |  |  | ba974a09-b0ff-4d7d-851d-4c547d9090f3 |  | https://web.fulcrumapp.com/photos/view?photos=ba974a09-b0ff-4d7d-851d-4c547d9090f3 | Concrete | Circular Joint | Leaks
e8f3124e-9dc8-4b41-88aa-630ab7a34f82 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:26:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 69 | 4 | Grout Injection Hole | Grout Injection Hole |  | 85858 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 69, 4 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. Condition rating 5. |  | Grout injection hole has leak - active at time of inspection. Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak is inactive at time of inspection. May have been repaired. Salt deposit present around the injection hole. Medium priority | yes | no | Medium |  |  | 4a53f3bc-01ae-4d70-8811-14c0a1e169cc |  | https://web.fulcrumapp.com/photos/view?photos=4a53f3bc-01ae-4d70-8811-14c0a1e169cc | Concrete | Grout Hole | Leaks
02d065b8-b9b8-4ee9-bcd3-95cf99d10f0f | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:56:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 70 | 10 | Steel Channel Bracket | Steel Channel Bracket |  | 85855 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 70, Consider entry 10 & 12 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | Dr |  | Bolt only missing missing at 10 Clock. | no | no |  | no |  | a5d8cf3b-c42a-442b-a6cc-8c555944b793 |  | https://web.fulcrumapp.com/photos/view?photos=a5d8cf3b-c42a-442b-a6cc-8c555944b793 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
ddeb89ca-5bc0-4d9d-81fa-25404a34053c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 13:25:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 70 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27416 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 50% coverage. |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor - isolated corrosion only. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Likely Likelihood of failure, resulting in a Priority 2. | Loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA BP |  | Corrosion in missing support braket risk low / monitor | [5 empty] | 915b0e52-8414-4ac1-9024-85860751faf8,a5f72209-47f2-413e-8672-ff651cfd472e,c6a989e2-5c82-4fcc-bd4b-38fcb741c153 | ,, | https://web.fulcrumapp.com/photos/view?photos=915b0e52-8414-4ac1-9024-85860751faf8%2Ca5f72209-47f2-413e-8672-ff651cfd472e%2Cc6a989e2-5c82-4fcc-bd4b-38fcb741c153 | Steel | Channel Bracket | Missing
a06bda5e-15f7-49c3-b953-cc8b29ccd026 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:24:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 70 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41942 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Structure, Ring 70, 7 O'Clock, Concrete Element | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Active Leak Shell Segment Penetration |  | Active Leak Shell Segment Penetration | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak at tunnel segment grout injection hole. Carry out leak seal in accordance with approved remediation work scope. | Engineering repair method and specification required. Concrete remediation crew. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | Leak not sighted at time of inspection. Suggest no longer active and obscured by dirt. | no | no |  | yes | Priority and risk to be downgraded | 0a5983a9-e0ea-4eee-b15b-afe377cc09da,35a249d1-3055-4603-87c5-eff07fa81ee3 | , | https://web.fulcrumapp.com/photos/view?photos=0a5983a9-e0ea-4eee-b15b-afe377cc09da%2C35a249d1-3055-4603-87c5-eff07fa81ee3 | Concrete |  | Leaks
0ac8ca3c-5076-44bc-9108-cebf85a86b6d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:25:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 70 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41897 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Structure, Ring 70, 8 O'Clock, Concrete Element | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at segment bolted joints at two locations 600mm x 200mm. |  | Grout Delamination / debonding at segment bolted joints at two locations 600mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | no |  | e8739648-0a67-4be9-8c24-9a518780e869,9b1fedd2-b956-47a8-bda2-addb5a9471e4 | , | https://web.fulcrumapp.com/photos/view?photos=e8739648-0a67-4be9-8c24-9a518780e869%2C9b1fedd2-b956-47a8-bda2-addb5a9471e4 | Concrete | Circular Joint | Drummy
bc2a137e-6bf1-4f6a-88b8-efac3b7e46a4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:31:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 71 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99527 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 71, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 300 mm x 200 mm |  | Grout Delamination / Drummy Grout at radial joint over an area of 300 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | No change area of drummy concrete is same. |  |  |  | yes |  | 0a6701b3-eafd-4d16-9b6f-eeca00131a43 |  | https://web.fulcrumapp.com/photos/view?photos=0a6701b3-eafd-4d16-9b6f-eeca00131a43 | Concrete | Grout Hole | Drummy |  | Grout hole not radial Joint
3b27e960-8f9e-4ed8-9dc0-c529d6d4e011 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:12:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 72 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26810 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 72, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | The leak behind the steel bracket is inactive at the time of the inspection. | no | yes |  | no |  | ab45abe2-0ce9-42ad-8b1e-0e9882925441,3fe33895-0fc6-42db-8c41-e89edbaca186 | , | https://web.fulcrumapp.com/photos/view?photos=ab45abe2-0ce9-42ad-8b1e-0e9882925441%2C3fe33895-0fc6-42db-8c41-e89edbaca186 | Concrete,Steel | Channel Bracket | Leaks |  | Not reinforcement should be Channel Bracket
4fdc513b-555b-4bf7-ad8a-ce9155f23838 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:23:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 72 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41947 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 72, 4 o'clock. Concrete Liner Panel. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Hydrophilic Joint Seal (Radial) has Leak - Inactive at time of inspection. |  | Hydrophilic Joint Seal (Radial) has Leak - Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | Dr |  | Leak still inactive at time of inspection. No change to condition of defect. | no | yes |  | no |  | a1a423d8-18c6-4f08-b879-e98e3b81cb89 |  | https://web.fulcrumapp.com/photos/view?photos=a1a423d8-18c6-4f08-b879-e98e3b81cb89 | Concrete | Circular Connection | Leaks |  | Circular Connection
ee24910c-9d83-4f70-b028-22f055381942 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:30:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 72 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69084 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 72, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 100mm x 200mm |  | Concrete shell segment has drummy concrete over an area of 100mm x 200mm | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | ad50e967-5b3f-410f-9b98-d4c254dd22a2,3053491c-356c-4153-b35a-9fffdd386b73 | , | https://web.fulcrumapp.com/photos/view?photos=ad50e967-5b3f-410f-9b98-d4c254dd22a2%2C3053491c-356c-4153-b35a-9fffdd386b73 | Concrete | Circular Joint | Drummy |  | Circular joint not reinforcement
a10d714b-4a0f-4204-b0d6-5a6c51a36eb3 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:29:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 72 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41943 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 72, 9 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. - Condition rating 5. |  | Grout injection hole has Leak Active at time of inspection. - Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | A.Acero |  | No change in deffect. Non leak risk low | no | no |  | no |  | bd3bad28-f8e6-44f8-99cc-200c886a65c0 |  | https://web.fulcrumapp.com/photos/view?photos=bd3bad28-f8e6-44f8-99cc-200c886a65c0 | Concrete | Grout Hole | Leaks
95d9acd4-ca32-4708-859a-c6c5ea4feabf | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:53:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 73 | 11 | Grout Injection Hole | Grout Injection Hole |  | 85862 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 73, 11 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak is inactive at time inspection. Staining and salt deposit present in the injection hole. Grout plug is missing. High priority | yes | no | High |  |  | e194082a-bc77-4685-bf81-f3ff2967cfb3,4693a01f-aa99-4581-9a03-90fc7496e81f,614ebf1e-1fb8-4c33-b3bc-da5660251ff2 | ,, | https://web.fulcrumapp.com/photos/view?photos=e194082a-bc77-4685-bf81-f3ff2967cfb3%2C4693a01f-aa99-4581-9a03-90fc7496e81f%2C614ebf1e-1fb8-4c33-b3bc-da5660251ff2 | Concrete | Grout Hole | Leaks,Missing
3e2bd8bd-34b5-454c-a55c-81a4fce088dc | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:24:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 73 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26811 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA |  | Non Active leak risk low | [5 empty] | 1de1b3a4-7aff-473d-b94f-e094543bf72b,dbb97b65-dc54-448f-9c38-4436cb172127,fc5c7df4-89a5-49f5-b5e4-90a0b5b22445 | ,, | https://web.fulcrumapp.com/photos/view?photos=1de1b3a4-7aff-473d-b94f-e094543bf72b%2Cdbb97b65-dc54-448f-9c38-4436cb172127%2Cfc5c7df4-89a5-49f5-b5e4-90a0b5b22445 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
ba100246-93c0-4a66-bd51-4423e51cc3b3 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 12:25:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 73 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27417 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 73, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout in two locations of 250mm x 200mm and 250mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout in two locations of 250mm x 200mm and 250mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AC BP |  | Repair patches of grout across radial seam, no leak | no | yes |  | yes | Remarked with orange paint | 4a45e58f-1050-483b-96a7-7f10a4cb67ef |  | https://web.fulcrumapp.com/photos/view?photos=4a45e58f-1050-483b-96a7-7f10a4cb67ef | Concrete | Radial Joint,Reinforcement | Drummy,Leaks
ad226626-52b9-4240-af60-a8d928d73b23 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:50:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 74 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26914 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 74, 12 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 200mm x 200mm. |  | Concrete shell segment has drummy concrete over an area of 200mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Break out loose and damaged concrete. Engineer to assess damage to reinforcement and remediation required. All areas of damaged concrete shall be replaced with high strength concrete patch repairs including embedment of galvanic Cathodic Protection (CP) anodes. Corroded reinforcement that has not been removed shall be thoroughly cleaned of all corroded material. Where corroded reinforcement has been removed it should be replaced by welding a new length of N grade reinforcement of the same diameter to the remaining undamaged reinforcing bar. Or replacing the damaged bar with a new N grade bar of the same diameter as the removed bar. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Supervisor | Dr |  | Defect is not present. Remove. | no | no |  | yes | Remove defect. | 55edaa7c-9a71-43a5-85e7-bcacb3658f90 |  | https://web.fulcrumapp.com/photos/view?photos=55edaa7c-9a71-43a5-85e7-bcacb3658f90 | Concrete | Reinforcement | Drummy
fe7cdc63-af5a-496d-8842-14decef4a4e6 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:29:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 75 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27418 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 75, 12 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | AA |  | Drummy concrete risk low | [5 empty] | 710cfc1c-83cd-4c13-a3f9-33fd22f0ae90 |  | https://web.fulcrumapp.com/photos/view?photos=710cfc1c-83cd-4c13-a3f9-33fd22f0ae90 | Concrete | Circular Joint | Drummy |  | Not Reinforcement
c07bb033-e031-457c-9bf9-f11cea753d12 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:31:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 75 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27419 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 75, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | 400mm x 400mm drummy concrete, potentially also sulphates. |  | 400mm x 400mm drummy concrete, potentially also sulphates. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA |  | Drummy concrete risk low | [5 empty] | a21901ce-64f9-4810-8b8b-34cbcc1fea25 |  | https://web.fulcrumapp.com/photos/view?photos=a21901ce-64f9-4810-8b8b-34cbcc1fea25 | Concrete | Reinforcement | Drummy
41122991-0c54-4235-a468-59aaa2b0c103 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:38:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 75 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41898 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 75, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400 mm x 100 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400 mm x 100 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 4308772a-8197-4b9c-8ea5-5f21fc3911de,64946e7c-0af9-4a3f-a462-ddfb4b96fcda | , | https://web.fulcrumapp.com/photos/view?photos=4308772a-8197-4b9c-8ea5-5f21fc3911de%2C64946e7c-0af9-4a3f-a462-ddfb4b96fcda | Concrete | Circular Joint | Drummy
74ac026b-ef94-4abd-b9c7-420b5bbfc62c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:35:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 76 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85902 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44875.8259 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | O'Clock, Steel Channel Bracket |  |  |  | Steel Channel Bracket has Level 2 Medium Low Corrosion |  | Steel Channel Bracket has Level 2 Medium Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | AA |  | Minor corrosion low risk. / loose bolt toward base frame support | no | no |  | no |  | 2954673d-eace-4c41-b136-1c781c923284,4d79f1c3-51cf-41dc-a924-c27702744c26,fba76c48-3af7-44c9-92c4-7fd6b120e2d6,7666fdb9-e651-4db1-a35d-18d4bc78c9f6 | ,,, | https://web.fulcrumapp.com/photos/view?photos=2954673d-eace-4c41-b136-1c781c923284%2C4d79f1c3-51cf-41dc-a924-c27702744c26%2Cfba76c48-3af7-44c9-92c4-7fd6b120e2d6%2C7666fdb9-e651-4db1-a35d-18d4bc78c9f6 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Loose
707eb0f9-e2f9-44d3-8b95-175715a8326e | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:38:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 77 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69085 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 77, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA |  | Drummy concrete risk low | [5 empty] | 21d61cf7-09bf-4963-a7f5-e0d940cf2a8a,aad23c8e-8883-4178-803b-a4f506db302a | , | https://web.fulcrumapp.com/photos/view?photos=21d61cf7-09bf-4963-a7f5-e0d940cf2a8a%2Caad23c8e-8883-4178-803b-a4f506db302a | Concrete | Circular Joint | Drummy |  | Not Reinforcement
985df64f-ea7a-49ec-b113-483e76576f17 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:47:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 79 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27089 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 79, 10 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Break out grout locally, abrasive blast steelwork, and inspect by competent engineer to develop repair detail. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Supervisor | Dr |  | Area of drummy and Delaminated concrete remains the same. Defect is at ring 80, not 79. | no | no |  | yes | Change defect to ring 80 | ec4b3993-353e-4ae1-ba6b-2a84edbdea9f,84c40f07-05cc-4c58-a9ff-39a6db6477a9 | , | https://web.fulcrumapp.com/photos/view?photos=ec4b3993-353e-4ae1-ba6b-2a84edbdea9f%2C84c40f07-05cc-4c58-a9ff-39a6db6477a9 | Concrete | Radial Joint | Drummy |  | Not Reinforcement
e0bcc0c6-cf27-441e-b14f-0e9681344f07 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:26:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 79 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99528 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 79, 12 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Inactive Leak Segment bolted circle joint |  | Inactive Leak Segment bolted circle joint | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | AA |  | Active minor leaking at grout injection hole - Risk low |  |  |  | yes | Initial inspection suggest leak is active, however on second inspection, leak is inactive. Update as inactive. DR | e7441cca-2d76-4c80-bb71-7db0c88090a6,46ae2fd8-2f47-435b-a92d-9575939e89e6,d3cb4bd5-5868-4bfc-a565-06c9960f2704 | ,,Showing inactive leak - DR Inspection | https://web.fulcrumapp.com/photos/view?photos=e7441cca-2d76-4c80-bb71-7db0c88090a6%2C46ae2fd8-2f47-435b-a92d-9575939e89e6%2Cd3cb4bd5-5868-4bfc-a565-06c9960f2704 | Concrete | Circular Joint,Grout Hole | Leaks
1e06ff48-fc6d-4ae7-8afa-2d8f4b5cc898 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:43:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 79 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26812 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 79, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AA |  | Active leaking at grout hole risk medium |  | yes |  |  |  | 7272ba37-86bb-49d0-9422-308f964401b6,c8357f59-15b7-4282-a9a7-c8c0e232edc9,2b1cf63b-fb8f-493d-ad32-75dae462bbac,8b673589-a690-42c1-9c1d-bbbf9b1d34f5 | ,,, | https://web.fulcrumapp.com/photos/view?photos=7272ba37-86bb-49d0-9422-308f964401b6%2Cc8357f59-15b7-4282-a9a7-c8c0e232edc9%2C2b1cf63b-fb8f-493d-ad32-75dae462bbac%2C8b673589-a690-42c1-9c1d-bbbf9b1d34f5 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
380ada28-3c38-458f-b9d8-5dcb475ae5c4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 03:45:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 79 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41920 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 79, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 500mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 500mm x 300mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Defect is drummy outside of the normal grout pad area. Parent concrete is affected. This should be treated. | no | yes |  | yes | Update description | 123ac819-cae1-43f1-96f2-7ba263f026ba,04acf598-8b11-428d-a8ec-3167b542290c,2eb3c3a5-6c14-46dc-8568-a4db6cffb0bd | ,, | https://web.fulcrumapp.com/photos/view?photos=123ac819-cae1-43f1-96f2-7ba263f026ba%2C04acf598-8b11-428d-a8ec-3167b542290c%2C2eb3c3a5-6c14-46dc-8568-a4db6cffb0bd | Concrete | Circular Joint | Drummy |  | Not Reinforcement
258caafe-7a8b-4681-9b4d-8e4578b47ec1 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:48:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 80 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26813 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 4. >= US$250 million, < US$2 billion |  | Severity Level 4. >= US$250 million, < US$2 billion | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | No | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | AA |  | Not visible defect. Remove line |  | yes |  |  |  | 7e8251e6-87e5-4ce4-86ba-04e33ab73e75,3b5b08cf-8a93-471b-ba91-314f4ff4435f,5a5c5a2e-4e3c-4e0a-85b9-35291ac0189c | ,, | https://web.fulcrumapp.com/photos/view?photos=7e8251e6-87e5-4ce4-86ba-04e33ab73e75%2C3b5b08cf-8a93-471b-ba91-314f4ff4435f%2C5a5c5a2e-4e3c-4e0a-85b9-35291ac0189c | Concrete | Grout Hole | Leaks |  | Not Reinforcement
7f03e994-c6dc-4b6a-9dca-fccaac294783 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:41:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 80 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27420 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 80, 10 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | DR |  | Drummy concrete is still present. No change to area of drummy concrete. | no |  |  |  |  | 6961a882-bbc5-4270-ac13-29e40ce59acf,da42329a-a2e0-41cf-b056-1546778bfa8d | , | https://web.fulcrumapp.com/photos/view?photos=6961a882-bbc5-4270-ac13-29e40ce59acf%2Cda42329a-a2e0-41cf-b056-1546778bfa8d | Concrete | Circular Joint | Drummy |  | Not Reinforcement
fa61d76c-273f-437f-b1f5-394b29789a30 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 | -20.3216 | 118.5854 | POINT (118.58539 -20.3216274) | 2025-05-27 20:13:17 AEST | 2025-07-31 05:20:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 80 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99535 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 80, 4 o'clock. Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area of 400mm x 100mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area of 400mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Minor drummy area. | no | yes |  | no |  | 0df4aaf0-de28-46d6-a062-85e0dcadd17b,3a5fe652-1aa8-4173-bf98-6d45cf794acc | , | https://web.fulcrumapp.com/photos/view?photos=0df4aaf0-de28-46d6-a062-85e0dcadd17b%2C3a5fe652-1aa8-4173-bf98-6d45cf794acc | Concrete | Circular Joint | Drummy
2b63443e-886b-40d3-97fd-a5c8b67ddea0 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:22:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 80 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99534 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 80, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 200 mm x 100 mm |  | Grout Delamination / Drummy Grout at radial joint over an area of 200 mm x 100 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | A.Acero BP |  | No defect in ring area. Opposite support beam | no | no |  | no |  | e3d8bcf0-b73c-4ab7-83f1-abb60cfe8534,60031727-da63-4418-bd9b-d03a06f1ec5e,991220a0-8186-42e8-a674-7d4ec0cb53a7 | ,, | https://web.fulcrumapp.com/photos/view?photos=e3d8bcf0-b73c-4ab7-83f1-abb60cfe8534%2C60031727-da63-4418-bd9b-d03a06f1ec5e%2C991220a0-8186-42e8-a674-7d4ec0cb53a7 | Concrete | Circular Joint | Drummy |  | Circular Joint not Radial Joint
affb4306-b9de-4db5-bdee-7d24d76da238 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:58:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 81 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85863 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 10/11/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 81, 4 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint seal has Leak Inactive at time of inspection. |  | Circle joint seal has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Engineering Repair Methodology Required Competent Engineer | Dr |  | No change to defect. Still inactive at time of inspection | no | yes |  |  |  | 894b18c6-e3e9-4e94-88a3-c8e6acf7fe39 |  | https://web.fulcrumapp.com/photos/view?photos=894b18c6-e3e9-4e94-88a3-c8e6acf7fe39 | Concrete | Circular Joint | Leaks
b0b94646-274b-4277-806f-4bcf8a0a58d7 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:25:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 82 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42032 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Carbonation Induced |  | Carbonation Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 82, 8 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | A.Acero |  | Delamination is converting to spall. While this is normally a low priority type of defect, there is part of the CP system affected. This should be treated. | no | yes |  | no |  | 2668f58f-dfbc-4ec6-934d-f96b693a60be,ac7a4e4a-807a-4ebf-ae7d-2b05bdde0d22,a0ab0085-1710-4a93-90a2-d42ca16e65b1 | ,, | https://web.fulcrumapp.com/photos/view?photos=2668f58f-dfbc-4ec6-934d-f96b693a60be%2Cac7a4e4a-807a-4ebf-ae7d-2b05bdde0d22%2Ca0ab0085-1710-4a93-90a2-d42ca16e65b1 | Concrete | Radial Joint | Drummy,Surface Damage |  | Not Reinforcement
b08ee475-129f-48f8-9ab9-a0dc56322312 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 14:22:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 83 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42490 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 83, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Active at time of inspection. Condition rating 5. |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Active at time of inspection. Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AC BP |  | Heavy deposition of stalactites | yes | yes |  | yes |  | f1189a67-cac0-4306-97d6-18b7b073caef,858d611b-2158-438e-8684-0e71b3e42611 | , | https://web.fulcrumapp.com/photos/view?photos=f1189a67-cac0-4306-97d6-18b7b073caef%2C858d611b-2158-438e-8684-0e71b3e42611 | Concrete | Circular Joint | Leaks
8fd3eb96-e4cd-4f84-bba2-d87621e23544 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:52:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 83 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99538 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 83, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 400mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 400mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | A.Acero BP |  | Drummy concrete at radial seam - low risk | no | yes |  | yes |  | 29bbec17-69e5-4b3c-b0a3-3366e837bc0c,62e0f68d-06d7-4685-81c6-eb0688966d18 | , | https://web.fulcrumapp.com/photos/view?photos=29bbec17-69e5-4b3c-b0a3-3366e837bc0c%2C62e0f68d-06d7-4685-81c6-eb0688966d18 | Concrete | Radial Joint | Drummy
8be4d72c-20da-40ff-bda2-526014cf98aa | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:27:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 83 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99581 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 83, 8 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 300mm x 100mm. |  | Grout Delamination / Drummy Grout at circle joint over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AA |  | Grout patch is spalling. To be treated. | no | no |  | no |  | 24dfde67-d8ee-462a-a12a-58b3369e2a88,ff4d20ee-d0e9-425e-9f77-3ccea8d06094 | , | https://web.fulcrumapp.com/photos/view?photos=24dfde67-d8ee-462a-a12a-58b3369e2a88%2Cff4d20ee-d0e9-425e-9f77-3ccea8d06094 | Concrete | Circular Joint | Drummy,Surface Damage
3a512fa5-951f-4bf6-b2be-2a96b94b4804 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 16:37:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 83 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99537 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 83, 9 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 250mm x 100mm. |  | Grout Delamination / Drummy Grout at circle joint over an area of 250mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | A.Acero |  | No change | no | no |  | no |  | fd1f36d2-7c66-4c10-bc0f-1d3d23c73273 |  | https://web.fulcrumapp.com/photos/view?photos=fd1f36d2-7c66-4c10-bc0f-1d3d23c73273 | Concrete | Circular Joint | Drummy
3e0952db-3d46-4e73-b883-a48049f431e2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 15:57:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 84 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 85903 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Loose Bolt |  | Loose Bolt | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Anchor bolt at steel channel is loose. |  | Anchor bolt at steel channel is loose. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace loose anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | AA |  | Loose bolt at 2 O’clock and 3 o’clock recommended to adjust bolts as they supports 3 cable ladder runs | [5 empty] | 92ecabfe-4199-42b2-a6e9-46ae56bb206f,37f61845-17b3-4cb0-a359-fdb7a8c89b5b,478f454e-b22c-4320-93f8-35dacb65ca3c,2f3fade0-9fbf-490a-9edb-9b4182611725 | ,,, | https://web.fulcrumapp.com/photos/view?photos=92ecabfe-4199-42b2-a6e9-46ae56bb206f%2C37f61845-17b3-4cb0-a359-fdb7a8c89b5b%2C478f454e-b22c-4320-93f8-35dacb65ca3c%2C2f3fade0-9fbf-490a-9edb-9b4182611725 | Steel | Channel Bracket-Bolt | Loose |  | Only Bolt
dc819757-1470-43e5-9176-bd5c29f3a51d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:31:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 85 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27090 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 85, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | AC BP |  | Still inactive | no | no |  | yes |  | 44d5dd54-9d7b-4e82-b86b-70eee5b63955,bc9e5027-f339-4ab9-ac1f-562eacb46fa2 | , | https://web.fulcrumapp.com/photos/view?photos=44d5dd54-9d7b-4e82-b86b-70eee5b63955%2Cbc9e5027-f339-4ab9-ac1f-562eacb46fa2 | Concrete | Reinforcement | Leaks |  | Not Reinforcement
4b082ff0-05cc-4c5f-a465-e9ec486380d6 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:37:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 88 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27114 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 88, 11 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive at time of inspection. Low priority | no | yes |  | no |  | c26f8e4b-2b60-4e46-9637-3e4f5d338617 |  | https://web.fulcrumapp.com/photos/view?photos=c26f8e4b-2b60-4e46-9637-3e4f5d338617 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
88e61ec3-36ce-4041-8ffe-f2fef5b66dfa | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:35:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 88 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85864 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 88, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | bac5d138-f37d-4d35-822c-e2af35e78ebf,4205ec03-6c1e-4714-bba8-a42269e0d641 | , | https://web.fulcrumapp.com/photos/view?photos=bac5d138-f37d-4d35-822c-e2af35e78ebf%2C4205ec03-6c1e-4714-bba8-a42269e0d641 | Concrete | Circular Joint | Drummy
5a6ea2ec-9c75-4ea9-bc0c-284c190a3e90 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:42:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 88 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27091 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 88, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No |  | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | AC BP |  | Leak is inactive | no | yes |  | yes |  | 19151176-65d4-40b2-bd4a-5469d0511958 |  | https://web.fulcrumapp.com/photos/view?photos=19151176-65d4-40b2-bd4a-5469d0511958 | Concrete |  | Leaks |  | Not Reinforcement
34083916-4222-4916-be17-23d9f9c84d3e | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 16:01:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 89 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26814 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | AA |  | No effect visible. Remove this defect | [5 empty] | cb1fceed-91a5-4572-995c-a67e75d10475,6f6da7d7-46b4-4292-804c-b1a64f9532cd | , | https://web.fulcrumapp.com/photos/view?photos=cb1fceed-91a5-4572-995c-a67e75d10475%2C6f6da7d7-46b4-4292-804c-b1a64f9532cd | Concrete | Grout Hole | Leaks |  | Not Reinforcement
09d617df-8167-4993-b954-2691aa4f69d7 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 16:03:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 90 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 69086 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44550.5628 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 90, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 25% coverage. |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | AA |  | Corrosion still present risk level low | [5 empty] | 73489de6-59d8-4580-93b3-dd4702536dcf,b6668be0-a3e0-4daa-a381-a92f0f4bfeda | , | https://web.fulcrumapp.com/photos/view?photos=73489de6-59d8-4580-93b3-dd4702536dcf%2Cb6668be0-a3e0-4daa-a381-a92f0f4bfeda | Steel | Channel Bracket | Corrosion-Surface
ef48afaa-6662-42c7-93fd-13ef95f97d36 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:05:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 90 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85904 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 90, 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | HM |  | Anchor bolt is still missing. | no | no | 4 | yes | Downgrade priority to 4. | 6ee4113d-03cb-4892-b841-b1b5aba8d781 |  | https://web.fulcrumapp.com/photos/view?photos=6ee4113d-03cb-4892-b841-b1b5aba8d781 | Steel | Channel Bracket-Bolt | Missing |  | only bolt
ee4e6832-e015-44c7-9075-f6f7322dcaa8 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 20 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:54:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 90 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85865 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 90, 7 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak is inactive at time of inspection. No evidence of leak. Low priority | yes | no | Low |  |  | 956eb3e1-dea0-4af0-ab24-6863eb0c2836 |  | https://web.fulcrumapp.com/photos/view?photos=956eb3e1-dea0-4af0-ab24-6863eb0c2836 | Concrete |  | Leaks
3fe8c8e2-3735-4d0a-9a35-dc55742ddff1 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 16 |  |  |  | 2025-07-24 16:45:20 AEST | 2025-07-27 16:07:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 92 | 6 | [34 empty] | O ‘ clock Crack at joint side | [24 empty] | A.Acero |  | Crack appearing risk level low monitor |  | no |  | no |  | 664545b0-6d24-48b3-a59f-562b9070c4ae,a5f734b1-87a4-40d2-879e-01b57469bc21 | , | https://web.fulcrumapp.com/photos/view?photos=664545b0-6d24-48b3-a59f-562b9070c4ae%2Ca5f734b1-87a4-40d2-879e-01b57469bc21 | Concrete | Radial Joint | Crack |  | Radial Joint
007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 15 |  |  |  | 2025-07-25 12:09:19 AEST | 2025-07-25 12:17:07 AEST | 30011704-user5@smec.com | james.stone@smec.com | 72 | 6 O’Clock Conveyor support beam / walkway |  |  | Base concrete and steel beam | [14 empty] | Corrosion - Connection |  | 2 | [39 empty] | AC BP |  | Some steel section loss, cracked concrete base |  | yes |  | yes | Remedial recoat with epoxy | b36cc6ad-b9ab-431b-b8c4-6aa2e1e0aa7c,1643b668-8405-4c81-885a-b88048ddfd9a,0479752a-c369-4344-9f89-b5f3047abc06,68767106-de3b-4fae-ab1f-a05ab0f78f9b,273ee17a-139d-46c8-9a33-711de2ac1174,97054597-cfdd-4621-8713-871d6227a54e,aaf9e908-8bbd-4fb1-95c6-6ff9d350db30,2c7f37ca-cc40-4433-8122-f0de30df49cc | ,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=b36cc6ad-b9ab-431b-b8c4-6aa2e1e0aa7c%2C1643b668-8405-4c81-885a-b88048ddfd9a%2C0479752a-c369-4344-9f89-b5f3047abc06%2C68767106-de3b-4fae-ab1f-a05ab0f78f9b%2C273ee17a-139d-46c8-9a33-711de2ac1174%2C97054597-cfdd-4621-8713-871d6227a54e%2Caaf9e908-8bbd-4fb1-95c6-6ff9d350db30%2C2c7f37ca-cc40-4433-8122-f0de30df49cc | Concrete,Steel | Centre Support | Corrosion-Heavy,Crack
fd439ff8-fde2-4f54-a60c-53caf48f5183 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 15 |  |  |  | 2025-07-25 12:32:14 AEST | 2025-07-25 12:43:19 AEST | 30011704-user5@smec.com | james.stone@smec.com | 76 | 6 O’Clock Support beam and walkway bracket |  |  | Conveyor and walkway support beam | [14 empty] | Corrosion - Connection |  | 2 | [31 empty] | Remedial Blast and epoxy coating | [7 empty] | AC BP |  | Conveyor Beam support base plate corroded. Circular walkway support fastener nut corroded | [5 empty] | 7c98c354-066b-4739-8145-b45b899c9530,deb75ad4-8cbd-48b7-9bf9-450aa66047c9,8e7d2911-e216-4edc-befc-6f75d4dcf376,b00e6920-3335-4e38-a563-9ad719b1cf79,1d7e90ab-7df6-4aa2-8932-a80e76877e43 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=7c98c354-066b-4739-8145-b45b899c9530%2Cdeb75ad4-8cbd-48b7-9bf9-450aa66047c9%2C8e7d2911-e216-4edc-befc-6f75d4dcf376%2Cb00e6920-3335-4e38-a563-9ad719b1cf79%2C1d7e90ab-7df6-4aa2-8932-a80e76877e43 | Steel | Walkway Support,Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support as well
d6407af9-d9a0-4a53-9e32-2c7c40887929 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 14 |  |  |  | 2025-07-25 14:01:04 AEST | 2025-07-25 14:05:36 AEST | 30011704-user5@smec.com | james.stone@smec.com | 80 | 6 O’Clock Conveyor and walkway support beam |  | Steel Channel Bracket | [16 empty] | Other | 2 | [33 empty] | Yes | [5 empty] | AC BP |  | Corroded baseplate Steel support beam. Nut needs replacement |  | yes |  | yes |  | a9575dcc-3908-4802-8462-c6d607a6b82e,4ab8c7a7-a95b-40f8-9f2c-1299520585f2 | , | https://web.fulcrumapp.com/photos/view?photos=a9575dcc-3908-4802-8462-c6d607a6b82e%2C4ab8c7a7-a95b-40f8-9f2c-1299520585f2 | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support not channel bracket
0a50d00d-423b-4bd1-b54f-6ea215daf809 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 14 |  |  |  | 2025-07-25 14:22:15 AEST | 2025-07-25 14:45:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 83 | 4 O’Clock circumference seam |  |  | Heavy stalactite deposit | [16 empty] | 3 | [39 empty] | AC BP |  | Heavy deposits at circumferential seam |  | no |  | yes |  | 6ef0150c-3078-44ed-a216-09a74f782138,c81f3c0a-1565-4745-bd2f-9f5a7f88abb6,c9ad238a-ec38-4d9e-b2f1-00c9eeacfde7,9d2b8b0d-4f94-405c-a164-c42e7df3fb3c,6e390dfe-72aa-40e2-aedb-fc71bfae1f8b | ,,,, | https://web.fulcrumapp.com/photos/view?photos=6ef0150c-3078-44ed-a216-09a74f782138%2Cc81f3c0a-1565-4745-bd2f-9f5a7f88abb6%2Cc9ad238a-ec38-4d9e-b2f1-00c9eeacfde7%2C9d2b8b0d-4f94-405c-a164-c42e7df3fb3c%2C6e390dfe-72aa-40e2-aedb-fc71bfae1f8b | Concrete | Circular Connection,Circular Joint,Centre Support |  |  | Centre Support as well
d8c30d2c-2a2f-4e75-9ca3-7554b689c587 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 14 |  |  |  | 2025-07-25 14:46:04 AEST | 2025-07-25 14:56:08 AEST | 30011704-user5@smec.com | james.stone@smec.com | 91 | 7 O’clock | [61 empty] | Ring frame Circular seam corroded. Stallactites accumulated |  |  |  | yes |  | 5c804070-ad56-42fc-b65e-5548989d9b36,70e08e43-f8f9-416c-8752-caa6d48844e9,65f49dfb-4953-4b3d-82c5-eddc68803208 | ,, | https://web.fulcrumapp.com/photos/view?photos=5c804070-ad56-42fc-b65e-5548989d9b36%2C70e08e43-f8f9-416c-8752-caa6d48844e9%2C65f49dfb-4953-4b3d-82c5-eddc68803208 | Concrete | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support
bdfdebe4-160d-4851-a9a3-b527a6a8414d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 14 |  |  |  | 2025-07-25 14:50:46 AEST | 2025-07-25 14:54:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 92 | 6 O’Clock | [17 empty] | Corrosion - Connection | [41 empty] | AC BP |  | Support beam and baseplate corroded. Cracked concrete | [5 empty] | 7ffe7a8a-55b6-4c63-8c87-8dca6004367b,931d877f-799a-4a20-8f59-962d0bc5f010,4e951ae7-2a26-4834-acad-58af057076f7,717f859d-caa0-4924-8301-1a07012eb82c,3ad33a0a-b51e-4412-a153-5254d93ca4d3 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=7ffe7a8a-55b6-4c63-8c87-8dca6004367b%2C931d877f-799a-4a20-8f59-962d0bc5f010%2C4e951ae7-2a26-4834-acad-58af057076f7%2C717f859d-caa0-4924-8301-1a07012eb82c%2C3ad33a0a-b51e-4412-a153-5254d93ca4d3 | Concrete | Centre Support | Crack |  | Centre Support
eda90375-414c-4158-94c5-197a4b51a23a | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 11 |  |  |  | 2025-07-27 15:48:32 AEST | 2025-07-27 15:51:00 AEST | 30011704-user5@smec.com | james.stone@smec.com | 80 | 1 | [34 empty] | Active leaking at injection grout hole | [24 empty] | AA |  | Active grout leaking starting to appear at grout hole risk - low to medium | [5 empty] | 8328cf07-43cc-4478-a658-e3ae7b07bd63,8eb9921e-364e-4d3d-a93b-6cb87b8a1fed,aa84f9e1-d0fd-40ce-b49e-3451a8a815b3 | ,, | https://web.fulcrumapp.com/photos/view?photos=8328cf07-43cc-4478-a658-e3ae7b07bd63%2C8eb9921e-364e-4d3d-a93b-6cb87b8a1fed%2Caa84f9e1-d0fd-40ce-b49e-3451a8a815b3 | Concrete | Grout Hole | Leaks
8701b36c-8640-4406-a685-2ddb4fd3cfed | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 7 |  |  |  | 2025-07-30 03:36:54 AEST | 2025-07-30 03:39:03 AEST | 30011704-user5@smec.com | james.stone@smec.com | 62 | 3 |  | Channel Anchor Bolts | [32 empty] | Ring 62, 3 o' clock, missing anchor bolts |  |  |  |  | Channel anchor bolt is missing. | [19 empty] | HM |  | 2 x anchor bolts are missing in the steel bracket |  | yes |  | no |  | d9ddc125-ac1e-4312-828f-c0dc0252e403,64f15765-eb90-4d3e-bc86-a8d7866ccaa2 | , | https://web.fulcrumapp.com/photos/view?photos=d9ddc125-ac1e-4312-828f-c0dc0252e403%2C64f15765-eb90-4d3e-bc86-a8d7866ccaa2 | Steel | Channel Bracket-Bolt | Missing
3246a177-2b50-484c-89aa-12e9f0939204 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 3 |  |  |  | 2025-07-31 03:39:17 AEST | 2025-07-31 03:40:35 AEST | 30011704-user5@smec.com | james.stone@smec.com | 75 | 9 |  | Grout Injection Hole | [32 empty] | Active leaking at injection grout hole | [24 empty] | SS |  | Active grout leaking starting to appear at grout hole risk - low to medium |  | no |  | yes | Fill empty fields | facf4c3d-19b0-485f-8866-8e323e769b30,e1e22c10-7937-4e0b-93ea-b882df233c20 | , | https://web.fulcrumapp.com/photos/view?photos=facf4c3d-19b0-485f-8866-8e323e769b30%2Ce1e22c10-7937-4e0b-93ea-b882df233c20 | Concrete | Grout Hole | Leaks
f585d567-5b17-4dde-9822-c61fe24778eb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:02:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 92 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26815 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 92, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | HM |  | Grout leak is inactive at the time of the inspection. It is possible the leak is fixed. | no | yes |  | no |  | cff40b20-41e7-4dcf-9e4e-63ad4e1f3a67,5f2d38bb-f3b9-46f1-99fd-3ca4cd1e2b0c | , | https://web.fulcrumapp.com/photos/view?photos=cff40b20-41e7-4dcf-9e4e-63ad4e1f3a67%2C5f2d38bb-f3b9-46f1-99fd-3ca4cd1e2b0c | Concrete | Grout Hole | Leaks |  | Not reinforcement
4a51f523-68e6-4e5d-9a0e-cdf6108aacca | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 03:00:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 92 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85905 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44875.8314 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 92, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel Channel Bracket has Level 2 Medium Low Corrosion |  | Steel Channel Bracket has Level 2 Medium Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Minor corrosion of the steel anchor bracket. | no | yes |  | no |  | 1f51cce4-342c-4e4b-9a9f-c1cdd452669f |  | https://web.fulcrumapp.com/photos/view?photos=1f51cce4-342c-4e4b-9a9f-c1cdd452669f | Steel | Channel Bracket | Corrosion-Surface
7a07d732-8c7f-4a3e-9e92-16dc629a8b17 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:45:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 92 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69087 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 92, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has leak - Active at time of inspection. Condition rating 5. |  | Concrete shell segment at bolted connection penetration has leak - Active at time of inspection. Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak is still active at the time of inspection. Steel bracket and anchor bolt heavily corroded. Salt deposits present as well. High priority. | yes | no | High priority | no |  | 48094c54-fd9a-4dce-a6fd-0e91feccd159,5dd18618-1bc8-4072-a186-b39286c0f373 | , | https://web.fulcrumapp.com/photos/view?photos=48094c54-fd9a-4dce-a6fd-0e91feccd159%2C5dd18618-1bc8-4072-a186-b39286c0f373 | Concrete,Steel | Walkway Support | Leaks |  | Walkway support
6c0c8b27-38ec-46d9-813b-8a6728aa9566 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:45:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 92 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 41944 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44043.5132 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Structure, Ring 92, 7 O'Clock, Concrete Element |  |  |  | Non-Active Leak Grout Injection Hole |  | Non-Active Leak Grout Injection Hole | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Defect listed twice. Remove |  |  |  | yes | Listed twice, remove |  |  |  | Concrete | Grout Hole | Leaks
ab28569f-fb66-4b3a-aba2-37fef9b025fa | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:59:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 93 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26816 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 93, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer | HM |  | Grout hole leak is inactive at the time of inspection. It is possible the leak has been fixed. | no | yes |  | no |  | 8524aee4-1eaa-4ad9-876c-adece091aef9 |  | https://web.fulcrumapp.com/photos/view?photos=8524aee4-1eaa-4ad9-876c-adece091aef9 | Concrete | Grout Hole | Leaks |  | Not reinforcement
e8f6009c-d4f9-4ad7-8a6c-71a088190853 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:35:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 93 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41948 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 93, 10 to 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Major leak still present. Collection of salt deposits around the grout injection hole and concrete surface. High priority defect. | yes | no | High | no |  | df9f393e-28bb-4d2b-bdd7-0440a3b5c669,c63163a1-ed6e-483f-b8f4-d0184f50e26d,3f8425ef-e2fe-41fb-91a5-fdc4ea0addcd | ,, | https://web.fulcrumapp.com/photos/view?photos=df9f393e-28bb-4d2b-bdd7-0440a3b5c669%2Cc63163a1-ed6e-483f-b8f4-d0184f50e26d%2C3f8425ef-e2fe-41fb-91a5-fdc4ea0addcd | Concrete | Grout Hole | Leaks
d7e94c09-ea48-4667-9d93-e89d757005fd | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:57:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 93 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27425 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 93, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | HM |  | This defect is a duplication. Suggest deleting it. Refer to the notes in the similar defect. | no | yes |  | yes | Delete this defect. | eb5f5bd3-3eef-4fbf-9ce1-9490fb227df1 |  | https://web.fulcrumapp.com/photos/view?photos=eb5f5bd3-3eef-4fbf-9ce1-9490fb227df1 | Concrete | Grout Hole | Leaks |  | Not reinforcement
1565e672-3a2e-4584-9de4-f11c5b98afa4 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:55:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 93 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27422 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 93, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | HM |  | Grout hole leak is inactive at the time of inspection. It is possible leak has been fixed. | no | yes |  | no |  | d46b1c38-a98c-4385-b1a0-8e0df4511740,7575c9bb-2120-4162-a487-28b1a5f41106 | , | https://web.fulcrumapp.com/photos/view?photos=d46b1c38-a98c-4385-b1a0-8e0df4511740%2C7575c9bb-2120-4162-a487-28b1a5f41106 | Concrete | Grout Hole | Leaks |  | Not reinforcement
023ff6fc-aa04-4c6d-9266-88c3a8cf4044 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:33:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 94 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41949 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 94, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | Dr |  | No evidence leak found. Remove defect. | yes | no | No priority | no |  | c22b1cd9-582a-4722-b669-abd06c867c9e,47b2f3b9-b8df-431a-84da-b791e3c7b4eb | , | https://web.fulcrumapp.com/photos/view?photos=c22b1cd9-582a-4722-b669-abd06c867c9e%2C47b2f3b9-b8df-431a-84da-b791e3c7b4eb | Concrete | Grout Hole | Leaks
1109abae-6780-44f2-8540-cc5b2d86f5a2 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:52:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 94 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85906 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 94, 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | HM |  | Anchor channel bolt is still missing. | no | no | Downgrade to priority 4 | yes | Update priority | fb67957f-deb0-454a-a6c9-6d5752bde9d0 |  | https://web.fulcrumapp.com/photos/view?photos=fb67957f-deb0-454a-a6c9-6d5752bde9d0 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
a3b6f204-de42-4f92-abb4-0589bf29ead7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:47:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 94 | 7 | Grout Injection Hole | Grout Injection Hole |  | 99539 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 94, 7 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. - Condition Rating 5 |  | Grout injection hole has Leak Active at time of inspection. - Condition Rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak is inactive at time of inspection. May have been repaired. Low priority | yes | no | Low |  |  | 250ab6c0-c194-4503-89a9-f999b94dc316,81f8d7b1-93bb-419c-8e6a-0f4a94cf8149 | , | https://web.fulcrumapp.com/photos/view?photos=250ab6c0-c194-4503-89a9-f999b94dc316%2C81f8d7b1-93bb-419c-8e6a-0f4a94cf8149 | Concrete | Grout Hole | Leaks
f21d4acd-6180-479e-aa7b-4823b4bfde88 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:49:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 95 | 1 | Grout Injection Hole | Grout Injection Hole |  | 68871 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 95, 1 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer | HM |  | Grout hole leak is inactive at the time of the inspection. It is possible the leak has been fixed. | no | yes |  | no |  | f23884d2-efa4-41b8-8da4-81f8d67b68a7 |  | https://web.fulcrumapp.com/photos/view?photos=f23884d2-efa4-41b8-8da4-81f8d67b68a7 | Concrete | Grout Hole | Leaks |  | Not reinforcement
23559c8c-23a5-4bec-8b9d-37f822954385 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:31:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 95 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41950 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 95, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. - Condition rating 4. |  | Grout injection hole has Leak Inactive at time of inspection. - Condition rating 4. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | BP |  | Leak still inactive at time of inspection. Grout injection hole in good condition. No change | no | no | Low | no |  | dec9c789-c106-485e-bebb-83fe3eb728a8,33227cf9-4d4a-4ccf-8076-abd2ca23c830 | , | https://web.fulcrumapp.com/photos/view?photos=dec9c789-c106-485e-bebb-83fe3eb728a8%2C33227cf9-4d4a-4ccf-8076-abd2ca23c830 | Concrete | Grout Hole | Leaks
bf3eb9a8-8be3-4a76-b949-eb940c724267 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:38:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 95 | 6 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27426 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 95,6 O'Clock,Concrete Element,Identified in 2018 |  |  |  | Spalling in Floor |  | Spalling in Floor | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | DR |  | No spalling on floor at 6 O Clock. Remove defect | yes | no | No priority | yes | Remove defect |  |  |  | Concrete |  | Surface Damage
25c22f01-40ac-478d-bb81-a49008371a9d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 16:28:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 96 | 11 | Grout Injection Hole | Grout Injection Hole |  | 99540 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 96, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. - Condition Rating 4 |  | Grout injection hole has Leak Inactive at time of inspection. - Condition Rating 4 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | BP |  | Staining around bolt hole. No leak. Low risk | no | no |  |  |  | 48308045-2c21-4807-9249-4e348ac7ceb4 |  | https://web.fulcrumapp.com/photos/view?photos=48308045-2c21-4807-9249-4e348ac7ceb4 | Concrete | Grout Hole | Leaks
09196aa1-2dc2-4592-8d86-00d6dc69ad49 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 15:04:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 96 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85866 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 96, 7 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | AC BP |  | Bottom section of Steel support ring, corroded with stalactite deposits | yes | yes |  | yes |  | 0d5fce2c-04ac-46f5-b38d-0980711626d9,c4639101-1c5d-45c1-bdc6-53d5278cd74d,5d3e8ef6-237a-48ee-8247-d765d29f8c70,2fb74ed0-40ba-460c-9823-ab2eacd1bb6d | ,,, | https://web.fulcrumapp.com/photos/view?photos=0d5fce2c-04ac-46f5-b38d-0980711626d9%2Cc4639101-1c5d-45c1-bdc6-53d5278cd74d%2C5d3e8ef6-237a-48ee-8247-d765d29f8c70%2C2fb74ed0-40ba-460c-9823-ab2eacd1bb6d | Concrete,Steel | Conveyor Support | Leaks |  | Conveyor Support
254bf200-cdf8-4fd3-9c8e-8419e79c75d4 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 02:46:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 97 | 1 | Grout Injection Hole | Grout Injection Hole |  | 68872 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 97, 1 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer | HM |  | Grout leak is inactive at the time of the inspection. It is possible the leak has been fixed. | no | yes |  | no |  | f634ffe1-3956-4977-bb53-85a7346ff715 |  | https://web.fulcrumapp.com/photos/view?photos=f634ffe1-3956-4977-bb53-85a7346ff715 | Concrete | Grout Hole | Leaks |  | Not reinforcement
192c525a-6ea1-469f-ba8b-f81ba572f6b3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:29:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 97 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 69088 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.5667 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 97, 11 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Concrete she'll segment has been repaired. Defect can be removed. | yes | no | No priority | yes | Defect can be removed | affd646c-526a-4be1-b4d4-ba8329fc3dcb |  | https://web.fulcrumapp.com/photos/view?photos=affd646c-526a-4be1-b4d4-ba8329fc3dcb | Concrete |  | Test Hole
cada60e6-6146-4bc7-976a-1151f1bcb935 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:28:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 97 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27428 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 97, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | Dr |  | Leak still inactive at time of inspection. Grout plug in good condition. Low priority. | no | no | Low | no |  | 88679a70-4a9c-4738-9e5d-5ebc7df69262,aac66373-9358-406e-9dd0-7bd626599964 | , | https://web.fulcrumapp.com/photos/view?photos=88679a70-4a9c-4738-9e5d-5ebc7df69262%2Caac66373-9358-406e-9dd0-7bd626599964 | Concrete | Grout Hole | Leaks |  | Not reinforcement
7ee6e04a-09e0-41cd-a072-fda0e28c1290 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 16:41:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 98 | 1 - chloride induced segment | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26818 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 98, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | BP |  | Inactive leak, concrete dry when inspected. Medium risk | no | yes |  | yes |  | ce75da53-e9d9-4063-9d68-72d3946c006b |  | https://web.fulcrumapp.com/photos/view?photos=ce75da53-e9d9-4063-9d68-72d3946c006b | Concrete | Channel Bracket | Leaks |  | Cahnnel bracket not reinforcement
b8fa9417-1c6d-4cce-b09c-7d539191d2cb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 16:36:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 98 | 1 , Steel bracket corroded | Steel Channel Bracket | Steel Channel Bracket |  | 26817 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 98, 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 - Major Corrosion |  | Steel channel support bracket has Level 4 - Major Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), revised recommended action to blast and paint only. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services. | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. | Nil | No | Off-Line | Yes | Scaffolding | - | Corrosion Repair Competent Supervisor | BP |  | Steel bracket support overhead pipes Corroded. Medium risk, need blast and paint remediation | yes | yes |  | yes |  | 276f3ca2-b707-4ac8-b25c-57c634740ade |  | https://web.fulcrumapp.com/photos/view?photos=276f3ca2-b707-4ac8-b25c-57c634740ade | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
5abac53a-ba55-42ea-8050-4befc17adc99 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:49:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 98 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 69089 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.5687 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Ring 98, 7 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | AC BP |  | Defect not visible, may have been patched | yes | yes |  | no |  | 66fb7d6f-9b19-47e7-b500-c1743ad5d854,bb3ba1d3-cf40-4ede-949e-9f765231269c | , | https://web.fulcrumapp.com/photos/view?photos=66fb7d6f-9b19-47e7-b500-c1743ad5d854%2Cbb3ba1d3-cf40-4ede-949e-9f765231269c | Concrete |  | Test Hole
69ff1d32-fad2-4113-8d56-685e72de294d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 16:56:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 98 | 8 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 99541 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 45415.3216 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 98, 8 o'clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Crack at radial joint bolted joint grout patch. |  | Crack at radial joint bolted joint grout patch. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | AC BP |  | No defect, surface markings. Low risk. | [5 empty] | 9550c2aa-eb95-4828-b37f-0587fc42d7b7,4eb629cb-e16f-4608-967d-540dfb0d0351,1c1d9d15-01ab-40a5-8821-404114d6ed0e,22516a6f-007a-4120-a5e2-a6a496b02166 | ,,, | https://web.fulcrumapp.com/photos/view?photos=9550c2aa-eb95-4828-b37f-0587fc42d7b7%2C4eb629cb-e16f-4608-967d-540dfb0d0351%2C1c1d9d15-01ab-40a5-8821-404114d6ed0e%2C22516a6f-007a-4120-a5e2-a6a496b02166 | Concrete | Radial Joint | Crack
64e0d9be-b406-4f0c-a0c8-19f401786f11 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-29 23:32:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 99 | 1 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 41954 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 99, 1 o'clock. Concrete Shell Segment. | Failure to seal joint | Failure to seal joint |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Inactive at time of inspection. - Condition rating 4 |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Inactive at time of inspection. - Condition rating 4 | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak remains inactive at time of inspection. No change | no | yes |  | no |  | a8c1cd91-43bb-476b-83a7-f8c22ddc3241,693a0c08-b7af-46f8-b082-ef91386c5eec | , | https://web.fulcrumapp.com/photos/view?photos=a8c1cd91-43bb-476b-83a7-f8c22ddc3241%2C693a0c08-b7af-46f8-b082-ef91386c5eec | Concrete | Circular Joint | Leaks
54180008-e9b0-4447-a7ad-8af2d8f75e01 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:53:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 99 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99542 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 99, 4 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 150 mm x 75 mm |  | Grout Delamination / Drummy Grout at circle joint over an area of 150 mm x 75 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Defect is visible from grid mesh on walkway, however unable to inspect adequately due to poor access underneath. | no | no |  | yes | Priority and risk to be downgraded | 2bb6be24-9dd6-4fbb-99f7-016ef00bb962,a94e88e9-2576-4e01-975d-11b77f9dbdc8 | , | https://web.fulcrumapp.com/photos/view?photos=2bb6be24-9dd6-4fbb-99f7-016ef00bb962%2Ca94e88e9-2576-4e01-975d-11b77f9dbdc8 | Concrete | Circular Joint | Drummy
0b822531-4759-4754-86c6-8ef5c7088368 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-29 23:57:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 100 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99543 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 100, 1 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 200mm x 300mm. |  | Grout Delamination / Drummy Grout at circle joint over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | DR |  | No change to condition of defect. Same area is delaminated and drummy | no | yes |  |  |  | 158ba375-bd0e-44fb-b984-9d35b3bb6822,0413dee5-2902-4ec0-831b-d987428d1a42 | , | https://web.fulcrumapp.com/photos/view?photos=158ba375-bd0e-44fb-b984-9d35b3bb6822%2C0413dee5-2902-4ec0-831b-d987428d1a42 | Concrete | Circular Joint | Drummy
bd3f12bc-5f61-4200-805a-3ec89618e43c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 15:12:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 100 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99544 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 100, 8 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area of 200mm x 100mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area of 200mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Spalled area at lip. This has little structural effect. Suggest downgrading risk and priority | no | no |  | yes | Suggest update priority and risk to low. | 59d00c87-da41-4731-877d-ac6ab957fcbf,ab7adf5a-b8b7-40e6-8b78-e9be4a38724c | , | https://web.fulcrumapp.com/photos/view?photos=59d00c87-da41-4731-877d-ac6ab957fcbf%2Cab7adf5a-b8b7-40e6-8b78-e9be4a38724c | Concrete | Circular Joint | Drummy,Surface Damage
15cf87f9-2579-41cf-89d4-ebd4df111e82 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 21:50:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 101 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 42034 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44046.5217 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 101, 1 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has crack. Insufficient access to measure width, length approximately 300mm. |  | Concrete shell segment has crack. Insufficient access to measure width, length approximately 300mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Doesn't exist at the time of the inspection | yes | no |  | no |  | 83455c17-3157-40dc-9867-a508db52d6f9 |  | https://web.fulcrumapp.com/photos/view?photos=83455c17-3157-40dc-9867-a508db52d6f9 | Concrete | Grout Hole | Crack |  | Grout hole
58c31518-6e73-43d5-a189-a82abaaaee48 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 21:46:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 101 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26820 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 101, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | HM |  | Leak is still active at the time of inspection. Salt deposits on the pipe underneath. | no | yes |  | yes | Priority to be discussed as it's an active leak. | 22add23c-91c5-4861-9c62-420c722496dd,9f7f3fa3-4a42-4b38-8e43-b387447b052e | , | https://web.fulcrumapp.com/photos/view?photos=22add23c-91c5-4861-9c62-420c722496dd%2C9f7f3fa3-4a42-4b38-8e43-b387447b052e | Concrete | Grout Hole,Misc (Pipes/Cable Tray/etc) | Leaks |  | Not reinforcement
e0e48d05-8406-4832-b280-f4459dcefa6d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 21:47:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 101 | 12 | Grout Injection Hole | Grout Injection Hole |  | 85867 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 101, 12 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | No | Walkway | - | Scheduled Maintenance Competent Supervisor | HM |  | This defect is a duplication of the defect at 1 o' clock. | yes | no |  | no |  | 3c11a802-9a87-4662-a58a-d2f990946723,a84ad01e-d289-4e8c-a61a-ea0f2a16fbdf | , | https://web.fulcrumapp.com/photos/view?photos=3c11a802-9a87-4662-a58a-d2f990946723%2Ca84ad01e-d289-4e8c-a61a-ea0f2a16fbdf | Concrete | Grout Hole | Leaks
e4b01d86-3aa8-4594-ac31-2db0ca30976b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:00:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 101 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99545 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 101, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint on two locations over an area of 200mm x 200mm. |  | Grout Delamination / Drummy Grout at radial joint on two locations over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | c2cb1303-d661-48a6-8675-9a166a98a409,365d53ac-c7d4-49a9-a5ba-102ebd97f788,381a0dce-adc4-4aa7-8843-0b9185b01c62 | ,, | https://web.fulcrumapp.com/photos/view?photos=c2cb1303-d661-48a6-8675-9a166a98a409%2C365d53ac-c7d4-49a9-a5ba-102ebd97f788%2C381a0dce-adc4-4aa7-8843-0b9185b01c62 | Concrete | Radial Joint | Drummy
276515de-9364-4e64-a92e-2b3f8bda2c7b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:01:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 101 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41900 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 101, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | a4671207-03f5-4a37-856e-afc9d7668acb,addfa2b6-f81e-470f-a804-4c4b27cd945f | , | https://web.fulcrumapp.com/photos/view?photos=a4671207-03f5-4a37-856e-afc9d7668acb%2Caddfa2b6-f81e-470f-a804-4c4b27cd945f | Concrete | Circular Joint | Drummy
77a58cea-bda5-4674-bdc1-735aa328271f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 21:58:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 102 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85907 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44875.8373 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 102, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion up to 50% coverage. |  | Steel channel support bracket has Level 2 Minor Corrosion up to 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Minor corrosion of the steel bracket. | no | yes |  | no |  | 6db5f3cb-25e3-44f8-b7b1-61e16d8f8e07,3a6dac32-6dae-4886-8c5a-7adfab4f98d5 | , | https://web.fulcrumapp.com/photos/view?photos=6db5f3cb-25e3-44f8-b7b1-61e16d8f8e07%2C3a6dac32-6dae-4886-8c5a-7adfab4f98d5 | Steel | Channel Bracket | Corrosion-Surface
041bf985-29e3-4873-94a6-f49bf1facb0c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 22:13:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 105 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26821 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 105, 11 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | No water evident, however no sign of repair works. May have self healed | no | yes |  | no |  | acb9b2bf-c667-4ae7-85a0-80bd1a2b7874,51f89a8a-2e7b-4546-9252-bb4debcb17ab | , | https://web.fulcrumapp.com/photos/view?photos=acb9b2bf-c667-4ae7-85a0-80bd1a2b7874%2C51f89a8a-2e7b-4546-9252-bb4debcb17ab | Concrete | Grout Hole | Leaks |  | Not reinforcement
6490e537-c966-4321-8341-c88dbdde3143 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:09:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 105 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41901 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 105, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | db772921-1c79-4ec5-8314-d7d4afbe91af |  | https://web.fulcrumapp.com/photos/view?photos=db772921-1c79-4ec5-8314-d7d4afbe91af | Concrete | Circular Joint | Drummy
7ff59e32-27f2-45ce-8de1-710126df1edf | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 22:17:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 106 | 10 | Channel Anchor Bolts | Channel Anchor Bolts |  | 99546 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 106, 10 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | SS |  | This is a single missing bolt. There are 6 others visible, possibly more obscured by pipes. | yes | yes |  | yes | Priority and risk to be downgraded | fba05dc3-641f-4ea2-af85-3625137a3107,09b4dabe-0ca9-4f24-aa2e-3bd5f1a2e697 | , | https://web.fulcrumapp.com/photos/view?photos=fba05dc3-641f-4ea2-af85-3625137a3107%2C09b4dabe-0ca9-4f24-aa2e-3bd5f1a2e697 | Steel | Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Missing
e014945b-6a89-427d-991b-b4d47f0ea96c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:16:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 106 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27432 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | 3 |  | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 106, 9 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. These areas seem patched, with no delamination evident | yes | no |  | yes | Suggest update priority and risk to low. | 35b3944f-8d9a-45cc-8cc3-69b4e87a7811,cf9456ef-9313-4054-81dc-db831db5646d | , | https://web.fulcrumapp.com/photos/view?photos=35b3944f-8d9a-45cc-8cc3-69b4e87a7811%2Ccf9456ef-9313-4054-81dc-db831db5646d | Concrete | Radial Joint | Drummy |  | Not reinforcement
145e4d4d-5e21-42b3-abc8-da340e8f512b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:22:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 107 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41902 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 107, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout delamination / drummy grout over an area of 300 mm x 300 mm. One area of drummy grout spalling with approximate depth of 20mm. |  | Circle joint has grout delamination / drummy grout over an area of 300 mm x 300 mm. One area of drummy grout spalling with approximate depth of 20mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact.Suggest update priority and risk to low. | no | no |  | yes | Suggest update priority and risk to low. | 568ed46b-6df6-4d2a-b5c6-a69dc8be2bea,9fba77ce-8929-4665-aca0-d7ebcf8f2665,9f024ee7-8640-43bd-882c-2d13dca43901 | ,, | https://web.fulcrumapp.com/photos/view?photos=568ed46b-6df6-4d2a-b5c6-a69dc8be2bea%2C9fba77ce-8929-4665-aca0-d7ebcf8f2665%2C9f024ee7-8640-43bd-882c-2d13dca43901 | Concrete | Circular Joint | Drummy,Surface Damage
05268615-feb3-43e9-b739-50332acf72c5 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:24:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 107 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41951 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 107, 8 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Suggest update priority and risk to low. | 28fa947b-a352-478d-8604-5befdc8b6ccb,73281399-e29f-471c-a7fa-277d1baab506 | , | https://web.fulcrumapp.com/photos/view?photos=28fa947b-a352-478d-8604-5befdc8b6ccb%2C73281399-e29f-471c-a7fa-277d1baab506 | Concrete | Grout Hole | Leaks
d0b26253-af43-48d2-b144-7b7d9f053803 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:28:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 108 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42036 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Impact |  | Impact | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Impact Damage from Equipment |  | Impact Damage from Equipment | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 108, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has section of concrete spalled at corner over 200 mm x 50mm. |  | Concrete shell segment has section of concrete spalled at corner over 200 mm x 50mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | HM |  | Minor spalling detected near the grout hole. Priority should be updated to 4 or 5. | yes | no |  | no |  | 8dc4ba39-54c3-4336-b461-fb8dae63179b,211690af-fec9-4948-ae30-560ad92ac292 | , | https://web.fulcrumapp.com/photos/view?photos=8dc4ba39-54c3-4336-b461-fb8dae63179b%2C211690af-fec9-4948-ae30-560ad92ac292 | Concrete | Corner,Grout Hole | Surface Damage
4cb68d6d-bf07-4a0b-9517-4d1c0381129d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:34:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 109 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41903 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 109, 8 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Suggest update priority and risk to low. | 81d47b2b-37a5-4ba7-8ea9-475eee67581b,61717f09-684a-4133-9181-72f96bed0b26 | , | https://web.fulcrumapp.com/photos/view?photos=81d47b2b-37a5-4ba7-8ea9-475eee67581b%2C61717f09-684a-4133-9181-72f96bed0b26 | Concrete | Circular Joint | Drummy
d11c9401-4a69-49ec-a5ca-328cdc5a41c2 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:36:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 110 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69095 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44550.5753 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 110, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 1 Low Corrosion. |  | Channel anchor bolts have Level 1 Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Minor corrosion of the steel channel bracket | no | yes |  | no |  | 9d452316-468e-4a71-9dc7-984642187317,4b20c6c3-66b8-496b-b891-af24c547b9d1 | , | https://web.fulcrumapp.com/photos/view?photos=9d452316-468e-4a71-9dc7-984642187317%2C4b20c6c3-66b8-496b-b891-af24c547b9d1 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
328ce410-ef29-40c8-9664-72dff1be70cf | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 22:24:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 110 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 85870 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 110, 10 & 12 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | SS |  | This is a single bolt that is missing. | yes | no |  | yes | Priority and risk to be downgraded | 2b3ae91d-599b-40b4-9b61-46c710092a93,c900594f-fe45-4fc2-9c23-1845f77712f9 | , | https://web.fulcrumapp.com/photos/view?photos=2b3ae91d-599b-40b4-9b61-46c710092a93%2Cc900594f-fe45-4fc2-9c23-1845f77712f9 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
6f395f30-2eb5-459c-a89f-75765d53cf7f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:49:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 110 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41952 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 110, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. Condition rating 4. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. Condition rating 4. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No leakage evident | no | yes |  | yes | Suggest update priority and risk to low. | 8acc2044-4780-4a20-8694-6c96d8c750ae,f9c7f0e3-1b44-455d-8cb0-2378a01799fe | , | https://web.fulcrumapp.com/photos/view?photos=8acc2044-4780-4a20-8694-6c96d8c750ae%2Cf9c7f0e3-1b44-455d-8cb0-2378a01799fe | Concrete |  | Leaks
a06a5d7a-7bd6-4991-940d-e5617ffe6aaa | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 22:41:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 111 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68874 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 111, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Suggest altering works requirement to monitor. | 15deaf45-a39b-46ba-a9e5-8ecd07c67966 |  | https://web.fulcrumapp.com/photos/view?photos=15deaf45-a39b-46ba-a9e5-8ecd07c67966 | Concrete | Grout Hole | Leaks |  | Not reinforcement
d49a5fd9-282a-4c1d-8d9b-e1f65bfc724e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:53:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 111 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41904 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 111, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 300 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 300 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Suggest update priority and risk to low. | 96d4cf03-61b6-4875-ba8b-ec563690f4d5 |  | https://web.fulcrumapp.com/photos/view?photos=96d4cf03-61b6-4875-ba8b-ec563690f4d5 | Concrete | Circular Joint | Drummy
91f3d268-1281-42e5-a635-712518d1421a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:54:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 111 | 8 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69093 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 111, 8 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints over an area of 200mm x 300mm. |  | Grout Delamination / debonding at radial segment bolted joints over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Suggest update priority and risk to low. | 6cbdf6af-5be7-448f-8a35-85104f27a50a,caa18863-af8c-4d8a-bf34-20e6bacef3dd | , | https://web.fulcrumapp.com/photos/view?photos=6cbdf6af-5be7-448f-8a35-85104f27a50a%2Ccaa18863-af8c-4d8a-bf34-20e6bacef3dd | Concrete | Radial Joint | Drummy
4bf81172-6050-48e6-8f58-3fe255b928f5 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 02:57:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 111 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69096 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 111, 9 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout Delamination / debonding at radial segment bolted joints over an area of 200mm x 100mm. |  | Grout Delamination / debonding at radial segment bolted joints over an area of 200mm x 100mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Suggest update priority and risk to low. | bc285c02-8a22-4f18-ba78-be78affe6cbc,a5c0284d-e45a-428d-aa9d-0c827cdaf913 | , | https://web.fulcrumapp.com/photos/view?photos=bc285c02-8a22-4f18-ba78-be78affe6cbc%2Ca5c0284d-e45a-428d-aa9d-0c827cdaf913 | Concrete | Circular Joint | Drummy |  | Circular Joint
56e59c1d-183c-4e22-94a5-0172d0044077 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 22:40:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 112 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41955 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 112, 12 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Suggest altering works requirement to monitor. | 047d538b-8ee2-4184-b4b8-81d6b348ff02 |  | https://web.fulcrumapp.com/photos/view?photos=047d538b-8ee2-4184-b4b8-81d6b348ff02 | Concrete | Grout Hole | Leaks
904bcdb2-dad1-4e47-bd1d-a006ec73c5cb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:48:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 112 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 42044 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44046.5472 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 112, 2 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | HM |  | Drilled holes for chloride sampling has been filled in at the time of the inspection. Can remove the priority. | yes | no |  |  |  | e1991a65-fdf5-434d-a5f0-4714615477fb |  | https://web.fulcrumapp.com/photos/view?photos=e1991a65-fdf5-434d-a5f0-4714615477fb | Concrete |  | Test Hole
fa555486-8b77-455d-85dd-5140989728a0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 22:39:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 113 | 0 | Grout Injection Hole | Grout Injection Hole |  | 68875 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 113, Various positions. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Suggest altering works requirement to monitor. | 94be80ec-0423-4815-a5ed-33f3d4273cba |  | https://web.fulcrumapp.com/photos/view?photos=94be80ec-0423-4815-a5ed-33f3d4273cba | Concrete | Grout Hole | Leaks |  | Not reinforcement
d36fe100-7fa1-4380-95e9-2272383ab645 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 22:45:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 114 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 85871 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 114, 10 & 12 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. One bolt has level 3 Corrosion. |  | Channel anchor bolt is missing. One bolt has level 3 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. - anchor bolts not missing. and corrosion is Level 2 only. | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | SS |  | This is a single bolt that is missing Corrosion is minor | no | yes |  | yes | Suggest altering works requirement to monitor. | 759b0c97-336a-492b-8c01-31108605aced,f2ce0f92-621d-462c-bffa-964cf29104dd,52f2dfc9-6194-46ae-9770-75156bfe5ee3 | ,, | https://web.fulcrumapp.com/photos/view?photos=759b0c97-336a-492b-8c01-31108605aced%2Cf2ce0f92-621d-462c-bffa-964cf29104dd%2C52f2dfc9-6194-46ae-9770-75156bfe5ee3 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
b8447522-8bf8-4966-8373-26c17414a5cb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:58:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 114 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 85908 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 114, 2 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | HM |  | Missing achor bolt at 3 o' clock position. Not 2 o' clock at noted in the previous inspection. Priority 4. | no | no |  | no |  | 4824c29f-8953-4f99-be9e-3a69bfe88c9c |  | https://web.fulcrumapp.com/photos/view?photos=4824c29f-8953-4f99-be9e-3a69bfe88c9c | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
5d321542-b9b9-4b60-99d2-e80254cf2cca | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 03:05:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 114 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41921 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Carbonation Induced |  | Carbonation Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 114, 8 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 350mm x 350mm. |  | Concrete shell segment has drummy concrete over an area of 350mm x 350mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Suggest update priority and risk to low. | 6bc20d1a-a216-41f9-b9e7-f65daa906f05,51acfbc6-22e2-4339-9d1a-6c71523f11eb | , | https://web.fulcrumapp.com/photos/view?photos=6bc20d1a-a216-41f9-b9e7-f65daa906f05%2C51acfbc6-22e2-4339-9d1a-6c71523f11eb | Concrete | Radial Joint | Drummy |  | Radial Joint Not reinforcement
5bea52be-d472-490c-bed3-6265c743e552 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 05:31:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 115 | 2 | Grout Injection Hole | Grout Injection Hole |  | 68876 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 115, 2 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer | HM |  | Leak is not evident at the time of inspection. It is possible it has been regrouted. Priority to be removed. | yes | no |  | no |  | d68040e8-628f-4ab8-ab40-3fee0c4f920f,085b5891-62cf-4d48-902b-4e5dbd034af1 | , | https://web.fulcrumapp.com/photos/view?photos=d68040e8-628f-4ab8-ab40-3fee0c4f920f%2C085b5891-62cf-4d48-902b-4e5dbd034af1 | Concrete | Grout Hole | Leaks |  | Not reinforcement
2696671a-fc1c-4f14-92b2-8ea78a5666a7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:14:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 116 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26823 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 116, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | HM |  | Severe corrosion to the steel channel bracket. | no | yes |  |  |  | 8559e52e-0689-4b6b-b847-2f88bd75e8b7,f8fab306-d703-4e0b-bf40-ed88155bb797,c4398150-350e-44fa-942c-7fc43b6cddf4,164c42db-4875-4db6-a9dc-9a4e9b84a96f,f5857d2a-ccc2-4df9-9260-0ce16a4875df,9ba48e91-858a-4bee-ab21-5dab1b0e6149 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=8559e52e-0689-4b6b-b847-2f88bd75e8b7%2Cf8fab306-d703-4e0b-bf40-ed88155bb797%2Cc4398150-350e-44fa-942c-7fc43b6cddf4%2C164c42db-4875-4db6-a9dc-9a4e9b84a96f%2Cf5857d2a-ccc2-4df9-9260-0ce16a4875df%2C9ba48e91-858a-4bee-ab21-5dab1b0e6149 | Concrete,Steel | Channel Bracket | Corrosion-Heavy,Leaks |  | Not reinforcement
7233e690-b6fe-4c61-a41d-b2f29d4f9c5a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 00:00:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 116 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27096 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 116, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 - Level 5. Major Corrosion up to 100% coverage. Level 4 corrosion to anchor bolts. |  | Steel channel support bracket has Level 4 - Level 5. Major Corrosion up to 100% coverage. Level 4 corrosion to anchor bolts. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Likely Likelihood of failure, resulting in a Priority 2. | Loss of services. | Priority: P3 |  |  |  | 1. Replace corroded channel, section size and specification to match as per existing or original design. 2. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | HM |  | Severe corrosion the steel channel bracket. Priority 2. | yes | yes |  | no |  | 7c571135-7c89-4ec1-92aa-6b4679d356fa,819b540d-3f64-496c-ad9f-fcbf1ce0e273,45d5bab0-c25e-4271-a0e1-32e375a6c38a | ,, | https://web.fulcrumapp.com/photos/view?photos=7c571135-7c89-4ec1-92aa-6b4679d356fa%2C819b540d-3f64-496c-ad9f-fcbf1ce0e273%2C45d5bab0-c25e-4271-a0e1-32e375a6c38a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
9a6892b7-2818-4434-8184-36b1e73bae39 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 22:47:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 117 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26824 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 117, 1 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak is still evident. Moisture and salt seen. | no | yes |  | no |  | 32bb53ee-07b9-4acb-a43f-22d7f8b2c799,61a9c2ed-5680-4531-8bc1-65717eea25ab | , | https://web.fulcrumapp.com/photos/view?photos=32bb53ee-07b9-4acb-a43f-22d7f8b2c799%2C61a9c2ed-5680-4531-8bc1-65717eea25ab | Concrete | Grout Hole | Leaks |  | Not reinforcement
e2527e28-a3ed-4d61-8902-9d4f54e58b6c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 03:13:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 118 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42492 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 118, 9 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. Condition Rating 5. |  | Grout injection hole has Leak Active at time of inspection. Condition Rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | No water evident, but salt deposits are visible. May have self healed. Should still be treated. | no | yes |  | no |  | eac8f9de-3da9-4629-8ad1-3dfc1c0895ef,9b87c113-72a0-4f86-8e67-cde89a176b62,510057b8-8383-474a-9f13-20f5a8f0d2c1 | ,, | https://web.fulcrumapp.com/photos/view?photos=eac8f9de-3da9-4629-8ad1-3dfc1c0895ef%2C9b87c113-72a0-4f86-8e67-cde89a176b62%2C510057b8-8383-474a-9f13-20f5a8f0d2c1 | Concrete | Grout Hole | Leaks
610d1396-321b-49c7-90da-d0d79c730c9c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 03:14:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 119 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41922 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 20/10/2021 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 119, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Suggest update priority and risk to low. | 9ceee7ca-833d-440b-9a20-efcdf5b4ddb4 |  | https://web.fulcrumapp.com/photos/view?photos=9ceee7ca-833d-440b-9a20-efcdf5b4ddb4 | Concrete | Circular Joint | Drummy |  | Not reinforcement
b8f1f68d-36f3-4bdb-a43a-a523b2ea945c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:02:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 120 | 11 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 69299 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44552.1091 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 120, 11 o'clock. Segmented Bolted Joint (Circle Joint) |  |  |  | Grout Delamination / debonding at circle segment bolted joints |  | Grout Delamination / debonding at circle segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This delamination is minor in area. Additionally, grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Suggest update priority and risk to low. | b7b16511-d2a6-4e28-8e3b-3c27cb359f74,e70bcb6d-c19b-47c9-8d8c-45f56f197fef,5a63486b-12e7-4af7-bcb4-66ac0ee859e9,3fa29915-e16b-43a7-b218-5dd14a5f8d14 | ,,, | https://web.fulcrumapp.com/photos/view?photos=b7b16511-d2a6-4e28-8e3b-3c27cb359f74%2Ce70bcb6d-c19b-47c9-8d8c-45f56f197fef%2C5a63486b-12e7-4af7-bcb4-66ac0ee859e9%2C3fa29915-e16b-43a7-b218-5dd14a5f8d14 | Concrete | Circular Joint | Drummy
4aa09434-dcc4-481a-9c03-ebe6bfef5f0a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 26 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 22:49:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 120 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41958 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 120, 7 o'clock. Concrete Liner Panel. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Hydrophilic Joint Seal (Radial) has Leak - Active at time of inspection. |  | Hydrophilic Joint Seal (Radial) has Leak - Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak is visible at the time of inspection, however the curved footing bracket is showing some advancing corrosion, and there are salt deposits in the area. | no | no |  | yes | Suggest reducing priority to P3 | 2b268461-d53a-45fd-adac-98c18e5a5825,c42c0ec9-73ef-4c70-8dfa-813242dde071,daa25e5c-2ff1-4544-a399-517623e169e0,bd3ff3a5-9c77-4b37-a62d-75446c36d17a | ,,, | https://web.fulcrumapp.com/photos/view?photos=2b268461-d53a-45fd-adac-98c18e5a5825%2Cc42c0ec9-73ef-4c70-8dfa-813242dde071%2Cdaa25e5c-2ff1-4544-a399-517623e169e0%2Cbd3ff3a5-9c77-4b37-a62d-75446c36d17a | Concrete | Conveyor Support | Leaks |  | Conveyor Support
a56850d9-4d9a-4228-b38d-af14f37fac77 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 20 |  |  |  | 2025-07-25 15:12:06 AEST | 2025-07-25 15:35:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 100 | 6 O’clock support base plate and beam |  | Steel Channel Bracket | [17 empty] | 2 | [39 empty] | AC & BP |  | Baseplate and beam corroded |  | yes |  | yes |  | 08f328ba-e30f-4a29-986e-55ec1280f44a,fd72f3b5-59a9-405e-b5af-3beafb340c69,c116790a-d784-4051-9b91-cad37ee20c2c | ,, | https://web.fulcrumapp.com/photos/view?photos=08f328ba-e30f-4a29-986e-55ec1280f44a%2Cfd72f3b5-59a9-405e-b5af-3beafb340c69%2Cc116790a-d784-4051-9b91-cad37ee20c2c | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | centre Support
6a6a5178-1717-419f-b658-8d430ee38c04 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 01:41:33 AEST | 2025-07-25 01:48:55 AEST | 30011704-user5@smec.com | james.stone@smec.com | 100 | 5 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 30% section loss. Base of RSJ and plate is showing 10% section loss |  | no |  | yes | Blank fields to be filled | 8932b491-78cd-4b0a-bb28-10cdf1980ace,fb63edd8-23ae-4dce-aa0b-4fcdf72b2bd9,2c9e84bb-a588-410c-857b-52406fe68acc | ,, | https://web.fulcrumapp.com/photos/view?photos=8932b491-78cd-4b0a-bb28-10cdf1980ace%2Cfb63edd8-23ae-4dce-aa0b-4fcdf72b2bd9%2C2c9e84bb-a588-410c-857b-52406fe68acc | Steel | Centre Support | Corrosion-Heavy
25274911-8d10-44f0-83a5-ae288150ae3e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 02:04:40 AEST | 2025-07-25 02:05:49 AEST | 30011704-user5@smec.com | james.stone@smec.com | 104 | 5 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 30% section loss. Base of RSJ and plate is showing 10% section loss |  | no |  | yes | Blank fields to be filled | e27b2bf7-2052-4868-bbcc-5f7fa52cc109,fbe92043-bbf7-4e9f-8561-4bd12ddc2f62,c54f7f22-0cd4-46b3-89ca-647bd772d4e7,691c5ba7-1157-45ed-865e-334afd9ed05a | ,,, | https://web.fulcrumapp.com/photos/view?photos=e27b2bf7-2052-4868-bbcc-5f7fa52cc109%2Cfbe92043-bbf7-4e9f-8561-4bd12ddc2f62%2Cc54f7f22-0cd4-46b3-89ca-647bd772d4e7%2C691c5ba7-1157-45ed-865e-334afd9ed05a | Steel | Centre Support | Corrosion-Heavy
18880553-f173-4d94-8d7a-1f14c43afaa1 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 02:10:36 AEST | 2025-07-25 02:12:01 AEST | 30011704-user5@smec.com | james.stone@smec.com | 104 | 7 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base of RSJ and plate is showing 10% section loss |  | no |  | yes | Blank fields to be filled | d75142be-94a2-4f40-995b-d769c54da50f,61b62bf2-b815-4662-bedd-47fe1a5a1505,00551810-d75e-466b-a77d-c2c28abbd958,3e0ddd96-1fdb-4a2c-8b31-58ba60dff89f | ,,, | https://web.fulcrumapp.com/photos/view?photos=d75142be-94a2-4f40-995b-d769c54da50f%2C61b62bf2-b815-4662-bedd-47fe1a5a1505%2C00551810-d75e-466b-a77d-c2c28abbd958%2C3e0ddd96-1fdb-4a2c-8b31-58ba60dff89f | Steel | Conveyor Support | Corrosion-Heavy |  | Conveyor Support
0cccf7dc-9437-40a1-b936-1d7e47ffe360 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 02:27:13 AEST | 2025-07-25 02:28:35 AEST | 30011704-user5@smec.com | james.stone@smec.com | 108 | 7 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 5% section loss |  | no |  | yes | Blank fields to be filled | d9bd0a33-b334-48d4-b04a-00de7f36b281,a76148d8-28d5-4312-a977-bb0be475b4c3,afedf938-009c-44d9-97e3-e6e03376a0ce | ,, | https://web.fulcrumapp.com/photos/view?photos=d9bd0a33-b334-48d4-b04a-00de7f36b281%2Ca76148d8-28d5-4312-a977-bb0be475b4c3%2Cafedf938-009c-44d9-97e3-e6e03376a0ce | Steel | Conveyor Support | Corrosion-Heavy |  | Conveyor Support
9ceb4475-61bc-4747-af8b-22478e9b0829 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 02:30:08 AEST | 2025-07-25 02:31:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 108 | 5 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 10% section loss |  | no |  | yes | Blank fields to be filled | 7269c23a-3558-4308-9bed-4f9fc7d3f212,1fa1b398-b07a-4a7a-9e3a-7f7a02d0e634,dd4ca900-0b95-4719-815f-6724ecc4976d | ,, | https://web.fulcrumapp.com/photos/view?photos=7269c23a-3558-4308-9bed-4f9fc7d3f212%2C1fa1b398-b07a-4a7a-9e3a-7f7a02d0e634%2Cdd4ca900-0b95-4719-815f-6724ecc4976d | Steel | Centre Support | Corrosion-Heavy
e15290ec-765f-4bfc-81f4-c3584afbdf0e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 02:59:20 AEST | 2025-07-25 03:00:20 AEST | 30011704-user5@smec.com | james.stone@smec.com | 112 | 7 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 5% section loss |  | no |  | yes | Blank fields to be filled | c13edc26-0c05-4ce5-9b6a-07d881c66279,ca7a5165-1fbd-401f-a153-4bce2194a479,9dc096fd-fa7c-4ea0-8d78-45f11ba37143 | ,, | https://web.fulcrumapp.com/photos/view?photos=c13edc26-0c05-4ce5-9b6a-07d881c66279%2Cca7a5165-1fbd-401f-a153-4bce2194a479%2C9dc096fd-fa7c-4ea0-8d78-45f11ba37143 | Steel | Centre Support | Corrosion-Heavy
e6be1681-c409-4ed5-9baf-d2a50954b4fc | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 03:00:37 AEST | 2025-07-25 03:02:24 AEST | 30011704-user5@smec.com | james.stone@smec.com | 112 | 5 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 10% section loss |  | no |  | yes | Blank fields to be filled | e7ce7e5f-6853-4c02-a7a8-66c83c7c2034,f9982a42-bd64-4f8d-9ed0-8c28f2c467e2 | , | https://web.fulcrumapp.com/photos/view?photos=e7ce7e5f-6853-4c02-a7a8-66c83c7c2034%2Cf9982a42-bd64-4f8d-9ed0-8c28f2c467e2 | Steel | Centre Support | Corrosion-Heavy
fb87fa48-7838-411e-8e0a-f0d1e4341905 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 03:08:12 AEST | 2025-07-25 03:09:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 116 | 7 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 5% section loss |  | no |  | yes | Blank fields to be filled | 0999fd44-e568-4fb4-adaa-330c431fdf06,02693db3-7415-48b7-b3b9-cc750bc46d77,42e529d3-d555-403f-a2b7-e38c0a2fa505,fdacb9e5-593a-47ec-85b9-d296c7d954d3,12385793-69ad-4394-b67a-621cdb816cc4 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=0999fd44-e568-4fb4-adaa-330c431fdf06%2C02693db3-7415-48b7-b3b9-cc750bc46d77%2C42e529d3-d555-403f-a2b7-e38c0a2fa505%2Cfdacb9e5-593a-47ec-85b9-d296c7d954d3%2C12385793-69ad-4394-b67a-621cdb816cc4 | Steel | Conveyor Support | Corrosion-Heavy |  | Conveyor support
5a55d9bd-fd19-440a-8279-72931323a28f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 03:09:16 AEST | 2025-07-25 03:22:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 116 | 5 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate and RSJ is showing roughly 10% section loss |  | no |  | yes | Blank fields to be filled | 3a8c6564-e33c-45cf-832b-d0301d766aec,4605fc0f-3c17-4422-aedc-54052fff249e,d217e5b6-ba64-400c-9edb-35587caf9a14 | ,, | https://web.fulcrumapp.com/photos/view?photos=3a8c6564-e33c-45cf-832b-d0301d766aec%2C4605fc0f-3c17-4422-aedc-54052fff249e%2Cd217e5b6-ba64-400c-9edb-35587caf9a14 | Steel | Centre Support | Corrosion-Heavy
6cdef391-3e69-484c-b911-43f9a2e0534e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 03:15:51 AEST | 2025-07-28 22:50:17 AEST | 30011704-user5@smec.com | james.stone@smec.com | 120 | 7 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 5% section loss |  | no |  | yes | Blank fields to be filled | a4c8ded8-2c98-4891-9032-603b3f7fff2d,4ec1806c-f37f-45a1-8a1c-6ea7b9684cbf,9de664d3-bea4-4757-aea4-78a552377f2e,d746d1b6-b084-401a-a398-5f6386cbb51c | ,,, | https://web.fulcrumapp.com/photos/view?photos=a4c8ded8-2c98-4891-9032-603b3f7fff2d%2C4ec1806c-f37f-45a1-8a1c-6ea7b9684cbf%2C9de664d3-bea4-4757-aea4-78a552377f2e%2Cd746d1b6-b084-401a-a398-5f6386cbb51c | Steel | Conveyor Support | Corrosion-Heavy |  | conveyor support
c2580cf6-2263-4416-b197-7be95c537753 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 21 |  |  |  | 2025-07-25 03:20:49 AEST | 2025-07-25 03:22:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 120 | 5 |  |  | Steelwork footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolts are corroded with section loss. |  |  | Loss of section to failure under load |  |  | Footing bolts and plate are corroding | [18 empty] | SS |  | Nuts are not exposed, assuming 10% section loss based on similar others. RSJ is showing roughly 10% section loss |  | no |  | yes | Blank fields to be filled | 5ac5d44d-ad09-4fbc-95c6-c3a881537b0e,7a28c6ab-bee4-478c-a162-32ffeffc271a | , | https://web.fulcrumapp.com/photos/view?photos=5ac5d44d-ad09-4fbc-95c6-c3a881537b0e%2C7a28c6ab-bee4-478c-a162-32ffeffc271a | Steel | Centre Support | Corrosion-Heavy
126e9d83-4a1e-4a28-9133-c93ca90f4dea | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 18 |  |  |  | 2025-07-25 22:06:19 AEST | 2025-07-25 22:10:29 AEST | 30011704-user5@smec.com | james.stone@smec.com | 102 | 1 |  | Channel Anchor Bolts | [15 empty] | Corrosion - Structure Member/Platework |  | 2 |  |  |  | Health & Safety |  |  | Localised Corrosion ATM |  |  | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Ring 102, 1 o' clock Channel Anchor Bolts |  | Shear failure of bolt |  |  |  | Minor corrosion |  |  | Steel bracket connection liner failure | [15 empty] | HM |  | Minor corrosion of the channel anchor bolt |  | yes |  | no |  | 8b4ddf7c-51cf-41e6-bbef-4f7b7ac12d0b,ad027e22-e547-4c99-ac2c-90aa32de5f40 | , | https://web.fulcrumapp.com/photos/view?photos=8b4ddf7c-51cf-41e6-bbef-4f7b7ac12d0b%2Cad027e22-e547-4c99-ac2c-90aa32de5f40 | Steel | Channel Bracket-Bolt | Corrosion-Surface
09ca859e-88a7-4d22-a91a-011029eb48e0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 18 |  |  |  | 2025-07-25 22:14:51 AEST | 2025-07-25 22:19:11 AEST | 30011704-user5@smec.com | james.stone@smec.com | 106 | 12 |  | Steel Channel Bracket | [15 empty] | Corrosion - Structure Member/Platework |  | 2 |  |  |  | Health & Safety |  |  | Localised Corrosion ATM |  |  | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Ring 106, 12 o' clock, Steel Channel Bracket | [5 empty] | Minor corrosion of the steel channel bracket |  | Loss of minor services (NOT water pipe) | [16 empty] | HM |  | Minor corrosion of the Steel Channel Bracket | [5 empty] | c1938aff-44c9-454e-b82f-317b484dfa4d,5e72411d-b0ef-474b-9142-213fd06fcfe9 | , | https://web.fulcrumapp.com/photos/view?photos=c1938aff-44c9-454e-b82f-317b484dfa4d%2C5e72411d-b0ef-474b-9142-213fd06fcfe9 | Steel | Channel Bracket | Corrosion-Surface
d220c843-6ad1-47ab-a1c7-91ee334627a0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 18 |  |  |  | 2025-07-25 22:50:24 AEST | 2025-07-25 22:53:21 AEST | 30011704-user5@smec.com | james.stone@smec.com | 113 | 3 |  | Grout Injection Hole | [17 empty] | 3 |  |  |  | Health & Safety | [5 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Ring 113, 3 o' clock, grout injection hole |  |  |  |  | Grout injection hole has Leak - Active at time of inspection. | [19 empty] | HM |  | Leak is active at the time of the inspection | [5 empty] | 98101bea-c037-43fc-a216-3a0724f872ba,ae42b3cd-04f1-4578-8b7c-7701004b6110,ccca4e7f-daf0-4e7a-af25-3eb421dcb0f1 | ,, | https://web.fulcrumapp.com/photos/view?photos=98101bea-c037-43fc-a216-3a0724f872ba%2Cae42b3cd-04f1-4578-8b7c-7701004b6110%2Cccca4e7f-daf0-4e7a-af25-3eb421dcb0f1 | Concrete | Grout Hole | Leaks
fbbe66f1-1266-4265-94ff-dd82f8f22bb1 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:08:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 121 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26826 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 121, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Suggest update priority and risk to low. | 7f3b4276-4c77-41bc-9a69-4f49c79667e5,e336235f-e6d8-4c1b-aa76-632af068d7e6 | , | https://web.fulcrumapp.com/photos/view?photos=7f3b4276-4c77-41bc-9a69-4f49c79667e5%2Ce336235f-e6d8-4c1b-aa76-632af068d7e6 | Concrete | Grout Hole | Leaks |  | Not reinforcement
88d987f9-7aeb-4349-995c-20a6fb8e2381 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:34:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 121 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27433 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 121, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | HM |  | Leak is still active at the time of inspection. | no | yes |  |  |  | 382f08af-6bfe-4980-ba0c-28794d7019e1,a63ac322-ff1b-4d1f-91d3-a09ecbcf07ee,5d7bcd33-15b8-4ab2-97fc-038921668f48,dbd56ce4-18b5-481c-913a-ce467af82689 | ,,, | https://web.fulcrumapp.com/photos/view?photos=382f08af-6bfe-4980-ba0c-28794d7019e1%2Ca63ac322-ff1b-4d1f-91d3-a09ecbcf07ee%2C5d7bcd33-15b8-4ab2-97fc-038921668f48%2Cdbd56ce4-18b5-481c-913a-ce467af82689 | Concrete | Grout Hole | Leaks |  | Not reinforcement
0a4182c5-06a7-4bac-ba6f-074062100548 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 03:28:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 121 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85872 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 121, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 250mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | no |  | d6cc6aa6-12f0-4c9d-8b07-c688d375b0ee,a462fd7b-f0d4-4512-b998-36786580dbe8,79dd1e57-5c48-4466-b828-fdcf8c48ae99,c565268b-8e54-4fe4-a49e-487a9081c425 | ,,, | https://web.fulcrumapp.com/photos/view?photos=d6cc6aa6-12f0-4c9d-8b07-c688d375b0ee%2Ca462fd7b-f0d4-4512-b998-36786580dbe8%2C79dd1e57-5c48-4466-b828-fdcf8c48ae99%2Cc565268b-8e54-4fe4-a49e-487a9081c425 | Concrete | Circular Joint | Drummy
14098702-bacd-4afd-ba47-3448ae789704 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:46:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 122 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 85909 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44875.8412 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 122, 2 O'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion |  | Channel anchor bolts have Level 2 Medium Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Steel anchor bolts are corroded at 3 o' clock position | no | no |  |  |  | 2fd1cf99-a2b9-473b-92c0-4cace26addc8,4a0c1f2a-b5ff-450d-8d79-fbb2391bd3d4 | , | https://web.fulcrumapp.com/photos/view?photos=2fd1cf99-a2b9-473b-92c0-4cace26addc8%2C4a0c1f2a-b5ff-450d-8d79-fbb2391bd3d4 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
b30ab65c-b157-43d1-8eff-b0305742978f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 14:46:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 123 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99547 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 123, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 200mm x 200mm. |  | Grout Delamination / Drummy Grout at radial joint over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Update description | 64cd2fc3-cef6-45d0-8319-8e177e774299,6bb8a031-1fb0-460a-855f-55d6cf0daed5,3650e4da-e2f8-4d02-9c12-147601eefd47 | ,, | https://web.fulcrumapp.com/photos/view?photos=64cd2fc3-cef6-45d0-8319-8e177e774299%2C6bb8a031-1fb0-460a-855f-55d6cf0daed5%2C3650e4da-e2f8-4d02-9c12-147601eefd47 | Concrete | Radial Joint | Drummy
04617099-6add-4434-bd31-897631af60fe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:14:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 124 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26827 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 124, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Suggest update priority and risk to low. | c7f27b0d-e66a-4ce5-b06d-9ff5a06724b0,4b2a2826-05a1-4b22-a2b0-81ca44d5e1e7,9a22aa20-b83e-46af-8b48-4aa65791f33f | ,, | https://web.fulcrumapp.com/photos/view?photos=c7f27b0d-e66a-4ce5-b06d-9ff5a06724b0%2C4b2a2826-05a1-4b22-a2b0-81ca44d5e1e7%2C9a22aa20-b83e-46af-8b48-4aa65791f33f | Concrete | Grout Hole | Leaks |  | Not reinforcement
8041e2c7-6e06-44bf-a228-95cc764587dd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 | -20.3217 | 118.5853 | POINT (118.5853398 -20.3216873) | 2025-05-27 20:13:17 AEST | 2025-07-24 23:16:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 125 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26828 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 125, 11 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Small amount of moisture and large amounts of salt deposits seen. | no | yes |  | no |  | 6ea4c951-30b9-4f5b-b23c-f99bcff70e7f,184741f7-6212-4904-b4a8-4e8c4b312917,8ca17581-6a6a-468d-8a43-336dbf106ab3 | ,, | https://web.fulcrumapp.com/photos/view?photos=6ea4c951-30b9-4f5b-b23c-f99bcff70e7f%2C184741f7-6212-4904-b4a8-4e8c4b312917%2C8ca17581-6a6a-468d-8a43-336dbf106ab3 | Concrete | Grout Hole | Leaks |  | Not reinforcement
5bdb797e-8807-4fc6-ad9c-11a460404243 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:19:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 126 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 85873 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 126, 10 & 12 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | SS |  | This is a single bolt that is missing | no | no |  | yes | Suggest update priority and risk to low. | 21914ec9-2723-4bae-8aa9-7a0b8b0d573b,f4afc9fe-82d3-4be6-91b8-a5d92949a34e | , | https://web.fulcrumapp.com/photos/view?photos=21914ec9-2723-4bae-8aa9-7a0b8b0d573b%2Cf4afc9fe-82d3-4be6-91b8-a5d92949a34e | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
829ead90-e019-467c-a7d9-dc0992d98239 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:22:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 126 | 9 | Grout Injection Hole | Grout Injection Hole |  | 99548 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 126, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection- Condition Rating 5 |  | Grout injection hole has Leak Active at time of inspection- Condition Rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | No water evident, but salt deposits are visible. May have self healed. Should still be treated. | no | yes |  |  |  | 9b989044-da70-4564-a637-5aac2f03a4f4,4ad95e0c-eadb-4de8-8e70-ffd1e3961e04 | , | https://web.fulcrumapp.com/photos/view?photos=9b989044-da70-4564-a637-5aac2f03a4f4%2C4ad95e0c-eadb-4de8-8e70-ffd1e3961e04 | Concrete | Grout Hole | Leaks
4c171f5c-be7d-41a2-9376-2d525b79eb6b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:26:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 128 | 10 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85874 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 128, 10 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Suggest update priority and risk to low. | 67db41c0-4a25-4f40-abb8-7f538daf42c1,147b2730-773d-4a0e-9fcb-80f394c12f03 | , | https://web.fulcrumapp.com/photos/view?photos=67db41c0-4a25-4f40-abb8-7f538daf42c1%2C147b2730-773d-4a0e-9fcb-80f394c12f03 | Concrete | Circular Joint | Drummy
764287d1-6f3b-4b09-9b51-3d40607bcb6c | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 | -20.3216 | 118.5853 | POINT (118.585341 -20.3216403) | 2025-05-27 20:13:17 AEST | 2025-07-26 03:37:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 128 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42047 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 128, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 2efe6f94-99dd-4d7f-91db-c3c3b503f73d,28733385-5dc4-4ddc-9a2e-3be57506e86c | , | https://web.fulcrumapp.com/photos/view?photos=2efe6f94-99dd-4d7f-91db-c3c3b503f73d%2C28733385-5dc4-4ddc-9a2e-3be57506e86c | Concrete | Circular Joint | Drummy |  | Not reinforcement
8069b96b-5160-4b6e-bb54-d848cbf2d2c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 03:40:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 129-130 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99549 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Between ring 129 & 130, 8 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at Circle Joint over two areas of 300mm x 100mm. |  | Grout Delamination / Drummy Grout at Circle Joint over two areas of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | e030c1ec-bcdb-4c8f-a879-d1e853a46c14,ef592d81-9605-4cfd-b9e7-97518bf7662f,741bf341-d012-4b15-9618-fc10fb008ffa,4afb64c1-f320-4b48-9f15-a4fb599c2805 | ,,, | https://web.fulcrumapp.com/photos/view?photos=e030c1ec-bcdb-4c8f-a879-d1e853a46c14%2Cef592d81-9605-4cfd-b9e7-97518bf7662f%2C741bf341-d012-4b15-9618-fc10fb008ffa%2C4afb64c1-f320-4b48-9f15-a4fb599c2805 | Concrete | Circular Joint | Drummy
b99745a4-6c55-4c2d-a61f-61c711ec154f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:44:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 129 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26829 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 129, 10 & 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Leak is still inactive. Grout and sealant has been placed along the segment edges, and much of the patched area is delaminated. | no | yes |  | yes | Defect description to include delamination, as well as rectification methods. | 02158ce7-692d-418a-b92c-337ad141f258,10b30c12-8143-4d5e-a6fc-a2ba9ba22249,981dfbef-dab9-4686-b331-d993417897a5 | ,, | https://web.fulcrumapp.com/photos/view?photos=02158ce7-692d-418a-b92c-337ad141f258%2C10b30c12-8143-4d5e-a6fc-a2ba9ba22249%2C981dfbef-dab9-4686-b331-d993417897a5 | Concrete | Circular Joint | Drummy,Leaks |  | Circular joint
36047a2f-ceec-41b9-bd16-fbc58f3d9bcf | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 00:01:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 129 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42493 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 129, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Hydrophilic Joint Seal (Radial Joint) has Leak - Active at time of inspection. Condition rating 5. |  | Hydrophilic Joint Seal (Radial Joint) has Leak - Active at time of inspection. Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | HM |  | Leak is not active at the time of the inspection. Priority to be checked. | no |  |  | yes | Priority to be checked | 49455574-2f1c-4dfd-885c-5a2aa08b88ba |  | https://web.fulcrumapp.com/photos/view?photos=49455574-2f1c-4dfd-885c-5a2aa08b88ba | Concrete | Radial Joint | Leaks
800101e1-12c7-438b-aae8-acf58c388170 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 00:06:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 129 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27434 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 129, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 250mm x 250mm and local spalling. |  | Concrete shell segment has drummy concrete over an area of 250mm x 250mm and local spalling. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | Spalling is still not repaired at the time of inspection | no | no |  | no |  | 67d6067d-4359-4f3f-a42a-8c096472d14d,ce2f66ce-3d56-4c98-9611-d056136db93c | , | https://web.fulcrumapp.com/photos/view?photos=67d6067d-4359-4f3f-a42a-8c096472d14d%2Cce2f66ce-3d56-4c98-9611-d056136db93c | Concrete | Reinforcement | Drummy,Surface Damage
98b0160a-e4d9-495e-a71e-7f4bd089e740 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 00:11:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 129 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 42048 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44046.5553 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Ring 129, 3 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Drilled holes have been filled in at the time of the inspection | yes | no |  |  |  | 2c5c859e-3bf8-4846-aad9-8c4222b9cb51 |  | https://web.fulcrumapp.com/photos/view?photos=2c5c859e-3bf8-4846-aad9-8c4222b9cb51 | Concrete |  | Test Hole
910d3e2f-7f9c-4702-9a37-4bb93850ea69 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:47:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 129 | 0 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 41905 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 129, 9 & 10 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Delamination noted at the bolted connection, and also at the lip of the segments. Should be treated, as this is quite extensive. | no | yes |  | no |  | dfac495b-e0c5-448a-a396-81e8074fa85f,7ddc307c-38ee-4e1a-86d9-bd0cee161579 | , | https://web.fulcrumapp.com/photos/view?photos=dfac495b-e0c5-448a-a396-81e8074fa85f%2C7ddc307c-38ee-4e1a-86d9-bd0cee161579 | Concrete | Circular Joint | Drummy |  | Circular joint not radial
b4b874a0-b5c9-43ea-b4c5-d526140402d0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-28 14:46:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 130 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99551 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 130, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 200mm x 300mm. |  | Grout Delamination / Drummy Grout at radial joint over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | fcf1c48f-7895-4a3c-80d9-6bc0bf0fdc8c,dae4cce5-57b7-4ee3-a8b8-291a38ee938f,00c9d8dd-9bfd-49a3-a596-38d8f0071138,ad0a7959-c2b7-4f67-8720-7b24592ebe8f | ,,, | https://web.fulcrumapp.com/photos/view?photos=fcf1c48f-7895-4a3c-80d9-6bc0bf0fdc8c%2Cdae4cce5-57b7-4ee3-a8b8-291a38ee938f%2C00c9d8dd-9bfd-49a3-a596-38d8f0071138%2Cad0a7959-c2b7-4f67-8720-7b24592ebe8f | Concrete | Radial Joint | Drummy
e1774fb3-6f1f-4e6e-9937-98d24c610106 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 21:47:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 130 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99550 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 130, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 200mm x 200mm. |  | Grout Delamination / Drummy Grout at radial joint over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Suggest reduce severity and risk estimates | b8587a2b-d64e-4370-aea8-b27b61c3bd78,9a3c301d-0ece-4df9-9c7d-661ddd03ccbe | , | https://web.fulcrumapp.com/photos/view?photos=b8587a2b-d64e-4370-aea8-b27b61c3bd78%2C9a3c301d-0ece-4df9-9c7d-661ddd03ccbe | Concrete | Radial Joint | Drummy
d2079d53-6fdf-4cee-a81a-fa7a082ebf1b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 21:52:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 130 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41906 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 130, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150 mm x 300 mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150 mm x 300 mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority change to P3 | 61227878-00ea-410e-b8cd-107af2f2ed48,c1b4f27e-a2fe-4e7c-827e-8d484f25f65f | , | https://web.fulcrumapp.com/photos/view?photos=61227878-00ea-410e-b8cd-107af2f2ed48%2Cc1b4f27e-a2fe-4e7c-827e-8d484f25f65f | Concrete | Circular Joint | Drummy
ed123515-e4dc-4358-9603-5a750cac4f72 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 21:51:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 130 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41959 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 130, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | No leakage seen. Area is delaminated. Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Suggest priority reduce to p3 | 02f8be54-c54f-4303-880a-d1fcdddfc3e1,0e8d2a68-ccdd-4446-ba0e-749b56abd6da | , | https://web.fulcrumapp.com/photos/view?photos=02f8be54-c54f-4303-880a-d1fcdddfc3e1%2C0e8d2a68-ccdd-4446-ba0e-749b56abd6da | Concrete | Circular Joint,Circular Connection | Drummy,Leaks |  | Circual joint and connection
9bb5a904-f8ce-4b79-9e01-ae1498d0cc9e | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 00:03:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 132 | 2 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69098 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 132, 1 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Radial joint seal has Leak Inactive at time of inspection. |  | Radial joint seal has Leak Inactive at time of inspection. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak evident at time of inspection. | no | yes |  | yes | Change description to circle joint. Location is 2 o clock, not 1 | a7c3c37b-4e8a-464f-93ac-c2957888b5fe,a1acf176-6b73-48e1-83a4-def600cef99c | , | https://web.fulcrumapp.com/photos/view?photos=a7c3c37b-4e8a-464f-93ac-c2957888b5fe%2Ca1acf176-6b73-48e1-83a4-def600cef99c | Concrete | Circular Joint,Radial Joint | Leaks |  | Not reinforcement
55fd7f21-049f-4ca5-adc4-9a61a9c1d5b7 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-24 23:54:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 132 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26830 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 132, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Suggest update priority and risk to low. | 20ffd6bf-38f0-4263-9ea8-62498c64bf82,0b146d76-7340-47ec-bb06-1af2440b0aed,a29e1750-79f7-4b77-b9f0-2837ee693a23,c2e9bf4b-c1da-4eb9-90aa-d08edcbf10a7 | ,,, | https://web.fulcrumapp.com/photos/view?photos=20ffd6bf-38f0-4263-9ea8-62498c64bf82%2C0b146d76-7340-47ec-bb06-1af2440b0aed%2Ca29e1750-79f7-4b77-b9f0-2837ee693a23%2Cc2e9bf4b-c1da-4eb9-90aa-d08edcbf10a7 | Concrete | Grout Hole | Leaks |  | Not reinforcement
01d680a6-a0ad-44b5-94ff-74c2de606e60 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:00:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 133 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 41910 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 133, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | no |  | ed661ccd-3a9e-44ce-b612-d5902e117551,20598274-a77f-4988-9cd2-9011564b8e55 | , | https://web.fulcrumapp.com/photos/view?photos=ed661ccd-3a9e-44ce-b612-d5902e117551%2C20598274-a77f-4988-9cd2-9011564b8e55 | Concrete | Radial Joint | Drummy
ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 00:45:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 134 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27435 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Corrosion Under Buildup |  | Corrosion Under Buildup | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 134, 1 & 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 Major Corrosion up to 25% coverage. Channel anchor bolts have Level 2 3 |  | Steel channel support bracket has Level 4 Major Corrosion up to 25% coverage. Channel anchor bolts have Level 2 3 | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of minor services (NOT water pipe) | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | HM |  | Steel channel bracket and anchor bolt is heavily corroded at 1 & 3 o' clock. | no | yes |  | no |  | d77c133a-53e2-4dd4-ba36-bee3907f5285,edaf1aa8-7c72-4636-a99c-8b8ad1cd5496,2be78ddc-c48e-4b69-98d1-e1e2be196de6,cf3ffb0e-df2f-40b3-a53c-02e114f30297,fc7ecf2d-279d-4284-bb44-e094abaf936f,9888b100-0e3e-4f5d-96ed-26a878d29599,f8998f8a-4346-45eb-ac89-2fa69500c9ba,810a9103-0137-459b-adf3-96244c180337,5de84dd3-9b52-4462-8576-5dc02fedb22a,59a2f3d9-5ce7-4ca9-9a22-3d6b71cea106 | ,,,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=d77c133a-53e2-4dd4-ba36-bee3907f5285%2Cedaf1aa8-7c72-4636-a99c-8b8ad1cd5496%2C2be78ddc-c48e-4b69-98d1-e1e2be196de6%2Ccf3ffb0e-df2f-40b3-a53c-02e114f30297%2Cfc7ecf2d-279d-4284-bb44-e094abaf936f%2C9888b100-0e3e-4f5d-96ed-26a878d29599%2Cf8998f8a-4346-45eb-ac89-2fa69500c9ba%2C810a9103-0137-459b-adf3-96244c180337%2C5de84dd3-9b52-4462-8576-5dc02fedb22a%2C59a2f3d9-5ce7-4ca9-9a22-3d6b71cea106 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
3563de4c-7e46-482f-a0ec-88aedcda4768 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 00:50:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 134 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 85910 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44875.8424 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 134, 1 O'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings |  |  |  | Concrete shell segment has cracking - Crack extending 0.5m and 0.3mm in width. |  | Concrete shell segment has cracking - Crack extending 0.5m and 0.3mm in width. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Crack is still evident. | no | yes |  | no |  | 7eb8636e-ef63-4358-9ba1-2126ab435a41 |  | https://web.fulcrumapp.com/photos/view?photos=7eb8636e-ef63-4358-9ba1-2126ab435a41 | Concrete | Radial Joint | Crack |  | Radial Joint
debd1ce5-ca0e-46c6-bda9-cdfb7d4c3e73 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 05:32:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 134 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26832 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 134, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - active at time of inspection. |  | Concrete shell segment at bolted connection penetration has Leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | SS |  | This appears to be a double entry of the same defect at 12 o'clock. See that defect for current update. | no | yes |  | yes | Possible redundant entries. |  |  |  | Concrete | Reinforcement | Leaks |  | Duplicate - Remove
aaec5a64-4502-4839-97e3-8e6c9cf7608b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 05:30:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 134 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85875 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 134, 12 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak seems active, but slow. Bracket and hangers showing advancing corrosion and section loss. Suggest works still required. | no | yes |  | no |  | 045a9432-13d5-4cbd-830c-624b07d61535,ef0c5393-8379-42fc-8507-adb91d07feff,eaf0e58f-4760-401f-9f0e-5cc1018f1328,4542aca2-e18b-4872-9b43-158cc7d89e15 | ,,, | https://web.fulcrumapp.com/photos/view?photos=045a9432-13d5-4cbd-830c-624b07d61535%2Cef0c5393-8379-42fc-8507-adb91d07feff%2Ceaf0e58f-4760-401f-9f0e-5cc1018f1328%2C4542aca2-e18b-4872-9b43-158cc7d89e15 | Concrete | Channel Bracket | Corrosion-Heavy,Leaks |  | Channel bracket
383d50f3-4531-4c3a-8d98-443b92af09c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 03:49:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 134 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99552 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 134, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 300mm x 300mm. |  | Grout Delamination / Drummy Grout at radial joint over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 0e573c0e-7550-41e3-a1fc-545ea5f985fb,e1e7357d-a140-4611-88b7-e6e201d31b05,cbf1391d-cc50-420a-be20-2b7a914c782d | ,, | https://web.fulcrumapp.com/photos/view?photos=0e573c0e-7550-41e3-a1fc-545ea5f985fb%2Ce1e7357d-a140-4611-88b7-e6e201d31b05%2Ccbf1391d-cc50-420a-be20-2b7a914c782d | Concrete | Radial Joint | Drummy
0e4daed3-c796-4773-847f-b8812ad8c5b8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:04:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 135 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 41912 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 20/10/2021 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 135, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 15bd11f9-c8e0-42d1-9219-c0e018f08899,91951779-29e6-4712-b5d9-2c227b95dab6 | , | https://web.fulcrumapp.com/photos/view?photos=15bd11f9-c8e0-42d1-9219-c0e018f08899%2C91951779-29e6-4712-b5d9-2c227b95dab6 | Concrete | Circular Joint,Radial Joint | Drummy
eeaa2e67-c0ba-429f-a820-d1f3e04a9321 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:20:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 136 | 8 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85876 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 136, 8 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | No delam noted in marked area | yes | yes |  | yes | Update description, change action to monitor. | ccd05839-4d5f-400a-af0c-c8d336a9ad51,afd5ae55-9944-4f2c-b559-63f848d41bc4 | , | https://web.fulcrumapp.com/photos/view?photos=ccd05839-4d5f-400a-af0c-c8d336a9ad51%2Cafd5ae55-9944-4f2c-b559-63f848d41bc4 | Concrete | Radial Joint | Drummy
431f13f4-30a6-4a8a-9a63-84e1fda18faf | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:10:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 136 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99553 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 136, 8 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 200 mm x 200 mm |  | Grout Delamination / Drummy Grout at circle joint over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 518d6277-cbd5-4c00-8539-eb959eda7142,b3db6445-d401-4eb8-962c-f0dbc02505f8 | , | https://web.fulcrumapp.com/photos/view?photos=518d6277-cbd5-4c00-8539-eb959eda7142%2Cb3db6445-d401-4eb8-962c-f0dbc02505f8 | Concrete | Circular Joint | Drummy
887f3e3a-e07b-4323-a4b8-306d4d05d7d8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:13:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 136 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69101 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | 4 |  | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 136, 9 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Active at time of inspection. |  | Grout injection hole has leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Previously listed under AIMS defect 41961 under incorrect AIMS quadrant. 41961 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Large salt deposit, water still coming through. This needs to be treated. | yes | yes |  | no |  | 1c211c47-e292-45ae-8ad8-daa1a5a7088a,4b3caefd-02ce-4c57-97fc-2a6cb7190cae,b92b7c1e-026e-4f31-bc04-671d0b06e110,ba45b649-d69a-49d7-b6e2-bb0f584e0664,1afad40b-15fb-43fd-9090-cd3063378110 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=1c211c47-e292-45ae-8ad8-daa1a5a7088a%2C4b3caefd-02ce-4c57-97fc-2a6cb7190cae%2Cb92b7c1e-026e-4f31-bc04-671d0b06e110%2Cba45b649-d69a-49d7-b6e2-bb0f584e0664%2C1afad40b-15fb-43fd-9090-cd3063378110 | Concrete | Grout Hole | Leaks |  | Not reinforcement
17067ec4-fc76-4013-a2c2-fb867d713246 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:18:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 136 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 26833 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing |  |  |  | 4 | [8 empty] | Severity Level 4 | Severity Level 4 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Structure,Ring 136,9 O'Clock,Concrete Element,Still existing in 2017. |  |  |  | Active Leak Grout Injection Hole |  | Active Leak Grout Injection Hole | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | Large salt deposits seen at surface. Affecting the steelwork, extensive corrosion. This needs to be treated. | no | no |  | yes | Increase priority to P2 | 980010c5-5242-4b3e-9f43-969e836f8bf9,b8b537c4-4efd-4cb8-ad30-4f61e37cb3bf,d382f388-3d14-4ed9-83fa-1f35b227fa7a | ,, | https://web.fulcrumapp.com/photos/view?photos=980010c5-5242-4b3e-9f43-969e836f8bf9%2Cb8b537c4-4efd-4cb8-ad30-4f61e37cb3bf%2Cd382f388-3d14-4ed9-83fa-1f35b227fa7a | Concrete | Grout Hole | Leaks
11197ffd-f03f-4ede-8dc1-18fde6e0a681 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 01:21:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 137 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27437 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 137, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | SS |  | Large leak through grout port. Unclear if active. Large salt deposits. This should be treated. | no | yes |  | no |  | d554bd2d-7cb1-4af7-8875-583bfca89b91,33bde6ca-4622-49fe-9d47-b684c3103611,1276c4d9-eacb-4972-b5c0-eca7fb820a19,912557c6-6b72-4bfc-9695-f3fd6c918f22,1673d7a4-6330-480b-8fe5-00b1e1c1909e,03de7e87-38a1-426b-8c1a-10231cebc16c | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=d554bd2d-7cb1-4af7-8875-583bfca89b91%2C33bde6ca-4622-49fe-9d47-b684c3103611%2C1276c4d9-eacb-4972-b5c0-eca7fb820a19%2C912557c6-6b72-4bfc-9695-f3fd6c918f22%2C1673d7a4-6330-480b-8fe5-00b1e1c1909e%2C03de7e87-38a1-426b-8c1a-10231cebc16c | Concrete | Grout Hole | Leaks |  | Not reinforcement
d9fb836e-c6e3-4b9b-8f55-108196102b03 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 05:49:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 137 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27113 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 137, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. - Condition Rating 5 |  | Grout injection hole has Leak Active at time of inspection. - Condition Rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | Large leak through grout port. Unclear if active. Large salt deposits. This should be treated. | no | yes |  | no |  | 048f336c-331c-44ab-be48-a1d1e382f180,0285259a-39db-470b-85c6-70732354b245,aae6bbad-32b0-47cf-bdde-de3776d87ca9 | ,, | https://web.fulcrumapp.com/photos/view?photos=048f336c-331c-44ab-be48-a1d1e382f180%2C0285259a-39db-470b-85c6-70732354b245%2Caae6bbad-32b0-47cf-bdde-de3776d87ca9 | Concrete | Grout Hole | Leaks
222f749a-135e-41c6-b361-e6e484967b47 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 01:18:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 137 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41924 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 137, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | HM |  | Delamination is still evident. Priority 3. | no | no |  | yes | Check the priority. | d5d7338a-e7b7-45ab-b46c-feef257e158f |  | https://web.fulcrumapp.com/photos/view?photos=d5d7338a-e7b7-45ab-b46c-feef257e158f | Concrete | Circular Joint | Drummy |  | Not reinforcement
141e8104-0ec7-40da-bb04-54359c11178b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 03:56:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 137 | 4 | Grout Injection Hole | Grout Injection Hole |  | 69104 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 137, 4 o'clock. Concrete Shell Segment - Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak not detected at the time of inspection. | no | yes |  | yes | Suggest update priority and condition | 174558fe-8dd9-4fa7-af87-61f8c3859668,a0e7be45-4b32-43c8-85c9-ffbb68096833,12bf45da-187b-4a55-a36b-b5cd9b811c3e,2926ca91-bc09-4e97-be33-34722a320eca,91dff720-7a11-4a7f-a930-6f991b6fa261 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=174558fe-8dd9-4fa7-af87-61f8c3859668%2Ca0e7be45-4b32-43c8-85c9-ffbb68096833%2C12bf45da-187b-4a55-a36b-b5cd9b811c3e%2C2926ca91-bc09-4e97-be33-34722a320eca%2C91dff720-7a11-4a7f-a930-6f991b6fa261 | Concrete | Grout Hole | Leaks |  | Not reinforcement
6dcea904-d085-481d-8420-db3025fc0fbc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:29:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 137 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99554 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 137, 7 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 100 mm x 300 mm |  | Grout Delamination / Drummy Grout at circle joint over an area of 100 mm x 300 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 02257ad4-c6f5-49c8-93c3-d5ac102459be,7a13b892-1f45-438d-ae36-10e573ac20f2 | , | https://web.fulcrumapp.com/photos/view?photos=02257ad4-c6f5-49c8-93c3-d5ac102459be%2C7a13b892-1f45-438d-ae36-10e573ac20f2 | Concrete | Circular Joint | Drummy
64fcdc3c-ea6e-4ebe-a6aa-fd339305c307 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:06:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 138 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26834 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Corrosion Under Buildup |  | Corrosion Under Buildup | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 138, 10 & 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel bracket has level 3 corrosion up to 20% coverage. Channel anchor bolts have level 3 corrosion. |  | Steel channel bracket has level 3 corrosion up to 20% coverage. Channel anchor bolts have level 3 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P3. Bolt replacement only, corrosion on channel is Level 2 only. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services | Priority: P3 |  |  |  | Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Scaffolding | Working at Heights, Hot Work | Replace Component Competent Supervisor | SS |  | Suggest that underlying cause of issue is a leak behind the bracket. This is addressed in separate defect | no | yes |  | no |  | cb84358a-1ee0-49fc-9240-a3a08dc12eb5,b304ffc2-232a-4e99-84e0-e1dabbf84399,dafacd1f-a5d3-4602-95d0-56106186da11,56f77b31-ad97-4f9b-89f0-d2f4e38bd74b,acb35c9a-dcc4-49f8-b174-d5d825eefb6b,dfd37fc9-129e-4c3e-a4ae-4e512f136012 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=cb84358a-1ee0-49fc-9240-a3a08dc12eb5%2Cb304ffc2-232a-4e99-84e0-e1dabbf84399%2Cdafacd1f-a5d3-4602-95d0-56106186da11%2C56f77b31-ad97-4f9b-89f0-d2f4e38bd74b%2Cacb35c9a-dcc4-49f8-b174-d5d825eefb6b%2Cdfd37fc9-129e-4c3e-a4ae-4e512f136012 | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks
46fc460e-a0ba-494c-8a96-54a0382bcd62 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 05:55:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 138 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42053 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 138, 10 o'clock. Segmented Bolted Joint (Circle Joint). | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 300 mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 300 mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | yes | no |  | yes | Suggest altering works requirement to monitor. Suggest update priority and risk to low. | 467debd4-4879-4375-958a-6600ba0842f2,be2e32b1-d22b-422e-b74a-d3d89ff8410b | , | https://web.fulcrumapp.com/photos/view?photos=467debd4-4879-4375-958a-6600ba0842f2%2Cbe2e32b1-d22b-422e-b74a-d3d89ff8410b | Concrete | Circular Joint | Drummy
c2fa3dd4-43d2-4f5c-bdca-8fef9de54fb0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:05:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 138 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69105 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 138, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor |  |  |  | no | yes |  | no |  | d8fc9fbb-5979-4485-b878-bab943cfa177,64e24e0c-488f-4eaf-bbe9-da8d389bb2d8,8053c45a-5309-4551-ab91-1698a3336ec0 | ,, | https://web.fulcrumapp.com/photos/view?photos=d8fc9fbb-5979-4485-b878-bab943cfa177%2C64e24e0c-488f-4eaf-bbe9-da8d389bb2d8%2C8053c45a-5309-4551-ab91-1698a3336ec0 | Concrete | Channel Bracket | Leaks |  | Channel Bracket
2fb4e483-6c33-4b3f-a375-3e85983f3dca | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 01:27:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 138 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27097 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 138, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | HM |  | Delamination is evident. | no | yes |  | no |  | f60dfe0e-7607-4515-b662-a6d685d4992a |  | https://web.fulcrumapp.com/photos/view?photos=f60dfe0e-7607-4515-b662-a6d685d4992a | Concrete | Radial Joint | Drummy |  | Not reinforcement
a8304509-aa85-4dd2-9281-f6ebaaa0269f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 03:59:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 138 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99555 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 138, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over two areas of same size 200mm x 200mm. |  | Grout Delamination / Drummy Grout at radial joint over two areas of same size 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Suggest update condition and risk | fe2af408-9d65-4d0c-afd9-b874ad7464ab,6f6ce16c-4a8e-44e2-805e-dc53e532aa87,e5705c84-89d3-4628-8a81-81749b095600 | ,, | https://web.fulcrumapp.com/photos/view?photos=fe2af408-9d65-4d0c-afd9-b874ad7464ab%2C6f6ce16c-4a8e-44e2-805e-dc53e532aa87%2Ce5705c84-89d3-4628-8a81-81749b095600 | Concrete | Radial Joint | Drummy
f023df65-b99b-4f4b-91d4-7d4dd711533d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:10:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 139 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26836 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 139, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | Defect does not seem active, bolt appears pristine. | no | yes |  | yes | This mat have been treated already. Suggest downgrade to monitor... | d17d2477-a793-487a-b840-2786fe87e4c5 |  | https://web.fulcrumapp.com/photos/view?photos=d17d2477-a793-487a-b840-2786fe87e4c5 | Concrete | Grout Hole | Leaks |  | Not reinforcement
523633b6-00c8-4ad5-b66d-af28a7d82129 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:34:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 140 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 41962 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44043.5983 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure, Ring 140, 7 O'Clock, Concrete Element |  |  |  | Non-Active Leak Shell Segment Penetration |  | Non-Active Leak Shell Segment Penetration | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Cannot locate defect to assess. | [5 empty] | a2a95716-88dc-4efd-b786-d28a6fa04a7a |  | https://web.fulcrumapp.com/photos/view?photos=a2a95716-88dc-4efd-b786-d28a6fa04a7a | Concrete |  | Leaks
109f4bd5-c219-42a5-8b77-67d3f03950d3 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:27:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 142 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 85877 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Loose Bolt |  | Loose Bolt | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 142, 10 & 11 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is loose. One bolt is missing at 11. |  | Channel anchor bolt is loose. One bolt is missing at 11. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace loose and missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | SS |  | This is a single bolt that is missing, and another slightly loose. Suggest reducing risk estimate. | no | yes |  | yes | Suggest reduce risk estimate | ea05410b-ae70-4a0b-8e8c-9c3ecf520241,84301d77-9a6c-4568-94b6-3d0846b6cfee,ebe96420-4023-4f8c-a947-003aeb13bc1c,e928c43b-a10d-4ccf-90fc-063cfdf12163 | ,,, | https://web.fulcrumapp.com/photos/view?photos=ea05410b-ae70-4a0b-8e8c-9c3ecf520241%2C84301d77-9a6c-4568-94b6-3d0846b6cfee%2Cebe96420-4023-4f8c-a947-003aeb13bc1c%2Ce928c43b-a10d-4ccf-90fc-063cfdf12163 | Steel | Channel Bracket,Channel Bracket-Bolt | Loose,Missing
90ceded3-5abc-4e24-ae89-53be65caf3f4 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:31:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 143 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26837 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 143, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | Patch has been placed, no leakage evident. | no | yes |  | yes | Suggest removing this defect from the list, as it appears to have been treated... | b95217c6-bd62-44d8-b5d9-89f6d4f240d7,4d158c83-df3c-432c-aef9-db3900320b13 | , | https://web.fulcrumapp.com/photos/view?photos=b95217c6-bd62-44d8-b5d9-89f6d4f240d7%2C4d158c83-df3c-432c-aef9-db3900320b13 | Concrete | Grout Hole | Leaks |  | Not reinforcement
9ab289f6-f7b4-498d-bdfc-58150311d0c5 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:47:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 143 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 42494 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Structure, Ring 143, 7 O'Clock, Concrete Element | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Active Leak Shell Segment Interface |  | Active Leak Shell Segment Interface | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak at interface of shell segments. Carry out leak seal in accordance with approved remediation work scope. | Engineering repair method and specification required. Concrete remediation crew. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer |  |  | No leak identified. | yes | yes |  | no |  | a31084ca-49a9-47a1-9d25-c40b536b6fc5,b61c16c9-9eab-47b7-8936-34063610a5f7 | , | https://web.fulcrumapp.com/photos/view?photos=a31084ca-49a9-47a1-9d25-c40b536b6fc5%2Cb61c16c9-9eab-47b7-8936-34063610a5f7 | Concrete |  | Leaks
7ad72d98-d76b-411b-8cd1-de70d311b8dc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 22:54:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 144 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41964 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 144, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | No bolted connection leak, inactive or otherwise has been identified. | no | yes |  | no |  | 1102c233-2efc-480a-926a-b699b899636e,f9011d44-8021-4bd4-9b07-0b684d5dc098 | , | https://web.fulcrumapp.com/photos/view?photos=1102c233-2efc-480a-926a-b699b899636e%2Cf9011d44-8021-4bd4-9b07-0b684d5dc098 | Concrete |  | Leaks
072ede3b-db09-4382-b7ea-355ee456bfe9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:36:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 145 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26838 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 145, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | Leak appears inactive, however large amounts of salt deposits are visible. This should be treated. | no | yes |  | no |  | a1f58cbf-26a8-4fb5-a7d2-d94822cf7aa7,8ef908c0-2712-4bd2-b46e-cda663dc170e,5034d408-455e-4283-b547-4ca2d1d54a47 | ,, | https://web.fulcrumapp.com/photos/view?photos=a1f58cbf-26a8-4fb5-a7d2-d94822cf7aa7%2C8ef908c0-2712-4bd2-b46e-cda663dc170e%2C5034d408-455e-4283-b547-4ca2d1d54a47 | Concrete | Grout Hole | Leaks |  | Not reinforcement
1cade013-f352-47ee-b7d6-91559ef6d009 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-26 03:29:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 146 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27111 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 146, 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 - Major Corrosion |  | Steel channel support bracket has Level 4 - Major Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor - corrosion is on the edge only. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | Leak causing corrosion | no | yes |  | yes | This issue appears to be due to a small leak behind the bracket. Suggest including leak treatment methodology.. | 62d61bc0-d1bc-43c5-9402-505d1db69135,57af7c89-a9fc-4c99-859f-5ea8679ca412,425ea099-b4d6-4634-bda2-fa3ccf914033,5882b3c1-70f8-4ad5-b81c-4015d09d9f38,79fd18da-75a8-490e-9012-ec5067301f90 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=62d61bc0-d1bc-43c5-9402-505d1db69135%2C57af7c89-a9fc-4c99-859f-5ea8679ca412%2C425ea099-b4d6-4634-bda2-fa3ccf914033%2C5882b3c1-70f8-4ad5-b81c-4015d09d9f38%2C79fd18da-75a8-490e-9012-ec5067301f90 | Steel | Channel Bracket | Leaks
3656cb31-58e3-485a-b23e-e5887d9d7326 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:44:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 146 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 69108 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44550.5884 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 146, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 25% coverage. Channel anchor bolts have Level 3 - Medium Corrosion. |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 25% coverage. Channel anchor bolts have Level 3 - Medium Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Corrosion is not as advanced as stated on this end of the bracket. | no | yes |  | yes | Suggest edit severity and risk downwards. | 43a78402-db86-4d45-ae37-88c3d9c138c3,e029ac16-2fb5-4868-829c-2408e4677be5,a2e722ef-9173-4534-9ec5-f63ce1adfbf0 | ,, | https://web.fulcrumapp.com/photos/view?photos=43a78402-db86-4d45-ae37-88c3d9c138c3%2Ce029ac16-2fb5-4868-829c-2408e4677be5%2Ca2e722ef-9173-4534-9ec5-f63ce1adfbf0 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
99e5ab55-10c7-415f-b20e-ca8f8b62c0a6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:10:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 146 | 8 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 41913 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 146, 8 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | no |  | 9796feb2-3719-48df-9f58-503f6238e97b |  | https://web.fulcrumapp.com/photos/view?photos=9796feb2-3719-48df-9f58-503f6238e97b | Concrete | Radial Joint | Drummy
a0c66409-2f0e-4a4c-a6cc-38609de9149d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:12:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 146 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 42495 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44054.5461 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Structure, Ring 146, 7 O'Clock, Concrete Element |  |  |  | Non-Active Leak Shell Segment Interface |  | Non-Active Leak Shell Segment Interface | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Leak still inactive | no | yes |  | no |  | 7be9d910-b1af-4294-9347-d6239351d06e,6e7469eb-53bc-4e0d-8c4f-b83f43747be0 | , | https://web.fulcrumapp.com/photos/view?photos=7be9d910-b1af-4294-9347-d6239351d06e%2C6e7469eb-53bc-4e0d-8c4f-b83f43747be0 | Concrete |  | Leaks
f0dad168-e3c4-4a95-94ab-e924a4588988 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:48:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 147 | 11 | Grout Injection Hole | Grout Injection Hole |  | 99556 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 147, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection - Condition Rating 4 |  | Grout injection hole has Leak Inactive at time of inspection - Condition Rating 4 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Extremely minor salt intrusion. | no | yes |  | yes | Suggest reduce severity and risk estimates | 55f5d44d-28cb-4716-8d41-314aaa741119,17fcf3bc-05bd-4140-851a-cf228751a924,faefdd16-2fa1-485d-8cc3-4efd445845bf,bdae1384-5452-44ea-ad39-f592854049cb | ,,, | https://web.fulcrumapp.com/photos/view?photos=55f5d44d-28cb-4716-8d41-314aaa741119%2C17fcf3bc-05bd-4140-851a-cf228751a924%2Cfaefdd16-2fa1-485d-8cc3-4efd445845bf%2Cbdae1384-5452-44ea-ad39-f592854049cb | Concrete | Grout Hole | Leaks
c4d1f892-b6b6-49a6-b3be-6445a5d1160b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:52:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 148 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27110 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 148, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | This grout port is showing a medium amount of salts built up, however no moisture evident | no | yes |  | yes | Increase condition rating | 48e93ab7-2d22-43d9-b93d-75bb1270dab8,ff296b50-e7e4-4595-87f9-70eeee027231 | , | https://web.fulcrumapp.com/photos/view?photos=48e93ab7-2d22-43d9-b93d-75bb1270dab8%2Cff296b50-e7e4-4595-87f9-70eeee027231 | Concrete | Grout Hole | Leaks |  | Not reinforcement
ebdae796-dab7-4f96-9bb9-ec01249d3233 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:20:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 148 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85878 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 148, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout and drummy concrete over an area of 400mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout and drummy concrete over an area of 400mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description and priority | e6426162-991f-4dcb-b299-9caca9228b36,77646e20-d50a-47e7-8447-25ce4ad22fc6,bf90a6ee-3c6c-476c-a058-a9d57b9c52b8 | ,, | https://web.fulcrumapp.com/photos/view?photos=e6426162-991f-4dcb-b299-9caca9228b36%2C77646e20-d50a-47e7-8447-25ce4ad22fc6%2Cbf90a6ee-3c6c-476c-a058-a9d57b9c52b8 | Concrete | Circular Joint | Drummy
d0ef7de2-ddff-4fda-88c0-de4574cb290a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:23:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 149 | 4 | Grout Injection Hole | Grout Injection Hole |  | 69109 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 149, 4 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Still active | no | yes |  | no |  | 41697202-670f-4eab-8e31-8ad651f35593,bd6e5570-a951-4165-8491-620e396610e8,6a7dd223-9a7b-470a-b2d0-f2adac02fe65 | ,, | https://web.fulcrumapp.com/photos/view?photos=41697202-670f-4eab-8e31-8ad651f35593%2Cbd6e5570-a951-4165-8491-620e396610e8%2C6a7dd223-9a7b-470a-b2d0-f2adac02fe65 | Concrete | Grout Hole | Leaks |  | Not reinforcement
596e41a3-dbf5-4c85-97b4-4f9b2d5080c6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 07:01:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 150 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41967 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 150, 10 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. Condition rating 5. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Major corrosion due to this leak. Should be treated as a matter of urgency. | no | yes |  | no |  | 6c6ab83e-e8b3-4c39-9d27-f8cd1111d113,7b614505-dd8d-4422-b2bf-500c39b0ae07,f0e2389b-c9e0-442e-89b0-e54c96351401,692a3c1b-4b72-4e74-9679-2e4dc0b6ea19,7e8864ee-1dbc-4c20-9006-808e80852081,908e745d-fe13-4747-b83f-5b04446f6d56,1e838a62-fd4a-4fdc-a31a-c62a46b562c6 | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=6c6ab83e-e8b3-4c39-9d27-f8cd1111d113%2C7b614505-dd8d-4422-b2bf-500c39b0ae07%2Cf0e2389b-c9e0-442e-89b0-e54c96351401%2C692a3c1b-4b72-4e74-9679-2e4dc0b6ea19%2C7e8864ee-1dbc-4c20-9006-808e80852081%2C908e745d-fe13-4747-b83f-5b04446f6d56%2C1e838a62-fd4a-4fdc-a31a-c62a46b562c6 | Concrete | Channel Bracket,Grout Hole | Leaks |  | Cahnnel bracket grout hole
e3a83c78-ce48-49f7-9fae-36f7e5323dbe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 14 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 06:59:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 150 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 26840 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 150, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 - Major Corrosion up to 50% coverage. Channel anchor bolts have level 4 corrosion. |  | Steel channel support bracket has Level 4 - Major Corrosion up to 50% coverage. Channel anchor bolts have level 4 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), revised recommended action to replace corroded anchor bolts and blast and paint. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services. | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. 3. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | Significant section loss, up to 90% in places. Multiple bolts failing. This will need works soon. | no | yes |  | yes | Increase priority, this is getting close to failure | 8aec4480-5969-4434-8634-595bffbebfad,2f93a6b0-54f3-4653-a477-8c53bd6744f6,f95e5914-6197-4658-9209-3b027d591d49,d6e2b017-96a7-46af-a258-91c766aa2b47,e7633f90-0897-4fc1-bf20-c6c32b258e30,4debb331-7b05-4dbd-86c7-ccdba12b1923,8dfa854c-5d84-40a2-b26d-bda905bb3d7e | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=8aec4480-5969-4434-8634-595bffbebfad%2C2f93a6b0-54f3-4653-a477-8c53bd6744f6%2Cf95e5914-6197-4658-9209-3b027d591d49%2Cd6e2b017-96a7-46af-a258-91c766aa2b47%2Ce7633f90-0897-4fc1-bf20-c6c32b258e30%2C4debb331-7b05-4dbd-86c7-ccdba12b1923%2C8dfa854c-5d84-40a2-b26d-bda905bb3d7e | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
5ef6d70d-561f-46a5-9580-934d19e7d80e | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 10 |  |  |  | 2025-07-25 03:26:29 AEST | 2025-07-25 03:33:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 124 | 7 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Curved footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 7 o'clock curved footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 5% section loss |  | no |  | yes | Fill blank fields | edc7189f-afd7-4d24-b285-6babe25d0647,26755449-d00f-4f0e-b4e3-d3dd944342b6,901030b5-5cdc-4bc0-b72c-4c633050158c,0784df72-90e8-4482-8f61-a2b5a5dc29fe | ,,, | https://web.fulcrumapp.com/photos/view?photos=edc7189f-afd7-4d24-b285-6babe25d0647%2C26755449-d00f-4f0e-b4e3-d3dd944342b6%2C901030b5-5cdc-4bc0-b72c-4c633050158c%2C0784df72-90e8-4482-8f61-a2b5a5dc29fe | Steel | Centre Support | Corrosion-Heavy
346e645c-2781-4628-a7c6-ca018732a962 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 10 |  |  |  | 2025-07-25 03:33:12 AEST | 2025-07-25 03:35:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 124 | 5 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 5 o'clock footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate and RSJ are showing roughly 10% section loss |  | no |  | yes | Fill blank fields | b64139f6-b7d0-45a7-849c-4efb48f5ca63,43a08049-c750-44d8-8e7d-70eb4b6a4e9a,4f91ea85-1f86-45ef-8a93-9d9fd436de3f,c6c42ea1-1e33-46a4-9d2f-4147dea5f27c | ,,, | https://web.fulcrumapp.com/photos/view?photos=b64139f6-b7d0-45a7-849c-4efb48f5ca63%2C43a08049-c750-44d8-8e7d-70eb4b6a4e9a%2C4f91ea85-1f86-45ef-8a93-9d9fd436de3f%2Cc6c42ea1-1e33-46a4-9d2f-4147dea5f27c | Steel | Centre Support | Corrosion-Heavy
f84cada6-2f37-456c-b76f-3d2e852af1ba | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 10 |  |  |  | 2025-07-25 03:40:57 AEST | 2025-07-25 03:42:16 AEST | 30011704-user5@smec.com | james.stone@smec.com | 128 | 7 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Curved footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 7 o'clock curved footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 5% section loss |  | no |  | yes | Fill blank fields | 52677a69-e488-4ba9-980f-8a271f393e95,67ea4000-8a43-431b-a416-e2d947965b3f,09ef15ac-24db-4a62-b0d6-3f03663a86e3 | ,, | https://web.fulcrumapp.com/photos/view?photos=52677a69-e488-4ba9-980f-8a271f393e95%2C67ea4000-8a43-431b-a416-e2d947965b3f%2C09ef15ac-24db-4a62-b0d6-3f03663a86e3 | Steel | Centre Support | Corrosion-Heavy
81cbcc23-02d5-476c-a144-e7541a7e800a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 10 |  |  |  | 2025-07-25 03:42:40 AEST | 2025-07-25 03:43:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 128 | 5 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 5 o'clock footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate and RSJ are showing roughly 10% section loss |  | no |  | yes | Fill blank fields | d8fb736f-d971-4b87-8a36-1ea2d61a5550,2b1b9226-cb65-466c-af27-3a00c58e51c8,03c0b8a5-24a0-4306-8b85-8ea0abcbb079 | ,, | https://web.fulcrumapp.com/photos/view?photos=d8fb736f-d971-4b87-8a36-1ea2d61a5550%2C2b1b9226-cb65-466c-af27-3a00c58e51c8%2C03c0b8a5-24a0-4306-8b85-8ea0abcbb079 | Steel | Centre Support | Corrosion-Heavy
aae40368-acd8-4e9c-942e-2325b18f8cfd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 10 |  |  |  | 2025-07-25 06:14:21 AEST | 2025-07-25 06:19:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 139 | 12 |  | Segment Bolted Joint (Radial Joint) | [15 empty] | Corrosion - Connection |  | 3 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Unlikely (Failure within 20 years) |  | Grout pads over bolted connection |  | Failure to seal joint |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | SS |  | Drummy grout. Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. |  | no |  | yes | Fill blank fields | d1a6dc5e-f0ca-41f3-8b75-1cfaeed3c5e6,62b115b1-b13a-40c0-af81-d412d607252f,a4793948-2e45-4019-a6f3-3c340273dce7 | ,, | https://web.fulcrumapp.com/photos/view?photos=d1a6dc5e-f0ca-41f3-8b75-1cfaeed3c5e6%2C62b115b1-b13a-40c0-af81-d412d607252f%2Ca4793948-2e45-4019-a6f3-3c340273dce7 | Concrete | Radial Joint | Drummy
aef5a7b8-bc4c-4984-92a6-e437e6826dcd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 10 |  |  |  | 2025-07-25 06:20:08 AEST | 2025-07-25 06:20:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 141 | 12 |  | Segment Bolted Joint (Radial Joint) | [15 empty] | Corrosion - Connection |  | 3 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Unlikely (Failure within 20 years) |  | Grout pads over bolted connection |  | Failure to seal joint |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | SS |  | Drummy grout. Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. |  | no |  | yes | Fill blank fields | daa55799-ac26-448f-8f68-f7cb32bdd9e5,c135c50d-cd84-4780-bd23-2bf5963f4e6f,225b9ea0-68af-4aa9-98e9-c9a5a8061a39 | ,, | https://web.fulcrumapp.com/photos/view?photos=daa55799-ac26-448f-8f68-f7cb32bdd9e5%2Cc135c50d-cd84-4780-bd23-2bf5963f4e6f%2C225b9ea0-68af-4aa9-98e9-c9a5a8061a39 | Concrete | Radial Joint | Drummy
8edc492f-440e-4a00-81f0-2f19fb6f97cb | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 6 |  |  |  | 2025-07-25 21:57:00 AEST | 2025-07-25 21:57:53 AEST | 30011704-user5@smec.com | james.stone@smec.com | 132 | 5 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 5 o'clock footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Nuts are showing roughly 15% section loss. Base plate and RSJ are showing roughly 10% section loss |  | no |  | yes | Fill blank fields | a772dca6-2e94-4749-a3e1-855400b3fa19,7b100185-72dd-4d46-8617-f78c6acb26e4,6c510e4f-dc6b-4dea-a615-9c57e3b6da73,386950d3-d005-45a4-a87a-623bbd001819 | ,,, | https://web.fulcrumapp.com/photos/view?photos=a772dca6-2e94-4749-a3e1-855400b3fa19%2C7b100185-72dd-4d46-8617-f78c6acb26e4%2C6c510e4f-dc6b-4dea-a615-9c57e3b6da73%2C386950d3-d005-45a4-a87a-623bbd001819 | Steel | Centre Support | Corrosion-Heavy
7b7b88c1-3dfc-47bc-bfca-059c31eade05 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 6 |  |  |  | 2025-07-25 22:21:09 AEST | 2025-07-25 22:26:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 136 | 7 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Curved footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 7 o'clock curved footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Grout hole is leaking adjacent, salts are affecting this footing. Nuts are showing roughly 10% section loss. Base plate is showing roughly 5% section loss |  | no |  | yes | Fill blank fields | 9a391b83-481a-4727-94c1-acc452f0d719,b165d502-43de-4243-ba66-d66fcd00da26,090c8e29-f037-4750-825f-4b295f93d478,84fd8589-72e3-4f5f-8571-ceb2af2dd6be,370ac7b9-1d76-4870-9ee1-88555e7f20cc,91d54b45-3670-4f84-95e1-0073e5f0c8a1 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=9a391b83-481a-4727-94c1-acc452f0d719%2Cb165d502-43de-4243-ba66-d66fcd00da26%2C090c8e29-f037-4750-825f-4b295f93d478%2C84fd8589-72e3-4f5f-8571-ceb2af2dd6be%2C370ac7b9-1d76-4870-9ee1-88555e7f20cc%2C91d54b45-3670-4f84-95e1-0073e5f0c8a1 | Steel | Grout Hole | Corrosion-Heavy,Leaks
e4dc191a-e47e-4fdf-bbdb-af15bcb43fd9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 6 |  |  |  | 2025-07-25 22:36:20 AEST | 2025-07-25 22:40:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 140 | 7 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Curved footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 7 o'clock curved footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Adjacent leak defect from list was not able to be located, however this footing is showing accelerated corrosion as though salts have been deposited. Nuts are showing roughly 10% section loss. Base plate is showing roughly 10% section loss |  | no |  | yes | Fill blank fields | bff15338-136e-41f5-8877-9bb7ea8769f2,32916502-f842-4dd2-b795-1f091a3121cc,3a8d0fac-5565-4c3a-9d95-c1a5feb9d335,61fd9046-19a6-4f10-af59-dc047020dc5e | ,,, | https://web.fulcrumapp.com/photos/view?photos=bff15338-136e-41f5-8877-9bb7ea8769f2%2C32916502-f842-4dd2-b795-1f091a3121cc%2C3a8d0fac-5565-4c3a-9d95-c1a5feb9d335%2C61fd9046-19a6-4f10-af59-dc047020dc5e | Steel | Centre Support | Corrosion-Heavy,Leaks
d2036d0c-4fc5-4cd3-80c8-24e517c99978 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 6 |  |  |  | 2025-07-25 22:42:07 AEST | 2025-07-25 22:43:11 AEST | 30011704-user5@smec.com | james.stone@smec.com | 132 | 5 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 5 o'clock footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Nuts are showing roughly 15% section loss. Base plate and RSJ are showing roughly 10% section loss |  | no |  | yes | Fill blank fields | 37ff5632-9c25-4c48-9f66-7fe75c20a820,cac25a3e-9fea-4175-b3f7-895298c0d862,6d8e5058-bc34-476b-b79f-1704a9cb6fae | ,, | https://web.fulcrumapp.com/photos/view?photos=37ff5632-9c25-4c48-9f66-7fe75c20a820%2Ccac25a3e-9fea-4175-b3f7-895298c0d862%2C6d8e5058-bc34-476b-b79f-1704a9cb6fae | Steel | Centre Support | Corrosion-Heavy
4545d5d4-4261-4c10-99d4-d55c3457b7dc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 6 |  |  |  | 2025-07-25 22:57:26 AEST | 2025-07-25 22:58:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 144 | 5 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 5 o'clock footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Nuts are showing roughly 15% section loss. Base plate and RSJ are showing roughly 10% section loss |  | no |  | yes | Fill blank fields | 10cf6696-9bbd-4e01-8c18-cb59796e9cf0,b36a0159-c164-4df3-b673-04cee0b07bfd,84670683-461b-4c6a-bbcd-4ea8717c85c9 | ,, | https://web.fulcrumapp.com/photos/view?photos=10cf6696-9bbd-4e01-8c18-cb59796e9cf0%2Cb36a0159-c164-4df3-b673-04cee0b07bfd%2C84670683-461b-4c6a-bbcd-4ea8717c85c9 | Steel | Centre Support | Corrosion-Heavy
f19aeb91-d25e-4824-8d63-e8dcdc15ee04 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 6 |  |  |  | 2025-07-25 23:17:06 AEST | 2025-07-25 23:17:53 AEST | 30011704-user5@smec.com | james.stone@smec.com | 148 | 5 |  |  | Steel footing plate | [14 empty] | Corrosion - Connection |  | 4 | [6 empty] | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Footing plate and bolted connection |  | Shear failure of bolt |  |  |  | 5 o'clock footing plate and bolts are showing corrosion |  |  | Conveyor failure | [15 empty] | SS |  | Nuts are showing roughly 15% section loss. Base plate and RSJ are showing roughly 10% section loss |  | no |  | yes | Fill blank fields | 602236ac-6e84-46d5-b1e8-03ff46d6e67d,cae8d23b-0e84-45a8-8fc5-a7ac5c898445,942b882e-0fa2-4c5b-b524-3112674a9ec0 | ,, | https://web.fulcrumapp.com/photos/view?photos=602236ac-6e84-46d5-b1e8-03ff46d6e67d%2Ccae8d23b-0e84-45a8-8fc5-a7ac5c898445%2C942b882e-0fa2-4c5b-b524-3112674a9ec0 | Steel | Centre Support | Corrosion-Heavy
afa45073-e8c6-40dc-8de9-066f5c506b6a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 6 |  |  |  | 2025-07-26 03:50:20 AEST | 2025-07-26 03:52:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 135 | 4 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Leak | 4 | [14 empty] | Grout hole |  |  |  |  | Grout injection hole has Leak - Active at time of inspection. | [19 empty] | SS |  | Large salt deposits, and moisture |  | yes |  | yes | Fill blank fields | f5c7ec6d-9532-4ed8-94b8-2b93c6158425,2aa90147-ca84-4184-b054-938be39279e4,dd6e1ffa-7d25-4b37-9cde-324d84846b79 | ,, | https://web.fulcrumapp.com/photos/view?photos=f5c7ec6d-9532-4ed8-94b8-2b93c6158425%2C2aa90147-ca84-4184-b054-938be39279e4%2Cdd6e1ffa-7d25-4b37-9cde-324d84846b79 | Concrete | Grout Hole | Leaks
64540b4a-7839-4db1-8e19-457aa72832fa | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 8 |  |  |  | 2025-07-26 00:11:55 AEST | 2025-07-26 00:14:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 129 | 3 |  | Grout Injection Hole | [17 empty] | 3 | [9 empty] | Severity Level 4 |  |  | Unlikely (Failure within 20 years) |  | Ring 129, 3 o' clock, grout injection hole leak |  |  |  |  | Grout injection hole has Leak - Active at time of inspection. | [19 empty] | HM |  | Grout injection hole leak active at the time of the inspection. Priority 3. | [5 empty] | 3c121795-1042-4e8e-8d95-a15784cded50,17ed5f55-ca9c-48c8-b66f-8c77f5a74027,9d0f658b-3f36-418d-892d-187850d72c71 | ,, | https://web.fulcrumapp.com/photos/view?photos=3c121795-1042-4e8e-8d95-a15784cded50%2C17ed5f55-ca9c-48c8-b66f-8c77f5a74027%2C9d0f658b-3f36-418d-892d-187850d72c71 | Concrete | Grout Hole | Leaks
51bb57ab-a0a2-4254-a00e-1b00e3d114dd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 8 |  |  |  | 2025-07-26 00:23:28 AEST | 2025-07-26 00:25:54 AEST | 30011704-user5@smec.com | james.stone@smec.com | 130 | 3 |  | Channel Anchor Bolts | [27 empty] | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Ring 130, 3 o' clock, missing anchor channel bolt |  |  |  |  | Channel anchor bolt is missing. | [19 empty] | HM |  | Anchor channel bolt is missing. | [5 empty] | c5c5c46c-e585-4edf-a2b5-482a7eaeb322 |  | https://web.fulcrumapp.com/photos/view?photos=c5c5c46c-e585-4edf-a2b5-482a7eaeb322 | Steel | Channel Bracket-Bolt | Missing
e197d5f3-117b-4d73-a487-22df8187f956 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 8 |  |  |  | 2025-07-26 00:27:40 AEST | 2025-07-26 00:30:17 AEST | 30011704-user5@smec.com | james.stone@smec.com | 131 | 2 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [17 empty] | 2 | [6 empty] | Poor Construction Methods |  |  | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Ring 131, 2 o' clock, spalled concrete | [5 empty] | Spalled concrete | [18 empty] | HM |  | Exposed rebar due to spalled concrete | [5 empty] | da78caef-d92e-4c89-9b0c-dcc7a1539eac,fcee5589-c6f1-43f7-813a-516c26a62649 | , | https://web.fulcrumapp.com/photos/view?photos=da78caef-d92e-4c89-9b0c-dcc7a1539eac%2Cfcee5589-c6f1-43f7-813a-516c26a62649 | Concrete | Reinforcement | Surface Damage
1617d1b3-9d83-460a-8a01-ee2eba215935 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 7 |  |  |  | 2025-07-26 03:41:24 AEST | 2025-07-26 03:44:15 AEST | 30011704-user5@smec.com | james.stone@smec.com | 150 | 3 |  | Channel Anchor Bolts | [17 empty] | 2 | [9 empty] | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Ring 150, 3 o' clock, channel anchor bolt missing | [5 empty] | Missing anchor channel bolt | [18 empty] | HM |  | Bolt is missing from the anchor channel | [5 empty] | ddfb31d0-8fb4-4c25-8266-5e95de75f0e3 |  | https://web.fulcrumapp.com/photos/view?photos=ddfb31d0-8fb4-4c25-8266-5e95de75f0e3 | Steel | Channel Bracket-Bolt | Missing
6bcb124f-7e46-41d8-9ede-92f496c0cf71 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:36:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 151 | 0 | Grout Injection Hole | Grout Injection Hole |  | 68877 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 151, 1 & 2 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | No change | no | yes |  | no |  | b6f472ea-25b1-43b6-ac51-f63840424501,63071f1c-e0b4-45fe-97c3-310c353624e5 | , | https://web.fulcrumapp.com/photos/view?photos=b6f472ea-25b1-43b6-ac51-f63840424501%2C63071f1c-e0b4-45fe-97c3-310c353624e5 | Concrete | Grout Hole | Leaks |  | Not reinforcement
98fd9997-c332-44fa-b796-5e644c245f9f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 23:37:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 152 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26842 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 152, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | No change | no | yes |  | no |  | 7db07702-c633-46db-951a-4f3cff5b8170,e4cfbdb7-5de3-4c8a-98c6-40fccfef81a0 | , | https://web.fulcrumapp.com/photos/view?photos=7db07702-c633-46db-951a-4f3cff5b8170%2Ce4cfbdb7-5de3-4c8a-98c6-40fccfef81a0 | Concrete | Grout Hole | Leaks |  | Not reinforcement
f30e2143-ce1d-4255-a155-cc0e21399236 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 17:32:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 152 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41970 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 152, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | BP |  | No defect | no | no |  | yes | [8 empty] | Defect not present - consider removing
5ac89e87-82be-4a89-9d1b-174fdd457155 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 | -20.3218 | 118.5853 | POINT (118.5852756 -20.3217662) | 2025-05-27 20:13:17 AEST | 2025-07-25 23:39:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 153 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69111 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 153, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | BP |  | Bolt hole sealed with grout. Good condition, no leak, Low risk | no | yes |  | no | Remediated. | 996f316a-f350-4a40-b356-0220db4cd6be,4436e8f6-f2f7-4167-b7b0-bcd5f5d0f5ba,75d58f15-8605-4e01-83db-475abd4cc269,c8641fbe-d8fb-44bd-b6cf-edb960e0c5d2 | ,,, | https://web.fulcrumapp.com/photos/view?photos=996f316a-f350-4a40-b356-0220db4cd6be%2C4436e8f6-f2f7-4167-b7b0-bcd5f5d0f5ba%2C75d58f15-8605-4e01-83db-475abd4cc269%2Cc8641fbe-d8fb-44bd-b6cf-edb960e0c5d2 | Concrete | Grout Hole | Leaks |  | Not reinforcement
1c621936-ea14-4372-9564-c7d2de1a26f4 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 17:35:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 153 | 2 | Grout Injection Hole | Grout Injection Hole |  | 68878 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 153, 2 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | BP |  | No change.Low risk | [8 empty] | Concrete | Grout Hole | Leaks |  | Not reinforcement
032abeeb-a73e-46bf-8d5a-1b882362d624 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 17:36:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 153 | 4 | Grout Injection Hole | Grout Injection Hole |  | 85879 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 153, 4 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | BP |  | NO LEAK, Low risk | [8 empty] | Concrete | Grout Hole | Leaks
19c9ea78-d7fd-47b6-9c24-33a5eaaf171d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 16:57:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 155 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68879 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 155, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | BP |  | Slight stalactite formed, non active leak. Low Risk. | no |  |  | yes |  | 5bad25e6-6a48-4405-a6e1-0e530521781f,fd0d10f9-0971-4051-9fb1-c92193ad6246 | , | https://web.fulcrumapp.com/photos/view?photos=5bad25e6-6a48-4405-a6e1-0e530521781f%2Cfd0d10f9-0971-4051-9fb1-c92193ad6246 | Concrete | Grout Hole | Leaks |  | Not reinforcement
1d205ac2-371c-481a-b10a-4045187437c2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 17:47:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 156 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69115 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 156, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer | BP |  | Grout injection hole. Inactive leaks behind channel.Low risk. | no | yes |  | yes |  | 7c5bb5dd-7aa7-439f-bed3-1f8880fedbb7 |  | https://web.fulcrumapp.com/photos/view?photos=7c5bb5dd-7aa7-439f-bed3-1f8880fedbb7 | Concrete | Grout Hole | Leaks |  | Not reinforcement
94a6f108-47de-4a25-b63f-a512a2e43730 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-30 05:53:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 157 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27109 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 157, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Very Rare Likelihood of failure, resulting in a Priority 4. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer | HM |  | Grout leak is inactive at the time of inspection. It is possible leak has been fixed. | no | yes |  | no |  | fb0983a1-d3c9-4cbd-8c37-c934bc766f1d,0ae4cec9-0257-4cbe-98a4-5babb0f08cfc | , | https://web.fulcrumapp.com/photos/view?photos=fb0983a1-d3c9-4cbd-8c37-c934bc766f1d%2C0ae4cec9-0257-4cbe-98a4-5babb0f08cfc | Concrete | Grout Hole | Leaks
432fcdf4-7714-43ec-8423-b6fbb3786aad | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 16:59:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 157 | 0 | Grout Injection Hole | Grout Injection Hole |  | 68880 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 157, 10 & 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | BP |  | Grout filled bolt hole. No leak - low risk | yes | no |  | yes |  | dbbd3c00-0c7e-4653-bf6a-db16ce226e84 |  | https://web.fulcrumapp.com/photos/view?photos=dbbd3c00-0c7e-4653-bf6a-db16ce226e84 | Concrete | Grout Hole | Leaks |  | Not reinforcement
1b8af2d8-2e9e-44f2-86ed-a88c087291cf | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-29 23:21:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 157 | 4 | Grout Injection Behind Ring | Grout Injection Behind Ring |  | 69120 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 157, 4 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout |  | Break up of grout | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Financial, Severity Level 1 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak remains inactive at time of inspection. Grout plug condition unknown. Medium priority. | no | no | Medium priority. |  |  | 2b95e20f-e53d-4d53-966c-e4b2eb9160e0,73cebea0-3e74-4009-8092-fcefc0e41d18 | , | https://web.fulcrumapp.com/photos/view?photos=2b95e20f-e53d-4d53-966c-e4b2eb9160e0%2C73cebea0-3e74-4009-8092-fcefc0e41d18 | Concrete | Grout Hole | Leaks |  | Not reinforcement
2370748b-7ebb-4880-b009-9060da5f0c6d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 17:00:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 158 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 69122 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 2 | Level 2 | Level 2 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 158, 10 & 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 100% coverage. Channel anchor 2 bolts are missing. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 100% coverage. Channel anchor 2 bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor | BP |  | Section cut & removed, need concrete repair 150 x 60mm ( 20mm deep) -low risk | yes |  |  | yes |  | f878161c-fb73-4167-82d3-f2a93625d8c9 |  | https://web.fulcrumapp.com/photos/view?photos=f878161c-fb73-4167-82d3-f2a93625d8c9 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Surface Damage |  | Surface damage not Corrossion
dcb9bc3b-96d3-46e0-a535-cdd5c055a9c9 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 02:09:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 158 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69118 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 158, 12 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has section cut / broken out and has not been repaired. |  | Concrete shell segment has section cut / broken out and has not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), downgraded to P3 and monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | BP |  | No change | no |  |  | no |  | a12b5c26-d698-49fd-a02f-5fe7c5f553fa,893810e3-6f8b-4fb5-926f-de55de96f439 | , | https://web.fulcrumapp.com/photos/view?photos=a12b5c26-d698-49fd-a02f-5fe7c5f553fa%2C893810e3-6f8b-4fb5-926f-de55de96f439 | Concrete |  |  |  | Duplicate - Remove
81923c34-5394-4c0d-9186-0c3fc765c9fe | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-29 23:16:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 159 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27438 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 159, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | Dr |  | Radial joint remains delaminated with the same size. No change to the defect. | no | yes |  |  |  | d0bf9f15-4cdf-4bd7-a13a-1f27f14cbe1d |  | https://web.fulcrumapp.com/photos/view?photos=d0bf9f15-4cdf-4bd7-a13a-1f27f14cbe1d | Concrete | Radial Joint | Drummy |  | Not reinforcement
31b29bee-2906-4fc9-95ec-f1bde1fac971 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-31 01:45:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 159 | 0 | Grout Injection Hole | Grout Injection Hole |  | 85880 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 159, 10 to 11 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - Inactive at time of inspection. |  | Grout injection hole has leak - Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | BP AA |  | Dried leaching salts . Leak is dry and no evidence or continuous leakings low risk | no |  |  | yes |  | e9f5c6c4-3277-4a66-ab84-88d171e6baf3,1470dce5-4eb0-4791-876b-74db09b26f86 | , | https://web.fulcrumapp.com/photos/view?photos=e9f5c6c4-3277-4a66-ab84-88d171e6baf3%2C1470dce5-4eb0-4791-876b-74db09b26f86 | Concrete | Grout Hole | Leaks
3ae9ee7d-8506-469e-955c-3bf208e59b2c | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-27 17:03:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 159 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 69123 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.6094 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 159, 2 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | AA |  | Aggregate exposed Leajk | [5 empty] | 02a51f70-b9b9-494c-9a2a-dfdfe3c52253 |  | https://web.fulcrumapp.com/photos/view?photos=02a51f70-b9b9-494c-9a2a-dfdfe3c52253 | Concrete |  | Test Hole
69953d3d-ea1b-4242-8d81-fd4eb6c74339 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-29 23:15:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 159 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26843 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 159, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | Dr |  | Leak remains inactive at time of inspection. | no | yes |  |  |  | 2acba1fe-9704-49ee-867d-c98ded834f68 |  | https://web.fulcrumapp.com/photos/view?photos=2acba1fe-9704-49ee-867d-c98ded834f68 | Concrete | Grout Hole,Reinforcement | Leaks
08c262a7-1d05-4817-91a9-b231e4a1e81c | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:17 AEST | 2025-07-25 18:40:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 160 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68881 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 160, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | BP |  | Aggregate rough surface, no leak | no | no |  | yes |  | b97e26da-86da-4ef9-b632-9a3c64f57c7b |  | https://web.fulcrumapp.com/photos/view?photos=b97e26da-86da-4ef9-b632-9a3c64f57c7b | Concrete | Grout Hole | Leaks |  | Not reinforcement
5c4e3434-5a4e-43de-ad15-d202824b207a | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:04:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 161 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27107 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 161, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. Etching below previous leak. - Condition rating 4 |  | Grout injection hole has Leak Inactive at time of inspection. Etching below previous leak. - Condition rating 4 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | BP |  | Aggregate surface grout hole | no |  |  | no |  | 13a94414-08dc-4211-93d3-419b2783ea62 |  | https://web.fulcrumapp.com/photos/view?photos=13a94414-08dc-4211-93d3-419b2783ea62 | Concrete | Grout Hole | Leaks
647adb88-42a8-439e-b69f-015b3203d437 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-31 01:26:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 161 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69125 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 161, 2 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | Dr |  | Leak still remains inactive at time of inspection. Grout plug is in good condition. Low priority defect | no | no | Low | no |  | 25e301d3-bb14-48c5-b1ee-24d0da511abc,558be3d2-fff7-44a8-a5b1-be645f15b46e | , | https://web.fulcrumapp.com/photos/view?photos=25e301d3-bb14-48c5-b1ee-24d0da511abc%2C558be3d2-fff7-44a8-a5b1-be645f15b46e | Concrete | Grout Hole,Reinforcement | Leaks
6b0aae3a-692b-4c0d-ba17-1496d5b2bda2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:06:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 161 | 9 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99557 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 161, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial Joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Radial Joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AC BP |  | Small surface crack 9 O’Clock. No defect 7 O’Clock position. Low risk | [5 empty] | 5baab012-a6c2-48eb-99df-df4306ce7014,bef5f32b-a413-40a9-bff9-15f3a38f41ef | , | https://web.fulcrumapp.com/photos/view?photos=5baab012-a6c2-48eb-99df-df4306ce7014%2Cbef5f32b-a413-40a9-bff9-15f3a38f41ef | Concrete | Circular Joint | Crack,Drummy |  | Circular joint not radial
c203dd29-9da1-47cb-8250-f038472f74d9 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-31 01:23:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 161 | 7- consider removing entry | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 69126 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.6124 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 161, 7 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Duplicated defect. Can be removed from list. | yes | no | No priority. | yes | Remove defect. Duplicated. |  |  |  | Concrete |  | Test Hole |  | Duplicate - Remove
7459ed16-f586-4036-a277-cedae4c732f6 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-30 05:47:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 163 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26844 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 163, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | HM |  | Grout hole leak is inactive at the time of the inspection. Grout hole has been closed off. | yes | no | 4 | yes | Remove priority as this defect has been fixed. | 3f9fb810-1ff6-4c0b-91ef-553524ff2143,d3175c42-875d-43b5-b9f2-d70c7c8d135e | , | https://web.fulcrumapp.com/photos/view?photos=3f9fb810-1ff6-4c0b-91ef-553524ff2143%2Cd3175c42-875d-43b5-b9f2-d70c7c8d135e | Concrete | Grout Hole | Leaks |  | Not reinforcement
09d4b046-e291-4caa-bfb1-f4e7cc8b3299 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-31 01:20:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 163 | 4,5 o’clock Consider removing entry | Grout Injection Hole | Grout Injection Hole |  | 85881 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 163, 4 to 5 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | Dr |  | No evidence of leak present at grout injection hole. Defect can be removed. | yes | no | No priority | no |  |  |  |  | Concrete | Grout Hole | Leaks
4c643bd5-60f9-4b26-b67e-b5e854d79209 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:19:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 164 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85882 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 10/11/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 164, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Break out grout locally, abrasive blast steelwork, and inspect by competent engineer to develop repair detail. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | BP |  | Inactive leak behind steel bracket. Low risk | no | yes |  | no |  | 8e39182b-61ee-4b09-9b91-f45043ad28ff |  | https://web.fulcrumapp.com/photos/view?photos=8e39182b-61ee-4b09-9b91-f45043ad28ff | Steel | Circular Joint | Drummy,Leaks
67fcc57b-c6cf-42fd-b8d9-9f4ef18a7ff3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 18:55:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 164 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41971 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 164, 9 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. Condition rating 4. |  | Grout injection hole has Leak Inactive at time of inspection. Condition rating 4. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | BP |  | Stalactite from grout hole | yes | no |  | no |  | e4ef72ed-ca0f-4261-bba3-0952c8d679a6,1c644a43-7e83-419b-a0c1-f813fd13d212 | , | https://web.fulcrumapp.com/photos/view?photos=e4ef72ed-ca0f-4261-bba3-0952c8d679a6%2C1c644a43-7e83-419b-a0c1-f813fd13d212 | Concrete | Grout Hole | Leaks
19ec8717-8b46-4dd5-be1d-117e1ed24dc4 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 18:59:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 166 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 69129 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 166, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Three channel anchor bolts are missing. |  | Three channel anchor bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor | BP |  | Snapped bolts | no |  |  |  |  | 8ba0c055-3f91-4e24-aea6-16e9df08d301,78d6672d-facb-4877-baf3-f2d718eeefde | , | https://web.fulcrumapp.com/photos/view?photos=8ba0c055-3f91-4e24-aea6-16e9df08d301%2C78d6672d-facb-4877-baf3-f2d718eeefde | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
48d55c66-fb66-45d5-bc2b-4d0d1fb15434 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:21:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 166 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99558 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 166, 7 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle Joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle Joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | BP |  | No defect | no | [7 empty] | Concrete | Circular Joint | Drummy
955558f7-2eed-497a-b9d7-320e810e86f2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 19:00:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 166 | 7 | Grout Injection Hole | Grout Injection Hole |  | 69131 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 166, 7 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AC |  |  | no | [7 empty] | Concrete | Grout Hole | Leaks |  | Not reinforcement
3d18012e-a494-4f85-a0cd-93df985c2c06 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-31 01:34:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 167 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68882 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 167, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | BP |  | Big spread stalactite drips from grout injection hole. Leak remains active. High priority defect. |  | no | High |  |  | 3a575d20-10f6-4265-a2b2-9f568e8fd700,6a3d7906-b64f-4603-b19f-922426027e83,d3bf7479-0c34-4d2f-b0b2-59f5156eed18 | ,, | https://web.fulcrumapp.com/photos/view?photos=3a575d20-10f6-4265-a2b2-9f568e8fd700%2C6a3d7906-b64f-4603-b19f-922426027e83%2Cd3bf7479-0c34-4d2f-b0b2-59f5156eed18 | Concrete | Grout Hole | Leaks |  | Not reinforcement
ea0534b9-cad0-4c50-b906-c69b5ec18285 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 19:07:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 167 | 7 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 41914 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44043.3886 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Structure, Ring 167, 7 O'Clock, Concrete Element |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | A.Acero |  | Stalactite building up from issue at 11 o’clock | [5 empty] | a8dda843-df2c-4e66-a807-c02066ef9c04 |  | https://web.fulcrumapp.com/photos/view?photos=a8dda843-df2c-4e66-a807-c02066ef9c04 | Concrete | Radial Joint | Drummy
31436f12-35af-4702-a006-8e43c19ca6c8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-30 05:38:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 169 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69133 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 169, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | HM |  | Grout hole leak is inactive at the time of inspection. | no | yes |  | no |  | 7db0e712-24aa-4dd5-9869-ad02cf68186e,ced6701c-5475-4d64-b201-b97bf1ecf2db | , | https://web.fulcrumapp.com/photos/view?photos=7db0e712-24aa-4dd5-9869-ad02cf68186e%2Cced6701c-5475-4d64-b201-b97bf1ecf2db | Concrete | Grout Hole | Leaks |  | Not reinforcement
699226d9-b0e9-4918-a4a9-931eb3c4829c | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-30 05:36:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 169 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 69132 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.6189 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 169, 2 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has previous repair. Repair has saw cuts that have not been repaired. |  | Concrete shell segment has previous repair. Repair has saw cuts that have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Condition unchanged. Repair has not been fixed properly. | no | yes |  | no |  | c9c8dc7d-7a6e-4907-8d70-12764e3d7d99,b4ed148a-1497-40b4-b5e0-9401792fde60 | , | https://web.fulcrumapp.com/photos/view?photos=c9c8dc7d-7a6e-4907-8d70-12764e3d7d99%2Cb4ed148a-1497-40b4-b5e0-9401792fde60 | Concrete
da6c09dc-7814-4644-aea6-f0a624552c0b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:30:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 169 | 4 | Grout Injection Hole | Grout Injection Hole |  | 69134 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 169, 4 o'clock. Concrete Shell Segment - Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | No close access. This is showing large salts buildup. Should be treated. | no | yes |  | no |  | 96a1226e-b339-4ae4-b1fb-d50f79da17bd,286b394e-adfe-4376-8961-0637aa4401e2,42230faa-69ae-49bc-84d7-cbfec0d17830 | ,, | https://web.fulcrumapp.com/photos/view?photos=96a1226e-b339-4ae4-b1fb-d50f79da17bd%2C286b394e-adfe-4376-8961-0637aa4401e2%2C42230faa-69ae-49bc-84d7-cbfec0d17830 | Concrete | Grout Hole | Leaks |  | Not reinforcement
f4aaf0eb-b143-415f-b8f0-477381dd1e15 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 19:11:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 169 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 41916 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 169, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | BP |  | No defect at 7 O’clock position | no |  |  | yes |  |  |  |  | Concrete | Radial Joint | Drummy
a57a38d6-3e6f-4cc5-8356-a765bbfdb4d3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 21:33:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 170 | 10 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85884 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 170, 10 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | BP |  | Steel bracket bolts corroded, white deposits behind bracket | yes | no |  | yes |  | 9e4abf42-ea23-414b-b5e3-f22b8a116da3,9842bc5b-4824-4838-a49b-a499663f1a86 | , | https://web.fulcrumapp.com/photos/view?photos=9e4abf42-ea23-414b-b5e3-f22b8a116da3%2C9842bc5b-4824-4838-a49b-a499663f1a86 | Concrete,Steel |  | Leaks
489cad8c-79bc-43a0-a8bb-f0465123a8ac | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-30 05:45:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 170 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26846 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 170, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel Channel Bracket has level 2 corrosion at 40% coverage. Channel anchor bolts have level 3 corrosion. |  | Steel Channel Bracket has level 2 corrosion at 40% coverage. Channel anchor bolts have level 3 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P3. Bolt replacement only, corrosion on channel is Level 2 only. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of minor services (NOT water pipe) | Priority: P3 |  |  |  | Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor | HM |  | Steel bracket and anchors have medium corrosion. Leak is still active behind the steel bracket. | no | yes |  | no |  | 09335eb5-f45a-4cd9-ab5e-499bf507eedf,cff9977b-de5c-460c-a6f5-7979cc63cc9c | , | https://web.fulcrumapp.com/photos/view?photos=09335eb5-f45a-4cd9-ab5e-499bf507eedf%2Ccff9977b-de5c-460c-a6f5-7979cc63cc9c | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks
eea2f38e-1b46-4723-9e4f-06d484c110d5 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:28:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 170 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85883 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 170, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over one area of 250mm x 250mm. |  | Circle joint has Grout Delamination / Drummy Grout over one area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | No close access. Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | b14ff9a1-9399-41b0-a28e-2f761c15bf91,3b0e9f21-634d-4efc-9005-ca7eef06b114 | , | https://web.fulcrumapp.com/photos/view?photos=b14ff9a1-9399-41b0-a28e-2f761c15bf91%2C3b0e9f21-634d-4efc-9005-ca7eef06b114 | Concrete | Circular Joint | Drummy
8aa8f6ac-ca8a-4631-a7b3-a23f0f763569 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:33:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 170 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41976 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 170, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. Condition rating 4. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. Condition rating 4. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete |  | Leaks
24427f18-17f9-4a42-8dc6-52d5ad88c70e | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:49:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 171 | 0 | Grout Injection Hole | Grout Injection Hole |  | 69135 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 171, 1 & 2 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | No change | no | yes |  | yes | Reduce condition state to 3 | 188a1943-0138-41e5-9d48-9ac06fcad0c7,c0efe520-1ba8-426e-803c-fb39524e81de,6f19513a-f1c8-42d0-bbfa-9d2d044f826c,56fd2193-7cd9-4ba3-bed5-b9932714316a | ,,, | https://web.fulcrumapp.com/photos/view?photos=188a1943-0138-41e5-9d48-9ac06fcad0c7%2Cc0efe520-1ba8-426e-803c-fb39524e81de%2C6f19513a-f1c8-42d0-bbfa-9d2d044f826c%2C56fd2193-7cd9-4ba3-bed5-b9932714316a | Concrete | Grout Hole | Leaks |  | Not reinforcement
ca634e3a-b151-4ae0-ae8a-96bc2204c01b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:54:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 172 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69136 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 172, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | No change. No salt deposits or moisture seen. | yes | yes |  | yes | Reduce condition state to 3 | f681c0c1-c176-4d60-9b88-793fb4f74707,320dc32d-dd2a-49db-9418-3ecb7f478f67,2ca8b5e1-3862-44ce-a753-168a9d1afed4 | ,, | https://web.fulcrumapp.com/photos/view?photos=f681c0c1-c176-4d60-9b88-793fb4f74707%2C320dc32d-dd2a-49db-9418-3ecb7f478f67%2C2ca8b5e1-3862-44ce-a753-168a9d1afed4 | Concrete | Grout Hole,Reinforcement | Leaks
33a85c96-52b5-4813-ae6e-a7bd1f160262 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:59:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 173 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26847 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 173, 1 & 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | SS |  | No change. Appears to be patched already. | no | yes |  | yes | Reduce condition state to 3 | 3df17178-3975-4101-adb9-cc0f55aee2d2,5fef17d9-87ed-45b8-8b06-1b0aa56ea4b0,f7a65051-dfaf-44b8-9b78-e93035c71df5,32114db7-1894-46f1-b332-8de9f1189dd8 | ,,, | https://web.fulcrumapp.com/photos/view?photos=3df17178-3975-4101-adb9-cc0f55aee2d2%2C5fef17d9-87ed-45b8-8b06-1b0aa56ea4b0%2Cf7a65051-dfaf-44b8-9b78-e93035c71df5%2C32114db7-1894-46f1-b332-8de9f1189dd8 | Concrete | Grout Hole | Leaks |  | Not reinforcement
c0e1f8ef-5d7d-4593-b963-4a67438bc76b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:02:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 173 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69300 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 173, 12 o'clock. Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area of 100mm x 350mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area of 100mm x 350mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Update condition and priority | 1c16af19-e8de-427d-b719-2e18e74592c5,a90d19aa-2f70-4c13-a69f-daecac57f197,f5c30318-bc78-4911-92b5-6b2799066bcc,80b346e7-13fd-45f1-ac0e-2752bf5a143b | ,,, | https://web.fulcrumapp.com/photos/view?photos=1c16af19-e8de-427d-b719-2e18e74592c5%2Ca90d19aa-2f70-4c13-a69f-daecac57f197%2Cf5c30318-bc78-4911-92b5-6b2799066bcc%2C80b346e7-13fd-45f1-ac0e-2752bf5a143b | Concrete | Circular Joint | Drummy
f0c22191-2d91-455f-8615-987529213fe8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 | -20.3216 | 118.5853 | POINT (118.5853287 -20.321598) | 2025-05-27 20:13:18 AEST | 2025-07-28 05:57:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 173 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41977 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 173, 8 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. Condition rating 5. |  | Grout injection hole has Leak Active at time of inspection. Condition rating 5. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | No salt deposits. Very minor moisture. Suggest downgrading | no | no |  | yes | Reduce condition rating to 3. Priority to P3 | e1a4d9ae-cbfc-4cb2-990d-57f8e3f3457a,16a77e9b-11a1-4429-8a49-39f92d469cd0 | , | https://web.fulcrumapp.com/photos/view?photos=e1a4d9ae-cbfc-4cb2-990d-57f8e3f3457a%2C16a77e9b-11a1-4429-8a49-39f92d469cd0 | Concrete | Grout Hole | Leaks
8927c9f5-4823-4295-8a0c-8771414689b8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:05:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 174 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69137 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 174, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Replace missing anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor | SS |  | No change. | no | yes |  |  |  | 6bca8f70-1642-4da1-94d3-3f878de52b64,c00f0636-d1bf-47ac-9e51-13d0ce897db4,e9160bca-e8c4-4002-9f7b-5c1b8fccf454 | ,, | https://web.fulcrumapp.com/photos/view?photos=6bca8f70-1642-4da1-94d3-3f878de52b64%2Cc00f0636-d1bf-47ac-9e51-13d0ce897db4%2Ce9160bca-e8c4-4002-9f7b-5c1b8fccf454 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
af41be2b-f4a9-4abd-ad6d-d8f78093ee04 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:12:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 174 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41978 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 174, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | SS |  | Large salts deposit and moisture. This should be treated. | no | yes |  | no |  | d91677f0-c9f2-4352-87c7-ddf317fff271,cdea7df3-064a-4e14-9665-6412460261c3 | , | https://web.fulcrumapp.com/photos/view?photos=d91677f0-c9f2-4352-87c7-ddf317fff271%2Ccdea7df3-064a-4e14-9665-6412460261c3 | Concrete | Grout Hole | Leaks
5a44871e-7e77-4166-87ad-fb0b7ca1923d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:12:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 174 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26849 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 174, 9 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak seems slightly active currently. This should be treated. | no | no |  | no |  | ad10839b-344c-44a1-9b21-2961ef7c4345,f5d9bf49-2bbd-43bc-9373-99fa2c9cd726 | , | https://web.fulcrumapp.com/photos/view?photos=ad10839b-344c-44a1-9b21-2961ef7c4345%2Cf5d9bf49-2bbd-43bc-9373-99fa2c9cd726 | Concrete | Grout Hole | Leaks |  | Not reinforcement
f52a8d49-51e7-4a19-9a90-bc3f1e2252bd | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:16:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 175 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69138 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/12/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 175, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Supervisor | SS |  | No change. No salt deposits or moisture seen. | no | yes |  | no |  | 29be8e5e-49bd-4878-8a2c-ea2536d2ce4a,46e3e8ad-aabc-4f06-905f-5dd779ccb546,4903ae76-d063-43f7-8665-c7638f042673 | ,, | https://web.fulcrumapp.com/photos/view?photos=29be8e5e-49bd-4878-8a2c-ea2536d2ce4a%2C46e3e8ad-aabc-4f06-905f-5dd779ccb546%2C4903ae76-d063-43f7-8665-c7638f042673 | Concrete | Grout Hole | Leaks |  | Not reinforcement
78c61d64-7372-45ce-93f8-c1ce4c00a996 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:20:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 177 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41925 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 177, 7 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 350mm x 150mm. |  | Concrete shell segment has drummy concrete over an area of 350mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Reduce priority and risk | d146af81-4eae-481d-8c84-8922de3f4d42,50e0b899-f296-417b-ba3f-2170052d5793 | , | https://web.fulcrumapp.com/photos/view?photos=d146af81-4eae-481d-8c84-8922de3f4d42%2C50e0b899-f296-417b-ba3f-2170052d5793 | Concrete | Circular Joint | Drummy |  | Circular Joint
44faeedd-988f-431e-84a5-834740232a2b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:30:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 178 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69139 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44550.6277 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 178, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 3 Low Corrosion. |  | Channel anchor bolts have Level 3 Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Steel anchor bracket and bolt is showing moderate corrosion at the time of inspection. | no | yes |  | no |  | 7ebf3e5b-3ddd-475d-8080-88bbe5bf37f3,83c81869-6bfc-42a0-8af0-56049e86d0bf,26e1be60-6e81-4ead-83ed-be1fe40bc85d,5fd99501-125a-4df0-8494-65104b34b3f6 | ,,, | https://web.fulcrumapp.com/photos/view?photos=7ebf3e5b-3ddd-475d-8080-88bbe5bf37f3%2C83c81869-6bfc-42a0-8af0-56049e86d0bf%2C26e1be60-6e81-4ead-83ed-be1fe40bc85d%2C5fd99501-125a-4df0-8494-65104b34b3f6 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
6a1704d0-cfaa-451b-bd15-1637ceae1191 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 9 |  |  |  | 2025-07-26 01:23:54 AEST | 2025-07-28 09:55:05 AEST | 30011704-user5@smec.com | james.stone@smec.com | 180 | 6 O’clock |  |  | Steel bolts and footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [9 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Flanges and bolts |  |  | Failure of support member |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | [19 empty] | SS |  | Foot plate and bolts are buried, however connector flanges and bolts are representative and are showing 10% section loss |  | no |  | yes | Fill blank fields | decb5df6-d2e0-4560-91ca-a438fb60d09c,febf67f9-7d91-49af-88a1-85e5da71e6e1 | , | https://web.fulcrumapp.com/photos/view?photos=decb5df6-d2e0-4560-91ca-a438fb60d09c%2Cfebf67f9-7d91-49af-88a1-85e5da71e6e1 | Steel | Centre Support | Corrosion-Heavy |  | Centre Suppot
5a5b1b2a-b545-4e71-af0a-9923f39ec536 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 9 |  |  |  | 2025-07-26 01:29:52 AEST | 2025-07-26 01:31:36 AEST | 30011704-user5@smec.com | james.stone@smec.com | 180 | 7 |  |  | Steel bolts and footing plate | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [9 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Curved plate and bolts |  |  | Failure of support member |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | [19 empty] | SS |  | Curved foot plate and bolts are showing roughly 5% section loss |  | no |  | yes | Fill blank fields | 18e56def-acea-489d-a835-f17ae2e55434,de45e1b8-21ad-4a41-a550-8cef8ed7bb08 | , | https://web.fulcrumapp.com/photos/view?photos=18e56def-acea-489d-a835-f17ae2e55434%2Cde45e1b8-21ad-4a41-a550-8cef8ed7bb08 | Steel | Walkway Support,Walkway Support-Bolt | Corrosion-Heavy
9af9d80f-7446-4648-bce1-4d200be41d0d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 18 |  |  |  | 2025-07-25 18:16:46 AEST | 2025-07-25 18:21:24 AEST | 30011704-user5@smec.com | james.stone@smec.com | 156 | 10 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [15 empty] | Concrete Damage due to Cast- In |  | 1 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 1 |  |  | Unlikely (Failure within 20 years) |  | Concrete segment with rough surface possibly previous leak |  | Failure of shell segment in compression or tension leading to single ring failure. |  |  |  | Other | [10 empty] | Regular inspection | [7 empty] | AA |  | Minor deffect |  | no |  | no |  | 60f8347a-83fb-4464-941d-2bd7deaf2795,924f8d13-2f65-4961-937f-859b3cd5c2b7 | , | https://web.fulcrumapp.com/photos/view?photos=60f8347a-83fb-4464-941d-2bd7deaf2795%2C924f8d13-2f65-4961-937f-859b3cd5c2b7 | Concrete | Grout Hole | Leaks |  | Grout Hole
6fc252c2-d129-44da-b6d4-6a67f25555e6 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 18 |  |  |  | 2025-07-25 18:25:04 AEST | 2025-07-25 18:28:46 AEST | 30011704-user5@smec.com | james.stone@smec.com | 160 | 10 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [15 empty] | Concrete Damage due to Cast- In |  | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Crack |  | Break up of grout and water leaks |  |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | [16 empty] | AA |  | Crack consequently leading to futue Leaks |  | no |  | no |  | eb348c84-346c-4b05-9585-17489195f91d,af775046-148a-4e95-89f1-61d9a07b50a1 | , | https://web.fulcrumapp.com/photos/view?photos=eb348c84-346c-4b05-9585-17489195f91d%2Caf775046-148a-4e95-89f1-61d9a07b50a1 | Concrete | Circular Joint | Crack,Leaks |  | Circular Joint
cbb4a87b-472c-47f1-bbdc-8699d34520f1 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 18 |  |  |  | 2025-07-25 18:32:01 AEST | 2025-07-25 18:45:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 161 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27107 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 161, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. Etching below previous leak. - Condition rating 4 |  | Grout injection hole has Leak Inactive at time of inspection. Etching below previous leak. - Condition rating 4 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA |  | As above | no | no |  | no |  | a71ffa0c-989b-4c00-8226-7ad59bd7b496,2c020c18-db49-4b79-aa96-c77da162e00d | , | https://web.fulcrumapp.com/photos/view?photos=a71ffa0c-989b-4c00-8226-7ad59bd7b496%2C2c020c18-db49-4b79-aa96-c77da162e00d | Concrete | Grout Hole | Leaks
8c5e4be6-b68c-4dea-a91e-b389bd198d6f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 18 |  |  |  | 2025-07-25 18:51:12 AEST | 2025-07-25 18:54:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 165 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [15 empty] | Concrete Damage due to Cast- In |  | 1 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 1 |  |  | Unlikely (Failure within 20 years) |  | Concrete segment with rough surface possibly previous leak |  | Failure of shell segment in compression or tension leading to single ring failure. |  |  |  | Other | [10 empty] | Regular inspection | [7 empty] | AA |  | Minor deffect |  | no |  | no |  | fae18fac-d352-4df7-9e9c-aae7e5522c89,f170f0af-5fd1-43b8-9665-32f945c0af88 | , | https://web.fulcrumapp.com/photos/view?photos=fae18fac-d352-4df7-9e9c-aae7e5522c89%2Cf170f0af-5fd1-43b8-9665-32f945c0af88 | Concrete | Grout Hole | Leaks |  | Grout Hole
3ad2a319-8f64-4798-b3e7-06278d5f7433 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 18 |  |  |  | 2025-07-25 18:59:06 AEST | 2025-07-31 01:33:29 AEST | 30011704-user5@smec.com | james.stone@smec.com | 167 | 9 | Grout Injection Hole | Grout Injection Hole |  | 68882 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 167, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | A.Acero and DR |  | Defect from 167-11 o clock starting to impact 10 o clock and 9 o’clock clock at the same ring location. Severe leak with salt deposits up to 9 O Clock. Grout injection hole heavily corroded. High priority | no | no | High priority defect. | no |  | 87acaa45-4f8e-4882-bbe6-9ce61dc7ca13,b16279e0-99ab-45fe-b1d3-265037fbdf81,607d8af8-14a6-47f6-8add-74e8c901ad80 | ,, | https://web.fulcrumapp.com/photos/view?photos=87acaa45-4f8e-4882-bbe6-9ce61dc7ca13%2Cb16279e0-99ab-45fe-b1d3-265037fbdf81%2C607d8af8-14a6-47f6-8add-74e8c901ad80 | Concrete | Grout Hole | Leaks |  | Not reinforcement
aa616cca-d466-4197-ab7c-49c7a60d73e2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 18 |  |  |  | 2025-07-25 19:16:10 AEST | 2025-07-26 23:09:26 AEST | 30011704-user5@smec.com | james.stone@smec.com | 171 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41976 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Severity Level 3 |  | Likely (Failure within 2 Years) | Possible (Failure within 5 Years) |  |  | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. Condition rating 4. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. Condition rating 4. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | AA |  |  | no | no |  | no |  | 3a35f9e4-66ac-4d7e-832f-99f267af8e6a,96843638-0d29-42d1-9843-fdfe98f8eb9d,3977261f-cda5-4193-a4f6-8b07b00a4841 | ,, | https://web.fulcrumapp.com/photos/view?photos=3a35f9e4-66ac-4d7e-832f-99f267af8e6a%2C96843638-0d29-42d1-9843-fdfe98f8eb9d%2C3977261f-cda5-4193-a4f6-8b07b00a4841 | Concrete | Grout Hole | Leaks |  | Grout Hole
f3a25cb3-b411-47d3-95bf-b3c1d990703f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 16 |  |  |  | 2025-07-26 04:13:25 AEST | 2025-07-28 09:51:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 174 | 1 & 3 |  | Steel Channel Bracket | [15 empty] | Corrosion - Structure Member/Platework |  | 2 | [6 empty] | Localised Corrosion EXT |  |  | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Ring 174, 1 & 3 o' clock, steel channel bracket is corroded | [5 empty] | Steel anchor channel corroded | [18 empty] | HM |  | Minor corrosion of steel anchor channel evident at 1 and 3 o' clock | [5 empty] | 5a254668-cb28-44ae-9ada-4160c751e681,33060705-d613-4ab3-910c-d130dd512b88,79e0bf4c-6632-4dfd-a5b2-d0d67bcc3b81 | ,, | https://web.fulcrumapp.com/photos/view?photos=5a254668-cb28-44ae-9ada-4160c751e681%2C33060705-d613-4ab3-910c-d130dd512b88%2C79e0bf4c-6632-4dfd-a5b2-d0d67bcc3b81 | Steel | Channel Bracket | Corrosion-Surface
b0a974c3-0c88-4ed5-800f-f307b3df2a88 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 16 |  |  |  | 2025-07-26 04:30:46 AEST | 2025-07-28 09:50:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 178 | 1 |  | Steel Channel Bracket | [15 empty] | Corrosion - Structure Member/Platework |  | 3 | [6 empty] | Localised Corrosion EXT |  |  | Severity Level 3 |  |  | Unlikely (Failure within 20 years) |  | Ring 178, 1 o' clock Steel anchor bracket corrosion |  |  |  |  | Class 3 - Medium corrosion | [19 empty] | HM |  | Steel anchor bracket is corroded. It is possible there is a small leak behind bracket. | [5 empty] | 36288dca-680d-4722-9613-123cd7a9efb8,8d0d82e4-dbde-427b-9ee5-93da8ec06eb9,bc534b78-b1e1-4a8b-a779-166f671b634c | ,, | https://web.fulcrumapp.com/photos/view?photos=36288dca-680d-4722-9613-123cd7a9efb8%2C8d0d82e4-dbde-427b-9ee5-93da8ec06eb9%2Cbc534b78-b1e1-4a8b-a779-166f671b634c | Steel | Channel Bracket | Leaks
b0ed1bcd-6a29-4105-a8eb-3835574708d3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 11 |  |  |  | 2025-07-27 17:25:56 AEST | 2025-07-27 17:31:21 AEST | 30011704-user5@smec.com | james.stone@smec.com | 152 | 6, support beam for conveyor & walkway | [59 empty] | BP AA |  | 6 O’clock, Corroded Base support beam conveyor & walkway. Medium risk |  | yes |  | yes |  | 48589e84-17bc-445a-8ed1-5763e7c83125,89054f45-b3dc-4646-b833-ffcd8c6dce03,7f44bcf4-b273-4f9e-90a5-ba67b546c846,313a19aa-397a-4490-a0b0-917f637cd3d1 | ,,, | https://web.fulcrumapp.com/photos/view?photos=48589e84-17bc-445a-8ed1-5763e7c83125%2C89054f45-b3dc-4646-b833-ffcd8c6dce03%2C7f44bcf4-b273-4f9e-90a5-ba67b546c846%2C313a19aa-397a-4490-a0b0-917f637cd3d1 | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Reinforcement
15c91b3d-cc04-4f83-a711-fc7326ffa96a | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 11 |  |  |  | 2025-07-27 17:37:22 AEST | 2025-07-27 17:43:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 156 | 6, support beam conveyor & 5, Curved bracket walkway | [17 empty] | Corrosion - Connection | [16 empty] | Black rust, Section loss support beam conveyor & walkway curved bracket | [24 empty] | BP AA |  | 6 o’clock support beam conveyor & walkway and 5 o’clock curved bracket corrosion . Medium Risk |  | yes |  | yes |  | 27582b24-a06c-4df6-aaec-33bf94ccbe6b,b9163fca-9d43-4c6c-adb5-910a02de5e55,02e2fe34-791f-40de-9abb-dd1f5f5b1347,a462c2f2-5b4c-4e0f-9307-90f81f8e4b9d,536d71aa-01e4-4d7e-8087-b21798c5fe98 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=27582b24-a06c-4df6-aaec-33bf94ccbe6b%2Cb9163fca-9d43-4c6c-adb5-910a02de5e55%2C02e2fe34-791f-40de-9abb-dd1f5f5b1347%2Ca462c2f2-5b4c-4e0f-9307-90f81f8e4b9d%2C536d71aa-01e4-4d7e-8087-b21798c5fe98 | Steel | Centre Support,Walkway Support | Corrosion-Heavy |  | Centre support and walkway support
8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 11 |  |  |  | 2025-07-27 17:48:49 AEST | 2025-07-27 17:58:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 160 | 7, 6 o’clock support beam conveyor & walkway curved bracket 5 o’clock | [17 empty] | Corrosion - Structure Member/Platework | [16 empty] | Loss of nut bolt fixing base plate , support beam | [24 empty] | BP AA |  | Active corrosion, black rust. Base plate and fixings. Medium risk |  | yes |  | yes |  | 9fd81ded-41f6-4d60-88af-06407e08fbc7,242d19ec-108b-4df4-8d67-b67d93a06b5e,0a12d4b1-13e5-4c5b-858f-a1eb910e8897,482317cd-9ef3-4c76-947c-a5ada5db4879,47255840-e77d-4cca-bf3c-d21e6877862d,7c5ac1e1-e10a-423b-950c-389f6e3022d7,4140eecb-e554-44be-be64-e77e4572c51e,197fd34b-94b2-474f-92e4-0e97901c2130 | ,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=9fd81ded-41f6-4d60-88af-06407e08fbc7%2C242d19ec-108b-4df4-8d67-b67d93a06b5e%2C0a12d4b1-13e5-4c5b-858f-a1eb910e8897%2C482317cd-9ef3-4c76-947c-a5ada5db4879%2C47255840-e77d-4cca-bf3c-d21e6877862d%2C7c5ac1e1-e10a-423b-950c-389f6e3022d7%2C4140eecb-e554-44be-be64-e77e4572c51e%2C197fd34b-94b2-474f-92e4-0e97901c2130 | Steel |  | Corrosion-Surface
2eb72ddf-1e7a-41a8-87c4-2b4ce4c17023 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 11 |  |  |  | 2025-07-27 18:08:42 AEST | 2025-07-27 18:15:33 AEST | 30011704-user5@smec.com | james.stone@smec.com | 164 | 7, 6 o’clock support beam conveyor & walkway | [59 empty] | AA BP |  | 7 and 6 o’clock support beam conveyor & walkway. Base plate, beam support corroded. Medium risk |  | yes |  | yes |  | b2078654-eff4-4c23-b4a0-8bee5b58a6fd,5cbc1470-cf81-4172-ae8e-aea56089ec7b,9aef9aa4-dac6-42ff-8599-c88b596c7e6d,b101022a-228f-476d-b3e1-09c000445053,e5b44645-43dd-44f6-a2a0-4caf78009f1d,f524da60-b1b9-4ba3-8503-16f608e99eaf,468c9287-5f19-4f4f-a753-19ddd5886261 | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=b2078654-eff4-4c23-b4a0-8bee5b58a6fd%2C5cbc1470-cf81-4172-ae8e-aea56089ec7b%2C9aef9aa4-dac6-42ff-8599-c88b596c7e6d%2Cb101022a-228f-476d-b3e1-09c000445053%2Ce5b44645-43dd-44f6-a2a0-4caf78009f1d%2Cf524da60-b1b9-4ba3-8503-16f608e99eaf%2C468c9287-5f19-4f4f-a753-19ddd5886261 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walway Suppot
b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 11 | -20.3218 | 118.5854 | POINT (118.5853721525106 -20.32183640643895) | 2025-07-27 18:24:58 AEST | 2025-07-27 19:34:02 AEST | 30011704-user5@smec.com | james.stone@smec.com | 168 | 7,6,5 o’clock support beam conveyor & circular walkway | [59 empty] | AS BP |  | Corroded 7,6,5 o’clock support beam conveyor & circular walkway | [5 empty] | 653ccb87-b1e6-4f31-bd18-02d14b22ee3c,8eb42811-e70d-4a7e-bac8-ed03656a87b9,a30c3873-731d-4e67-8a5b-b90cfc5edaae,e8beef56-28bc-44e6-8838-d11688e54afe,60ef6a0d-c41f-4561-a0d7-99124e996421,5cfb6008-84d5-42aa-ab7f-32a7773563ca,bb8ad476-2d21-415a-8910-26533b49f01f,ac61be30-0f9f-4b87-8de9-4a6563f69620,6c2d0af1-98ea-439b-a0d6-555758a0477e | ,,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=653ccb87-b1e6-4f31-bd18-02d14b22ee3c%2C8eb42811-e70d-4a7e-bac8-ed03656a87b9%2Ca30c3873-731d-4e67-8a5b-b90cfc5edaae%2Ce8beef56-28bc-44e6-8838-d11688e54afe%2C60ef6a0d-c41f-4561-a0d7-99124e996421%2C5cfb6008-84d5-42aa-ab7f-32a7773563ca%2Cbb8ad476-2d21-415a-8910-26533b49f01f%2Cac61be30-0f9f-4b87-8de9-4a6563f69620%2C6c2d0af1-98ea-439b-a0d6-555758a0477e | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor support
d071eaac-c3b4-4760-b9fe-d30a62169fd7 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 3 |  |  |  | 2025-07-31 01:39:46 AEST | 2025-07-31 01:40:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 163 | 11 O Clock |  | Grout Injection Hole | [57 empty] | Dr |  | Grout injection of previous leak location has drummy concrete. must be checked and repaired. High priority. |  | yes |  |  |  | eceb3dac-54d5-445e-9a84-4f3e0c495349,82ebea5e-3e29-46d2-9ccb-85c66057c571 | , | https://web.fulcrumapp.com/photos/view?photos=eceb3dac-54d5-445e-9a84-4f3e0c495349%2C82ebea5e-3e29-46d2-9ccb-85c66057c571 | Concrete | Grout Hole | Drummy,Leaks
a338411d-8ae9-455f-bdae-92df22461a07 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 14:44:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 182 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85885 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 182, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | c97e762f-685d-45e0-bcaa-70dab5511709,9c856b51-2ee4-459a-b732-1372b4361ab9,cb5fee15-5645-4fa6-994f-68c60a747aae | ,, | https://web.fulcrumapp.com/photos/view?photos=c97e762f-685d-45e0-bcaa-70dab5511709%2C9c856b51-2ee4-459a-b732-1372b4361ab9%2Ccb5fee15-5645-4fa6-994f-68c60a747aae | Concrete | Circular Joint | Drummy
d214fb78-1147-4156-880b-c11a6cfa6215 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:37:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 183 | 7 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 69142 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.6366 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 183, 7 o'clock. Concrete Shell Segment. |  |  |  | Grout Delamination / debonding at radial segment bolted joints |  | Grout Delamination / debonding at radial segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. Additionally, no delamination is detected at this location. | yes | yes |  | yes | Consider removing this defect from the list | 8497055c-d2da-42cb-87cd-be19caca0efb,59e94bd5-ab11-4998-b3bd-4c6b242bfe86 | , | https://web.fulcrumapp.com/photos/view?photos=8497055c-d2da-42cb-87cd-be19caca0efb%2C59e94bd5-ab11-4998-b3bd-4c6b242bfe86 | Concrete | Radial Joint | Drummy
27d6a4c5-36e7-4308-a89f-d330fc865ca5 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:59:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 184 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 99559 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 45415.3661 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 184, 3 o'clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 corrosion. |  | Steel channel support bracket has Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Minor corrosion in the steel bracket | no | no |  | no |  | 1b577c59-9e2d-4a79-877d-7597dcda63ac,773bfe7f-96f8-44cf-9401-120d60bea85e | , | https://web.fulcrumapp.com/photos/view?photos=1b577c59-9e2d-4a79-877d-7597dcda63ac%2C773bfe7f-96f8-44cf-9401-120d60bea85e | Steel | Channel Bracket | Corrosion-Surface
270472c6-7e0a-4275-848f-0d773e3535eb | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:40:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 187 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68883 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 187, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | No change. This seems to not be a defect | no | yes |  | yes | Suggest reduce severity and risk estimates | c5d957e4-560e-4b82-b943-bfb8dc7f5a34,c6ea20b7-8fa8-4013-9f47-80201dc96398 | , | https://web.fulcrumapp.com/photos/view?photos=c5d957e4-560e-4b82-b943-bfb8dc7f5a34%2Cc6ea20b7-8fa8-4013-9f47-80201dc96398 | Concrete | Grout Hole | Leaks |  | Not reinforcement
7cb9cfa1-954a-411b-9e3c-fca334c82d0f | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:44:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 188 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68884 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 188, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | Has been patched. | no | no |  | yes | Reduce condition and risk. Action to be monitor. | 16d0fb60-2015-4840-ac13-0577403f5613,fa5594a0-665d-4590-80fc-1be1e789e72e | , | https://web.fulcrumapp.com/photos/view?photos=16d0fb60-2015-4840-ac13-0577403f5613%2Cfa5594a0-665d-4590-80fc-1be1e789e72e | Concrete | Grout Hole | Leaks |  | Not reinforcement
1f80372c-75cd-493c-a4e9-b7cca5546697 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 | -20.3216 | 118.5853 | POINT (118.5853232 -20.3216084) | 2025-05-27 20:13:18 AEST | 2025-07-28 06:01:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 188 | 8 | Grout Injection Hole | Grout Injection Hole |  | 99560 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 188, 8 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection - Condition Rating 5 |  | Grout injection hole has Leak Active at time of inspection - Condition Rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | This appears to be patched | yes | no |  | yes | Update priority, condition and risk to suit | afcd54e6-9a78-4eea-a11d-8bdd919d58f6,536721a4-e5c5-4f32-a3e8-4b6e55e94c39 | , | https://web.fulcrumapp.com/photos/view?photos=afcd54e6-9a78-4eea-a11d-8bdd919d58f6%2C536721a4-e5c5-4f32-a3e8-4b6e55e94c39 | Concrete | Grout Hole | Leaks
91587f9e-7775-4a8c-9939-cd786d5c449f | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:46:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 189 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26853 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 189, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | Has been patched. Appears successful | no | no |  | yes | Reduce condition and risk. Action to be monitor. |  |  |  | Concrete | Grout Hole | Leaks |  | Not reinforcement
c948a567-bde1-46db-8c19-0ce6bd5993e9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:11:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 190 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85886 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 10/11/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 190, 4 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 1200mm x 1200mm. Potential extend further under mud build up. |  | Concrete shell segment has drummy concrete over an area of 1200mm x 1200mm. Potential extend further under mud build up. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P2 |  |  |  | Break out loose and damaged concrete. Engineer to assess damage to reinforcement and remediation required. All areas of damaged concrete shall be replaced with high strength concrete patch repairs including embedment of galvanic Cathodic Protection (CP) anodes. Corroded reinforcement that has not been removed shall be thoroughly cleaned of all corroded material. Where corroded reinforcement has been removed it should be replaced by welding a new length of N grade reinforcement of the same diameter to the remaining undamaged reinforcing bar. Or replacing the damaged bar with a new N grade bar of the same diameter as the removed bar. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | HM |  | Delamination couldn't be found at this location. | yes | no |  | no |  |  |  |  | Concrete |  | Drummy
81a93a60-d465-46ab-a3b9-c5f99e32dad3 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:14:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 191 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69143 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 191, 2 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | Leak is inactive at the time of the inspection. It is possible leak was closed | yes | no |  | no |  | beb95b15-3ec1-4d96-bd89-15aa27fafe92,4f11066d-2757-4186-9103-01da55289861 | , | https://web.fulcrumapp.com/photos/view?photos=beb95b15-3ec1-4d96-bd89-15aa27fafe92%2C4f11066d-2757-4186-9103-01da55289861 | Concrete | Grout Hole | Leaks |  | Not reinforcement
017f40ad-59c8-4a10-a358-6c86d87960b9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:21:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 191 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99561 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 191, 4 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 200 mm x 100 mm |  | Grout Delamination / Drummy Grout at circle joint over an area of 200 mm x 100 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Suggest reduce priority to P3 | e6d9322a-c28c-4289-b022-0bd362bb9ded,58025fff-b9ca-4f95-9fa6-14f9fb9fd53f,43380d83-68ac-45ce-a08a-71350fd71beb | ,, | https://web.fulcrumapp.com/photos/view?photos=e6d9322a-c28c-4289-b022-0bd362bb9ded%2C58025fff-b9ca-4f95-9fa6-14f9fb9fd53f%2C43380d83-68ac-45ce-a08a-71350fd71beb | Concrete | Circular Joint | Drummy
c512451e-e937-47f3-8d22-6261806679f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:05:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 191 | 12 | Grout Injection Hole | Grout Injection Hole |  | 68885 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 15/12/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 191, Various o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Update description | d2bd7954-2d90-4b26-87a6-aad6acbf06ab,a49af9e4-1a0d-42aa-93b3-0c8d011bd949,ac85b826-77e8-442c-b808-da200144c2c3,e3a4c912-9057-4b72-b931-dd127eaa5ffc | ,,, | https://web.fulcrumapp.com/photos/view?photos=d2bd7954-2d90-4b26-87a6-aad6acbf06ab%2Ca49af9e4-1a0d-42aa-93b3-0c8d011bd949%2Cac85b826-77e8-442c-b808-da200144c2c3%2Ce3a4c912-9057-4b72-b931-dd127eaa5ffc | Concrete | Grout Hole | Leaks |  | Not reinforcement
02f780c9-d25b-4d9d-a11e-0cc2b16db819 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:05:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 192 | 9 | Grout Injection Hole | Grout Injection Hole |  | 99562 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 45415.3757 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 192, 9 o'clock, Grout Injection Hole |  |  |  | Concrete shell segment has local spalling at grout injection hole at the approximate depth of 20mm. |  | Concrete shell segment has local spalling at grout injection hole at the approximate depth of 20mm. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 7123f25f-c6ea-470a-9e19-6275d4e2c72c,c0c85201-b328-47ce-b77c-72205eb22568,b6a91509-36c1-4840-bd88-e72fc7ba74eb,faeb5ce7-e710-41c4-b1c2-b8b2f9a60dc1 | ,,, | https://web.fulcrumapp.com/photos/view?photos=7123f25f-c6ea-470a-9e19-6275d4e2c72c%2Cc0c85201-b328-47ce-b77c-72205eb22568%2Cb6a91509-36c1-4840-bd88-e72fc7ba74eb%2Cfaeb5ce7-e710-41c4-b1c2-b8b2f9a60dc1 | Concrete | Grout Hole | Surface Damage
d9a82046-dcd7-4e70-a70e-996d1b093e3c | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:15:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 196 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69145 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 196, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Update description | 7d8ed08f-fde6-4d6f-818f-ccb97f2db5de,a9692007-05e3-4f26-8978-31cad190fe8c,92fa0871-8f87-455b-8a5d-9706311187d7,36a42707-f68f-4b6d-9e32-27d5674d354d | ,,, | https://web.fulcrumapp.com/photos/view?photos=7d8ed08f-fde6-4d6f-818f-ccb97f2db5de%2Ca9692007-05e3-4f26-8978-31cad190fe8c%2C92fa0871-8f87-455b-8a5d-9706311187d7%2C36a42707-f68f-4b6d-9e32-27d5674d354d | Concrete | Grout Hole | Leaks |  | Not reinforcement
cc778594-9985-441e-810e-283d8d080f26 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:17:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 196 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68886 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 196, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | No leak currently evident Leak may have already been treated | no | yes |  | yes | Update description | 0cfd2133-f9f7-4b17-bef7-260d06932062,d0521566-6155-472f-9506-807c5b6f7c5f | , | https://web.fulcrumapp.com/photos/view?photos=0cfd2133-f9f7-4b17-bef7-260d06932062%2Cd0521566-6155-472f-9506-807c5b6f7c5f | Concrete | Grout Hole | Leaks |  | Not reinforcement
0e199566-4862-4afc-a285-8a34c659352b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:19:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 198 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99563 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 198, 11 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over an area of 200 mm x 200 mm |  | Grout Delamination / Drummy Grout at radial joint over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | cdcbde5b-85cc-4791-a47e-5e5075955e34,101173bb-fe61-4ace-819f-3c95abd5eabc | , | https://web.fulcrumapp.com/photos/view?photos=cdcbde5b-85cc-4791-a47e-5e5075955e34%2C101173bb-fe61-4ace-819f-3c95abd5eabc | Concrete | Circular Joint,Radial Joint | Drummy
34ee6bef-3510-4e27-bc83-3fc80bc6a2d6 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:22:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 198 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 69148 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44550.6415 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 198, 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 50% coverage. |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This is extremely minor corrosion | no | yes |  | yes | Update description | b7a4d2de-f1cb-47fa-8702-6e8ca841b6e7,15852746-fd6d-42cd-a210-050b22a5734d | , | https://web.fulcrumapp.com/photos/view?photos=b7a4d2de-f1cb-47fa-8702-6e8ca841b6e7%2C15852746-fd6d-42cd-a210-050b22a5734d | Steel | Channel Bracket | Corrosion-Surface
2410be29-0702-4415-9daf-910f04ce85ff | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:28:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 198 | 12 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69146 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Loose Bolt |  | Loose Bolt | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 198, 12 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts is loose. |  | Channel anchor bolts is loose. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Replace loose anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Steelwork Remediation Crew. | No | Off-Line | Yes | - | - | Maintenance Repair Competent Supervisor | SS |  | No change to the loose bolt. Additionally, one of the hangers connecting bolt has fallen out. | no | yes |  | yes | Update description | d6d4d991-8359-49be-b5f7-52567f38c954,52c48b67-1c32-40e6-b814-63d4170db06b,be9ed26a-b125-47fd-a1a2-abf36bbea5d7,6d8a9eb2-bfa6-4714-8dc6-5b43ab0140b8 | ,,, | https://web.fulcrumapp.com/photos/view?photos=d6d4d991-8359-49be-b5f7-52567f38c954%2C52c48b67-1c32-40e6-b814-63d4170db06b%2Cbe9ed26a-b125-47fd-a1a2-abf36bbea5d7%2C6d8a9eb2-bfa6-4714-8dc6-5b43ab0140b8 | Steel | Channel Bracket,Channel Bracket-Bolt | Loose,Missing
a829edc5-3dcc-42be-8bba-b4105265a37c | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:29:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 198 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 99565 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 198, 3 o'clock, Steel Channel Bracket | Rupture | Rupture |  | Steel channel support bracket has Level 3 corrosion. |  | Steel channel support bracket has Level 3 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P3. | Safety | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. 3. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Remediation crew. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | HM |  | Steel channel bracket has minor corrosion. Priority 4. | no | no |  | no |  | 65e691be-5d55-4f10-b392-b0e4dc25e5c9,97240d9e-338f-4ff0-9771-50d1e7bd751e | , | https://web.fulcrumapp.com/photos/view?photos=65e691be-5d55-4f10-b392-b0e4dc25e5c9%2C97240d9e-338f-4ff0-9771-50d1e7bd751e | Steel | Channel Bracket | Corrosion-Surface
71edfa7e-2c02-491d-83ec-30c3f3213b15 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:31:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 198 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27100 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 198, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts have Level 4 Medium High Corrosion. |  | Channel anchor bolts have Level 4 Medium High Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services | Priority: P3 |  |  |  | Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | HM |  | Channel anchor bolt has minor corrosion. Priority 4. | no | no |  | no |  | ad77c5a3-d77d-4b83-980f-ec93bdf8fbf8 |  | https://web.fulcrumapp.com/photos/view?photos=ad77c5a3-d77d-4b83-980f-ec93bdf8fbf8 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
6e8b5bec-98fc-4f46-a29c-c1719e333220 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:32:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 199 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 69150 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44550.6428 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 199, 11 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. |  | Concrete shell segment has drilled holes for chloride sampling which have not been repaired. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | These have been patched | yes | no |  | yes | Close this issue as it has been treated | b6887a25-2a28-4c0c-ac8c-49317c1f8240,2bd87b22-fc41-42be-a208-3cab029364ec | , | https://web.fulcrumapp.com/photos/view?photos=b6887a25-2a28-4c0c-ac8c-49317c1f8240%2C2bd87b22-fc41-42be-a208-3cab029364ec | Concrete |  | Test Hole
3c2232eb-6d5b-4824-857b-57513c1f2c01 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:35:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 199 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26855 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 199, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 3 Medium Corrosion |  | Channel anchor bolts have Level 3 Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | HM |  | No channel anchor bolts detected at this position. Remove priority. | yes | no |  |  |  | 0d19978e-e46c-47c6-bc51-f71512bf3813 |  | https://web.fulcrumapp.com/photos/view?photos=0d19978e-e46c-47c6-bc51-f71512bf3813 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
2bc0340a-817a-4db4-98f0-8e0d7536e249 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:35:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 200 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69152 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 200, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No water evident, but salt deposits are visible. May have self healed. Should still be treated. | no | yes |  | yes | Update description | 447a1181-e665-4672-8cef-b49f6f1470e1,16e223d6-1f32-4be5-8fa0-88e60537830b,507c6e2e-76a2-4880-8700-e16aa7d9e378 | ,, | https://web.fulcrumapp.com/photos/view?photos=447a1181-e665-4672-8cef-b49f6f1470e1%2C16e223d6-1f32-4be5-8fa0-88e60537830b%2C507c6e2e-76a2-4880-8700-e16aa7d9e378 | Concrete | Grout Hole | Leaks |  | Not reinforcement
a9f1fb92-4ed9-4d18-ae32-8bffa4d69f27 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:38:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 200 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68887 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 200, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | This has been patched, with no further leaking evident | yes | yes |  | yes | Update condition and risk | 4611e8e7-9cc2-4349-9705-bdb13fd7b2ac,c1e075c0-37d1-4b34-9d00-f529551fde0d | , | https://web.fulcrumapp.com/photos/view?photos=4611e8e7-9cc2-4349-9705-bdb13fd7b2ac%2Cc1e075c0-37d1-4b34-9d00-f529551fde0d | Concrete | Grout Hole | Leaks |  | Not reinforcement
54501af9-0bda-4705-9d39-0ca6a8da45fb | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:41:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 201 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99566 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 201, 7 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout over an area of 200 mm x 300 mm |  | Grout Delamination / Drummy Grout over an area of 200 mm x 300 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | f58108d5-946f-42b2-a57c-7ee2b951297d,1722d5d3-396e-4f9d-8df3-a49c238a3132 | , | https://web.fulcrumapp.com/photos/view?photos=f58108d5-946f-42b2-a57c-7ee2b951297d%2C1722d5d3-396e-4f9d-8df3-a49c238a3132 | Concrete | Radial Joint | Drummy
637d1053-41f7-4019-8d2c-e2098b9408c2 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:42:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 202 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26858 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 202, 1 & 2 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts have level 4 corrosion up to 20% coverage. |  | Channel anchor bolts have level 4 corrosion up to 20% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), revised recommended action to replace corroded anchor bolts. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services | Priority: P3 |  |  |  | Replace corroded anchor bolts.Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Scaffolding | - | Replace Component Competent Supervisor | HM |  | Steel anchor bracket and bolts has moderate corrosion at 1, 2 and 3 o' clock. It is possible there is a minor leak behind the steel bracket. | no | yes |  | no |  | 33b49317-ff2e-4eea-a409-4d794d427fe4,df40629d-4eef-4d7e-8f83-5093b232fa4c,dd3631d5-2d8a-4029-8671-3c4b25e91cae,0650f97b-4b20-4a51-9982-42df4f971b54,065e7610-d0cb-4879-82b6-f7ad1ac194ab | ,,,, | https://web.fulcrumapp.com/photos/view?photos=33b49317-ff2e-4eea-a409-4d794d427fe4%2Cdf40629d-4eef-4d7e-8f83-5093b232fa4c%2Cdd3631d5-2d8a-4029-8671-3c4b25e91cae%2C0650f97b-4b20-4a51-9982-42df4f971b54%2C065e7610-d0cb-4879-82b6-f7ad1ac194ab | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks
5dfff68a-4a4b-4efa-9e74-488bb68cac10 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:44:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 202 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27101 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 202, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | HM |  | Leak is still active at the time of the inspection. This is impacting the steel anchor brackets/bolts underneath the leak. | no | yes |  | no |  | ba7ccb1d-c6a8-4c87-b73b-131dfcabc1a2,170ca34b-5245-4250-9699-f54ed7b169ee | , | https://web.fulcrumapp.com/photos/view?photos=ba7ccb1d-c6a8-4c87-b73b-131dfcabc1a2%2C170ca34b-5245-4250-9699-f54ed7b169ee | Concrete,Steel | Channel Bracket | Leaks |  | Channel Bracket
7e07a1cb-c3bf-41e7-9ff9-bb3992422a15 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:46:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 202 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26859 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 202, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 corrosion. |  | Steel channel support bracket has Level 3 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Steel bracket moderate corrosion is evident. Priority 3. | no | no |  | no |  | deea7e52-ac80-4ff2-9523-2906d5ba6250,57ed5fc2-3c1f-4c41-9bd0-6b96b57f2fe0,849dc715-c163-4db3-b901-5b7816cdb713,540743f7-4fcd-4ff4-a9a5-b982af7ea4bd | ,,, | https://web.fulcrumapp.com/photos/view?photos=deea7e52-ac80-4ff2-9523-2906d5ba6250%2C57ed5fc2-3c1f-4c41-9bd0-6b96b57f2fe0%2C849dc715-c163-4db3-b901-5b7816cdb713%2C540743f7-4fcd-4ff4-a9a5-b982af7ea4bd | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
a5170fe8-62c6-4894-9b44-044af6967863 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:42:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 202 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 41981 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 202, 9 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. Condition rating 5 |  | Grout injection hole has Leak Active at time of inspection. Condition rating 5 | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Salt deposits are visible, moisture is visible. This leak should be treated. | no | yes |  | yes |  | c12527bc-7d6c-4bd6-901c-89d415df2a89,e8332fc1-8a44-4347-bdb1-e36e0c72ef67,f06c80e3-5682-495f-a885-501cd811ac7d | ,, | https://web.fulcrumapp.com/photos/view?photos=c12527bc-7d6c-4bd6-901c-89d415df2a89%2Ce8332fc1-8a44-4347-bdb1-e36e0c72ef67%2Cf06c80e3-5682-495f-a885-501cd811ac7d | Concrete | Grout Hole | Leaks
d534a6c5-4f87-4707-86bc-dd77618644d4 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:48:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 203 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68888 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 15/12/2021 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 203, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | SS |  | No leak currently evident. | no | yes |  | no |  | 4aae738d-1c8d-4122-93e3-550d463f3cbb,4092a1a8-fb11-4986-9b7f-8e34f35ef8c0 | , | https://web.fulcrumapp.com/photos/view?photos=4aae738d-1c8d-4122-93e3-550d463f3cbb%2C4092a1a8-fb11-4986-9b7f-8e34f35ef8c0 | Concrete | Grout Hole | Leaks |  | Not reinforcement
39146f9b-283b-48ba-9de0-0b6a9435c55b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:48:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 203 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69153 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 203, 2 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | HM |  | Leak is inactive at the time of inspection. It is possible the leak has been fixed. Priority 4. | yes | no |  | no |  | bde00f29-2e4c-44c3-8450-ec7d05dad9c1 |  | https://web.fulcrumapp.com/photos/view?photos=bde00f29-2e4c-44c3-8450-ec7d05dad9c1 | Concrete | Grout Hole | Leaks |  | Not reinforcement
676f1d11-79a8-4b0b-97b5-24c841a5535f | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:49:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 204 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 99569 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 45415.3938 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 204, 3 o'clock, Steel Channel Bracket |  |  |  | Steel Channel Bracket has Level 2 - Corrosion. |  | Steel Channel Bracket has Level 2 - Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | There is no steel anchor bracket at this location. No priority. | yes | no |  | no |  | 19f46361-2f3e-4f06-bf9a-c9dde6678179,7f3f891f-f18b-44ce-bc84-6c56912e9e3e | , | https://web.fulcrumapp.com/photos/view?photos=19f46361-2f3e-4f06-bf9a-c9dde6678179%2C7f3f891f-f18b-44ce-bc84-6c56912e9e3e | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
c496cdd2-e787-4706-bd67-6a9cd7e49954 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:45:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 204 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99567 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 204, 7 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at circle joint over an area of 200 mm x 300 mm |  | Grout Delamination / Drummy Grout at circle joint over an area of 200 mm x 300 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 869bb8f7-e3da-451f-98eb-d07ac38bb49d,e10b51ed-426a-4616-95be-3a0103f33b83 | , | https://web.fulcrumapp.com/photos/view?photos=869bb8f7-e3da-451f-98eb-d07ac38bb49d%2Ce10b51ed-426a-4616-95be-3a0103f33b83 | Concrete | Circular Joint | Drummy
8e813717-e903-4ed6-92c6-b85bbe8cc8e3 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:48:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 204 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99570 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 204, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over area of same size 300mm x 300mm. |  | Grout Delamination / Drummy Grout at radial joint over area of same size 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 3cd2bf35-51ee-4a8d-af3c-9e2020c9eb9b,f0ec4ea3-a3af-4c7f-9d92-06d4ace9b11b | , | https://web.fulcrumapp.com/photos/view?photos=3cd2bf35-51ee-4a8d-af3c-9e2020c9eb9b%2Cf0ec4ea3-a3af-4c7f-9d92-06d4ace9b11b | Concrete | Radial Joint | Drummy
0a73665d-593e-4226-afc9-3b3eee38aed6 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:52:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 204 | 9 | Grout Injection Hole | Grout Injection Hole |  | 85887 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 10/11/2022 |  | 17/05/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 204, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Engineering Repair Methodology Required Competent Engineer | SS |  | Leak does not seem active at time of inspection | no | no |  | yes | Suggest update description and reduce priority to P3 | 5030fb7b-daf7-41c5-982d-577ac7055b01,64cfe7e4-5379-4279-bcd5-d50c32d21ff5 | , | https://web.fulcrumapp.com/photos/view?photos=5030fb7b-daf7-41c5-982d-577ac7055b01%2C64cfe7e4-5379-4279-bcd5-d50c32d21ff5 | Concrete | Grout Hole | Leaks
c80d8369-70ac-49f8-9c60-2772c49f3ecd | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:53:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 205 | 0 | Hydrophilic Joint Seal (Radial Joint) | Hydrophilic Joint Seal (Radial Joint) |  | 69158 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 205, 1, 2 & 3 o'clock. Hydrophilic Joint Seal (Radial Joint). - Condition Rating 4 | Failure to seal joint | Failure to seal joint |  | Hydrophilic joint seal has Leak - Inactive at time of inspection. |  | Hydrophilic joint seal has Leak - Inactive at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | HM |  | Radial joint has been regrouted. No leak is evident at the time of inspection. No priority. | yes | no |  | no |  | 303feee8-3384-4161-8ce9-3a6b701ff700,4a1345fa-7714-4654-b442-71132e1deac6,112bdf38-b1ad-46e2-bfe8-3964f9c55cd5,fe3ba384-173b-47fd-9f1f-fb3d4ae671b7 | ,,, | https://web.fulcrumapp.com/photos/view?photos=303feee8-3384-4161-8ce9-3a6b701ff700%2C4a1345fa-7714-4654-b442-71132e1deac6%2C112bdf38-b1ad-46e2-bfe8-3964f9c55cd5%2Cfe3ba384-173b-47fd-9f1f-fb3d4ae671b7 | Concrete | Radial Joint | Leaks
42ad8481-6272-4e83-b518-0eab2a097b0b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:55:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 205 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68889 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 15/12/2021 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 205, 11 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | This has been patched. No leak evident. | yes | yes |  | yes | Reduce priority and risk | 693314bc-b972-49a9-a14f-b9d6cf3379b3,cec94885-ac64-48b3-bdc2-a862246bf692 | , | https://web.fulcrumapp.com/photos/view?photos=693314bc-b972-49a9-a14f-b9d6cf3379b3%2Ccec94885-ac64-48b3-bdc2-a862246bf692 | Concrete | Grout Hole | Leaks |  | Not reinforcement
28d370c1-4b94-4780-b4c2-0e46f4cfca8e | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 06:01:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 206 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 69159 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44550.6493 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 206, 10 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 25% coverage. Channel anchor bolts have Level 3 - Medium Corrosion. |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 25% coverage. Channel anchor bolts have Level 3 - Medium Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Main bracket is not corroding, however bolts are | no | yes |  | yes | Update description | d4b2a2fc-8193-4955-a9c7-5177a0955d27,6f25b978-8fc8-4f17-98f3-e13bb4f99ca1,074b61a9-05b7-4ae4-981b-1e6555586a99,21bbfbca-fdfd-40f1-ab0c-561e80e55632,81326ae9-7f4a-4a1c-8ef9-a1bbc61efa3e | ,,,, | https://web.fulcrumapp.com/photos/view?photos=d4b2a2fc-8193-4955-a9c7-5177a0955d27%2C6f25b978-8fc8-4f17-98f3-e13bb4f99ca1%2C074b61a9-05b7-4ae4-981b-1e6555586a99%2C21bbfbca-fdfd-40f1-ab0c-561e80e55632%2C81326ae9-7f4a-4a1c-8ef9-a1bbc61efa3e | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
fd08c06f-b0bc-47c3-94bd-c149fb1c4d0b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:53:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 207 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85888 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 207, 7 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size of 200mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | b452cfd1-2084-4290-b84d-3c1c766a2c37,facfe9e3-381e-4d93-9874-e2b698d320c5 | , | https://web.fulcrumapp.com/photos/view?photos=b452cfd1-2084-4290-b84d-3c1c766a2c37%2Cfacfe9e3-381e-4d93-9874-e2b698d320c5 | Concrete | Radial Joint | Drummy
30eb7ba0-2b7d-4916-b731-b77a54cbbe83 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:55:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 208 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85889 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 44875.7999 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 208, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. |  | Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Minor corrosion is evident in the steel anchor bracket. | no | yes |  | no |  | c794d209-5fcd-4eb2-a441-014c182133ae,fbf4df60-c511-4ef2-ad84-7a2c73cfa184 | , | https://web.fulcrumapp.com/photos/view?photos=c794d209-5fcd-4eb2-a441-014c182133ae%2Cfbf4df60-c511-4ef2-ad84-7a2c73cfa184 | Steel | Channel Bracket | Corrosion-Surface
58762854-9a31-47b5-baa3-99d2033bf602 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 06:04:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 209 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69157 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/12/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 209, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Supervisor | SS |  | This has been patched, with no sign of further leaking | yes | yes |  | yes | Update description and condition | 1c419270-dbd2-4513-b74e-1d79ba80e66f,cb4c14ff-4d60-4321-afe9-8509c7e21fbe,ce61fa83-0af5-4997-8f84-6614256905b3,8025d18d-b1a2-4c64-b4f5-73c42397b5a8 | ,,, | https://web.fulcrumapp.com/photos/view?photos=1c419270-dbd2-4513-b74e-1d79ba80e66f%2Ccb4c14ff-4d60-4321-afe9-8509c7e21fbe%2Cce61fa83-0af5-4997-8f84-6614256905b3%2C8025d18d-b1a2-4c64-b4f5-73c42397b5a8 | Concrete | Grout Hole | Leaks |  | Not reinforcement
ccf0dc4f-4bdf-4f1c-b476-22b7b7a9bb2b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:56:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 209 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85890 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 209, 7 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of same size of 400mm x 350mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of same size of 400mm x 350mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 12bdd1bd-47c2-4348-ae38-075513ec3bce,7de52eb8-bcc5-457e-a646-9c582b3ecf7f,a7075f26-8e10-4bde-812b-d30d71631175 | ,, | https://web.fulcrumapp.com/photos/view?photos=12bdd1bd-47c2-4348-ae38-075513ec3bce%2C7de52eb8-bcc5-457e-a646-9c582b3ecf7f%2Ca7075f26-8e10-4bde-812b-d30d71631175 | Concrete | Radial Joint | Drummy
10de8c3f-3daa-437a-8545-e6b0fa0ae7e4 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 14 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:59:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 210 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27443 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 210, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion. |  | Steel channel support bracket has Level 3 - Medium Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Minor corrosion in the steel anchor bracket. | no | no |  | no |  | 8d4349e4-3d57-46e6-8ea1-60e6712a3d26,a6267e5d-ced0-4de0-ac8d-bda88b2eaa57 | , | https://web.fulcrumapp.com/photos/view?photos=8d4349e4-3d57-46e6-8ea1-60e6712a3d26%2Ca6267e5d-ced0-4de0-ac8d-bda88b2eaa57 | Steel | Channel Bracket | Corrosion-Surface
b013d6e6-a2d0-403c-b4b3-a244c5c20ce5 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 9 |  |  |  | 2025-07-26 04:37:11 AEST | 2025-07-26 04:42:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | 188 | 5 |  |  | Steel footing plate and bolts | [14 empty] | Corrosion - Connection |  | 4 | [9 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Vertical support and footing |  |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | [19 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 10% section loss |  | yes |  | yes | Fill blank fields | 50834895-acfd-40d9-84cf-bd0e2867de9f,b75116f2-62fd-4061-9fde-d63418a80516,02dafcc6-ddd9-47e0-86b8-b00c661f50ac,a5036ff8-6729-4ed8-835b-a6d60ae6a391 | ,,, | https://web.fulcrumapp.com/photos/view?photos=50834895-acfd-40d9-84cf-bd0e2867de9f%2Cb75116f2-62fd-4061-9fde-d63418a80516%2C02dafcc6-ddd9-47e0-86b8-b00c661f50ac%2Ca5036ff8-6729-4ed8-835b-a6d60ae6a391 | Steel | Walkway Support | Corrosion-Heavy
db2b23b8-7585-40cf-9a5f-1927849f9255 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 9 |  |  |  | 2025-07-26 04:44:28 AEST | 2025-07-26 04:46:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 192 | 5 |  |  | Steel footing plate and bolts | [14 empty] | Corrosion - Connection |  | 4 | [9 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Vertical support and footing |  |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | [19 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 10% section loss |  | yes |  | yes | Fill blank fields | c0e92b4b-3ce1-44ef-91b9-6ee6902e11e3,08894690-add4-4226-8dce-b98ff4ae73ea,29859e54-aa9f-488d-9e9a-0cf0941d614d | ,, | https://web.fulcrumapp.com/photos/view?photos=c0e92b4b-3ce1-44ef-91b9-6ee6902e11e3%2C08894690-add4-4226-8dce-b98ff4ae73ea%2C29859e54-aa9f-488d-9e9a-0cf0941d614d | Steel | Walkway Support | Corrosion-Heavy
8601ee5d-c41e-42f7-8007-3578a3b0f042 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 9 |  |  |  | 2025-07-26 04:47:14 AEST | 2025-07-28 14:45:21 AEST | 30011704-user5@smec.com | james.stone@smec.com | 196 | 5 |  |  | Steel footing plate and bolts | [14 empty] | Corrosion - Connection |  | 4 | [9 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Vertical support and footing |  |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | [19 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 10% section loss |  | yes |  | yes | Fill blank fields | 5e5fdae3-3d2f-4a70-99d9-03b16392c876,cc97bb52-451b-47bb-8c22-bd808872e046,c85e52d7-fa1a-4ce9-abb1-03c07fee87a6 | ,, | https://web.fulcrumapp.com/photos/view?photos=5e5fdae3-3d2f-4a70-99d9-03b16392c876%2Ccc97bb52-451b-47bb-8c22-bd808872e046%2Cc85e52d7-fa1a-4ce9-abb1-03c07fee87a6 | Steel | Walkway Support | Corrosion-Heavy
8698e62b-b6e8-4d41-aeaa-49aee47bcbd9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 9 |  |  |  | 2025-07-26 04:50:42 AEST | 2025-07-26 04:52:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 200 | 5 |  |  | Steel footing plate and bolts | [14 empty] | Corrosion - Connection |  | 4 | [9 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Vertical support and footing |  |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | [19 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 10% section loss |  | yes |  | yes | Fill blank fields | b6a8e03f-e757-48e6-8198-79c8e0fa9794,3b745c30-2da7-44a4-bea0-88c25f46d59a,62031d99-4df1-4764-97da-81d0d9f2508c | ,, | https://web.fulcrumapp.com/photos/view?photos=b6a8e03f-e757-48e6-8198-79c8e0fa9794%2C3b745c30-2da7-44a4-bea0-88c25f46d59a%2C62031d99-4df1-4764-97da-81d0d9f2508c | Steel | Walkway Support | Corrosion-Heavy
45e1a202-ec6c-4f96-9967-dc09739ecf52 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 7 |  |  |  | 2025-07-27 02:49:29 AEST | 2025-07-27 02:50:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 205 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99570 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 204, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / Drummy Grout at radial joint over area of same size 300mm x 300mm. |  | Grout Delamination / Drummy Grout at radial joint over area of same size 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 1f8630da-d067-4562-b214-ab92e7b475ff,52c51ba5-e515-4c11-9408-32c7968e75fd | , | https://web.fulcrumapp.com/photos/view?photos=1f8630da-d067-4562-b214-ab92e7b475ff%2C52c51ba5-e515-4c11-9408-32c7968e75fd | Concrete | Radial Joint | Drummy
0435f395-9584-44d0-a212-edd1b71b71e7 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 3 |  |  |  | 2025-07-30 02:31:56 AEST | 2025-07-30 02:36:03 AEST | 30011704-user5@smec.com | james.stone@smec.com | 188 | 7 |  |  | Steel footing plate and bolts | [14 empty] | Corrosion - Connection |  | 4 | [9 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Vertical support and footing | [5 empty] | Level 3 to 4 corrosion of plates. Also, one of the anchor bolts is missing, presumed corroded away. | [18 empty] | SS |  | Nuts are showing roughly 10% section loss. Base plate is showing roughly 10% section loss |  | no |  | yes | Fill blank fields | e6ac11b4-9bae-42a4-b90d-a111d05dc4c1,386fba4e-1692-47b9-b489-d26b15d0ba35,2bf6226d-214f-4d35-b9a9-87df01ec42c3 | ,, | https://web.fulcrumapp.com/photos/view?photos=e6ac11b4-9bae-42a4-b90d-a111d05dc4c1%2C386fba4e-1692-47b9-b489-d26b15d0ba35%2C2bf6226d-214f-4d35-b9a9-87df01ec42c3 | Steel | Walkway Support | Corrosion-Heavy,Missing |  | Walkway Support not Centre Support
b91d8619-2ffb-4c20-8809-e57d14e6cdc0 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:09:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 211 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 99572 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 211, 3 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle Joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Circle Joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | HM |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact | no | no |  | yes | Priority to be downgraded to P4 | 50b297bb-d31b-45e0-92a2-6a7d80d5682a,90111df9-724b-4108-962e-df788c7c32e6 | , | https://web.fulcrumapp.com/photos/view?photos=50b297bb-d31b-45e0-92a2-6a7d80d5682a%2C90111df9-724b-4108-962e-df788c7c32e6 | Concrete | Circular Joint | Drummy
6f2fa6df-4ab9-4b9f-8aa1-724595d71659 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:22:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 212 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26862 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 212, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint between Ring 211 & 212 has leak Inactive at time of inspection. |  | Circle joint between Ring 211 & 212 has leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | Leak still seems inactive. This should still be treated. | no | yes |  | no |  | 7f4001d3-77fe-4db1-ac41-5ddb55e0baa9,1b89e0a5-a70a-4798-bb38-a8a753db8ae7,26abfb80-1fa1-4640-84e0-a9177a4a8a77,cbe78643-9d28-4905-91c2-141f4016e4ff | ,,, | https://web.fulcrumapp.com/photos/view?photos=7f4001d3-77fe-4db1-ac41-5ddb55e0baa9%2C1b89e0a5-a70a-4798-bb38-a8a753db8ae7%2C26abfb80-1fa1-4640-84e0-a9177a4a8a77%2Ccbe78643-9d28-4905-91c2-141f4016e4ff | Concrete | Circular Joint | Leaks |  | Not reinforcement
3eeb6d62-9e00-44f4-9b6a-0b0e4539bd88 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:11:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 212 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85891 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 212, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | yes | no |  | yes | Priority and risk to be downgraded | b2d77ca2-c55c-44f9-87ee-bed383c24e97,e7936735-238d-49a7-bf47-a9ee6ae26e43 | , | https://web.fulcrumapp.com/photos/view?photos=b2d77ca2-c55c-44f9-87ee-bed383c24e97%2Ce7936735-238d-49a7-bf47-a9ee6ae26e43 | Concrete | Circular Joint | Drummy
f4b96f10-4ca8-4a14-8c09-4f48d8bb48ac | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:02:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 212 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99573 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 212, 7 o'clock, Segmented Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Radial Joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial Joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. Grout has spalled away over most of the connection | no | no |  | yes | Priority and risk to be downgraded | 20d23781-85ee-4873-afa8-39e938e4ecbd,f3321cd0-5cdd-42a2-b9e4-5d34eae2dea1 | , | https://web.fulcrumapp.com/photos/view?photos=20d23781-85ee-4873-afa8-39e938e4ecbd%2Cf3321cd0-5cdd-42a2-b9e4-5d34eae2dea1 | Concrete | Radial Joint | Drummy,Surface Damage
b1c6be0f-a75a-40f7-957a-f8a1d020baac | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:12:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 214 | 2 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 99574 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 45415.4039 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 214, 2 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Crack in grout patch of 0.1mm wide and 200mm long. |  | Crack in grout patch of 0.1mm wide and 200mm long. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This is not considered a significant defect | no | yes |  | no |  | a3c0cf9b-2f7d-4e33-90d7-6f2aa89de423,5664954b-4216-4c5c-b013-a15635bfe4d0 | , | https://web.fulcrumapp.com/photos/view?photos=a3c0cf9b-2f7d-4e33-90d7-6f2aa89de423%2C5664954b-4216-4c5c-b013-a15635bfe4d0 | Concrete | Radial Joint | Crack
bb814c00-8560-4524-8b35-cf6807aac3c4 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:15:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 215 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69161 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 215, 2 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | No change | no | yes |  | no |  | 721a6368-0ee3-4a00-90c9-e7cec9557117,f6a1f104-ef88-46a6-a299-44025eeedcda | , | https://web.fulcrumapp.com/photos/view?photos=721a6368-0ee3-4a00-90c9-e7cec9557117%2Cf6a1f104-ef88-46a6-a299-44025eeedcda | Concrete | Grout Hole | Leaks |  | Not reinforcement
65c23745-b085-4b2a-a7fb-afff57709387 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:05:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 215 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99575 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 215, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial Joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial Joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 6556226c-48aa-40f4-9f4c-103a3f8e98b4,0d477d29-b929-4575-a20e-47644980100e | , | https://web.fulcrumapp.com/photos/view?photos=6556226c-48aa-40f4-9f4c-103a3f8e98b4%2C0d477d29-b929-4575-a20e-47644980100e | Concrete | Radial Joint | Drummy
217f48ed-f901-40bb-a5df-7768abf351b8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:19:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 215 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27446 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 215,1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | The typical bolt in the base of the port is not visible, however grout is seen. Liquid is noted to be emanating slowly, however no salts are depositing. Still to be treated. | no | yes |  | yes | Update description | a6e0b2e4-db9b-49b2-9d6d-29bbe50390d4,1d888be2-04a6-4241-927d-2910d4a99ff0,99063f92-60e7-47e4-976e-094afdc4f4af | ,, | https://web.fulcrumapp.com/photos/view?photos=a6e0b2e4-db9b-49b2-9d6d-29bbe50390d4%2C1d888be2-04a6-4241-927d-2910d4a99ff0%2C99063f92-60e7-47e4-976e-094afdc4f4af | Concrete | Grout Hole | Leaks |  | Not reinforcement
ccecdf3f-5227-420f-891c-4ec6bfa58963 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:16:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 216 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85892 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 216, 1 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 7f5cf3fd-a759-4c42-889a-747c90e9399c,0a2c5fcf-a01f-4320-ab05-4ef844dc3b4e | , | https://web.fulcrumapp.com/photos/view?photos=7f5cf3fd-a759-4c42-889a-747c90e9399c%2C0a2c5fcf-a01f-4320-ab05-4ef844dc3b4e | Concrete | Circular Joint | Drummy
7f1a03f0-777d-4ed1-af2e-da8af53b2ab5 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:12:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 216 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69162 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 216, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | No | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | Leak is still inactive | no | yes |  | no |  | 6b872d0d-c1f5-41c3-9180-7db58933c914,1c41c3f2-30a9-4f3f-957f-0d80a92909c2 | , | https://web.fulcrumapp.com/photos/view?photos=6b872d0d-c1f5-41c3-9180-7db58933c914%2C1c41c3f2-30a9-4f3f-957f-0d80a92909c2 | Concrete | Grout Hole | Leaks |  | Not reinforcement
30e83917-3a63-4839-b329-6b9aee33150d | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:18:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 216 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26863 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 216, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2- Surface Corrosion and missing 1 bolt. |  | Steel channel support bracket has Level 2- Surface Corrosion and missing 1 bolt. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Corrosion is extremely minor. Missing bolt noted, however this is within allowed limits | no | yes |  | yes | Update description | da590e1a-b6fc-48d7-82d9-d6ca09b9638d,f9857c9d-a198-4b42-a9e2-c4456a13b939 | , | https://web.fulcrumapp.com/photos/view?photos=da590e1a-b6fc-48d7-82d9-d6ca09b9638d%2Cf9857c9d-a198-4b42-a9e2-c4456a13b939 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
985293b2-5faf-4288-9151-be9b0dd6e51a | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:08:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 218 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27103 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 218, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | SS |  | This defect is identical to the one at 12 o'clock. This duplication adds no value. Suggest deleting this one. | no | yes |  | yes | Suggest deleting this duplicate |  |  |  | Concrete | Reinforcement | Leaks |  | Duplicate - Remove
fe693e76-3162-4a19-aeca-956d3f3aa13e | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:06:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 218 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 69163 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 218, 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 3 - Surface Corrosion up to 5% coverage. Channel anchor bolts have Level 4 - Medium High Corrosion. |  | Steel channel support bracket has Level 3 - Surface Corrosion up to 5% coverage. Channel anchor bolts have Level 4 - Medium High Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. 3. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Scaffolding | - | Corrosion Repair Competent Supervisor | SS |  | Associated with other works on this area. While this defect is correctly a P3, the other works are P2, and this should be done at the same time. | no | yes |  | no |  | afc7e22a-3764-4d46-be20-26c6ebc2bfbc,72973e32-f780-4246-83b9-e54304c71dc6 | , | https://web.fulcrumapp.com/photos/view?photos=afc7e22a-3764-4d46-be20-26c6ebc2bfbc%2C72973e32-f780-4246-83b9-e54304c71dc6 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
5ed0e1ff-0b8d-4797-839d-3208ad26e6d9 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:56:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 218 | 12 | Grout Injection Hole | Grout Injection Hole |  | 68890 |  | 6311 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 15/12/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 218, 11, 12 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer | SS |  | Leak is behind a bracket, and has caused enormous damage to it. Suggest increasing priority to P2. | yes | no |  | yes | Increase priority to P2, condition to 4 | 7b19c6ee-5672-4301-92aa-15aa8eb84188,231f51af-8a8c-43e2-8b09-22b1b41fe330,f10d8c19-826d-4a92-b774-fc872f1ad25d,33794802-4e00-4f25-973d-403bfef0a6af | ,,, | https://web.fulcrumapp.com/photos/view?photos=7b19c6ee-5672-4301-92aa-15aa8eb84188%2C231f51af-8a8c-43e2-8b09-22b1b41fe330%2Cf10d8c19-826d-4a92-b774-fc872f1ad25d%2C33794802-4e00-4f25-973d-403bfef0a6af | Concrete | Grout Hole | Leaks |  | Not reinforcement
d237f5e8-afd9-4956-9d04-35f5da7da5e8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:59:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 218 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85893 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 10/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 218, 12 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has leak - Active at time of inspection. |  | Concrete shell segment at bolted connection penetration has leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | In conjunction with the similar issue on the 11oclock end of the same bracket, this entire area needs works. | no | yes |  | yes | Update description | e97294af-a50b-420a-8712-a5aef4725666,97b7b63e-ef3a-4f43-b3af-159695897554,94d329dc-31b3-46b6-a803-a4a538209f7c | ,, | https://web.fulcrumapp.com/photos/view?photos=e97294af-a50b-420a-8712-a5aef4725666%2C97b7b63e-ef3a-4f43-b3af-159695897554%2C94d329dc-31b3-46b6-a803-a4a538209f7c | Concrete | Channel Bracket | Leaks |  | Steel channel
f003acb6-94af-457c-9fda-6c3ac642fa41 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:03:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 218 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 26864 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Structure,Ring 218,11 O'Clock,Support Bracket,Still existing in 2017. | Rupture | Rupture |  | Class 4 - Medium high corrosion of steelwork and Class 5 Corrosion of bolts. |  | Class 4 - Medium high corrosion of steelwork and Class 5 Corrosion of bolts. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), revised recommended action to include replacement of corroded anchor bolts. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Likely Likelihood of failure, resulting in a Priority 2. | Loss of services | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. 3. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | SS |  | See associated defects in this area. The bolts on the 9-11 section are almost all completely gone. Leak needs to be treated, and the steelwork replaced. | no | no |  | yes | Increase priority to P2 | 160f4acb-3899-4c2f-ad22-61eda55d1b72,94e5774b-e438-4817-9948-c5f89bddffc0,7fb3401f-6f5d-4126-8fa2-cd9d3be8a483,2ab891b7-1fb6-490c-b71a-ae809345d6bc,c424f3d0-e74f-4269-8526-33385068a11c,dcd1ef1e-c993-4893-a97e-d9dbe7541c3d,a9e0ed59-53e5-413d-8b55-e558b20d93d3 | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=160f4acb-3899-4c2f-ad22-61eda55d1b72%2C94e5774b-e438-4817-9948-c5f89bddffc0%2C7fb3401f-6f5d-4126-8fa2-cd9d3be8a483%2C2ab891b7-1fb6-490c-b71a-ae809345d6bc%2Cc424f3d0-e74f-4269-8526-33385068a11c%2Cdcd1ef1e-c993-4893-a97e-d9dbe7541c3d%2Ca9e0ed59-53e5-413d-8b55-e558b20d93d3 | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks
07542b54-89a3-4927-b6b3-dedf9585949f | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:50:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 219 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 85894 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 1-225) | SIM-FixedPlant |  |  | 44875.81 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 219, 1 O'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings |  |  |  | Concrete shell segment has Cracking - Crack extending 50mm and 0.3mm in width. |  | Concrete shell segment has Cracking - Crack extending 50mm and 0.3mm in width. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This is not a significant defect | no | yes |  | yes | Update description | b6306faf-35ca-4a95-84f8-a75854dd65ba,1d57c757-a452-4f99-81ed-7c4abeb5f9a5 | , | https://web.fulcrumapp.com/photos/view?photos=b6306faf-35ca-4a95-84f8-a75854dd65ba%2C1d57c757-a452-4f99-81ed-7c4abeb5f9a5 | Concrete | Circular Joint | Crack |  | Circular Joint
486d3faf-2261-4a46-aa8c-50d11de588e2 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:46:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 220 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 99576 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 220, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete at segmental concrete wall over an area of 500mm x 500mm. Rust staining was observed. There is local spalling and 25mm cover loss. |  | Concrete shell segment has drummy concrete at segmental concrete wall over an area of 500mm x 500mm. Rust staining was observed. There is local spalling and 25mm cover loss. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | This defect is still untreated. Affected area is in parent concrete material, not patching grout over bolted connections. Spalled area is 300x100 with depth of 40mm. Drummy area is 600x600. This needs to be treated. | no | yes |  | yes | Update description | 9548eb65-137f-4204-b8c9-43a267781b76,26a23157-b67a-4398-a788-df2d4be4edb0,6b6a98c1-a2a8-4b9e-8b15-7aaab3283acd | ,, | https://web.fulcrumapp.com/photos/view?photos=9548eb65-137f-4204-b8c9-43a267781b76%2C26a23157-b67a-4398-a788-df2d4be4edb0%2C6b6a98c1-a2a8-4b9e-8b15-7aaab3283acd | Concrete | Grout Hole | Drummy,Surface Damage |  | Grout Holr
02e231be-5df8-4df7-9aa2-0afd2c273566 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:41:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 221 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69166 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 221, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | Hole has been patched, no leaking evidenced. | yes | no |  | yes | Suggest downgrade priority to P4 | cd4be038-6871-4482-844b-d5dd066ee6a1,25ce82ba-7044-41f5-9265-3ed1a40953e2 | , | https://web.fulcrumapp.com/photos/view?photos=cd4be038-6871-4482-844b-d5dd066ee6a1%2C25ce82ba-7044-41f5-9265-3ed1a40953e2 | Concrete | Grout Hole | Leaks |  | Not reinforcement
53e52f68-7f42-4275-87c5-1441702de853 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:12:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 221 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 99577 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 221, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial Joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial Joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Accelerate deterioration of concrete ring which may lead to local ring collapse and partial flooding of tunnel. | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 1b6bf916-3930-47fd-99a5-b506d9a29bf2,c314f965-ab83-4c78-b929-1962a56f7a19 | , | https://web.fulcrumapp.com/photos/view?photos=1b6bf916-3930-47fd-99a5-b506d9a29bf2%2Cc314f965-ab83-4c78-b929-1962a56f7a19 | Concrete | Radial Joint | Drummy
37fbf95d-9882-476d-8758-8f1e4576e9e0 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:21:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 222 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 69167 |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 222, 1 & 2 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel bracket has Level 4 - Surface Corrosion up to 5% coverage. All channel anchor bolts have Level 5 - High Corrosion. |  | Steel channel bracket has Level 4 - Surface Corrosion up to 5% coverage. All channel anchor bolts have Level 5 - High Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. 3. Replace corroded anchor bolts. Bolt size and specification to match as per existing or original design. There should be at least two (2) threads pf projection outside the nut and maximum of 10mm when fully tightened. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak is causing corrosion, see other defects for detail | no | yes |  | no |  | a0bab063-72ad-4a89-9ca0-d56dac515f2d,da73b2bd-28b6-4067-bf98-cbccde56db54,4feb5552-e524-4282-931a-1f4e2b3bd3e1,3859679d-87e4-44ef-9312-05e0136ad3b8,0263cd5c-0470-48cb-8636-87ffc8de9e41 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=a0bab063-72ad-4a89-9ca0-d56dac515f2d%2Cda73b2bd-28b6-4067-bf98-cbccde56db54%2C4feb5552-e524-4282-931a-1f4e2b3bd3e1%2C3859679d-87e4-44ef-9312-05e0136ad3b8%2C0263cd5c-0470-48cb-8636-87ffc8de9e41 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Leaks
d644bca6-f382-41e8-aa10-5ec89677ef45 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:38:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 222 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26866 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 222, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. Evidence of etching. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. Evidence of etching. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Nil | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | SS |  | Leak not active at time of inspection, however corrosion damage on bracket is advancing | no | yes |  | no |  | f880c58e-e0dc-429b-886d-f01e25e998b3,54f78566-43da-45ed-a83e-848bcf4a90aa,6ba592e1-04c5-4e40-af67-02917a5ff2fa | ,, | https://web.fulcrumapp.com/photos/view?photos=f880c58e-e0dc-429b-886d-f01e25e998b3%2C54f78566-43da-45ed-a83e-848bcf4a90aa%2C6ba592e1-04c5-4e40-af67-02917a5ff2fa | Concrete | Reinforcement | Leaks
0fffb071-c977-411e-bd92-72b9becd739f | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:35:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 222 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 26865 |  | 6311 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 222, 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 - Major Corrosion |  | Steel channel support bracket has Level 4 - Major Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of services | Priority: P3 |  |  |  | Remove corrosion by abrasive blasting or mechanical means. Carry out over-plate repairs / apply protective coatings in accordance with BHP Procedures and Standard Repair Details | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | Scaffolding | Working at Heights | Corrosion Repair Competent Supervisor | SS |  | Corrosion is advancing | no | yes |  | no |  | c16c6718-21e8-4e70-94b8-bcf45264aa12,2a42b45f-1da3-4b3c-82c4-8c3745788f27,0fc7cca5-7559-4f76-bdab-32b16ac8f99e | ,, | https://web.fulcrumapp.com/photos/view?photos=c16c6718-21e8-4e70-94b8-bcf45264aa12%2C2a42b45f-1da3-4b3c-82c4-8c3745788f27%2C0fc7cca5-7559-4f76-bdab-32b16ac8f99e | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
60be9aac-6c7a-41aa-9077-26474891fb6b | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 08:32:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 223 | 1 | Grout Injection Hole | Grout Injection Hole |  | 68896 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 223, 1 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | Leak still inactive | no | yes |  | no |  | 9f8a872d-a1f2-49ff-9e4b-ccd29a127749,28e13da9-2cc3-4a14-b50e-5db1fb1a4978 | , | https://web.fulcrumapp.com/photos/view?photos=9f8a872d-a1f2-49ff-9e4b-ccd29a127749%2C28e13da9-2cc3-4a14-b50e-5db1fb1a4978 | Concrete | Grout Hole | Leaks |  | Not reinforcement
2201324a-f06f-4d5f-9aaf-62309893fd4a | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 | -20.3178 | 118.5772 | POINT (118.5772307 -20.3178498) | 2025-05-27 20:13:18 AEST | 2025-07-27 08:31:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 224 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 99578 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant |  |  | 45415.4118 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 224, 10-12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion |  | Steel channel support bracket has Level 2 - Minor Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change noted | no | yes |  | no |  | 80f40d81-9e25-4e7a-bb73-75d51e6a7382,ad505a0f-172b-4df3-8a57-4f68360c7e68,3326c48a-b223-49c3-997c-4a2903de57fc,869e960e-a4c5-48da-996c-f0ba2b7ab39c | ,,, | https://web.fulcrumapp.com/photos/view?photos=80f40d81-9e25-4e7a-bb73-75d51e6a7382%2Cad505a0f-172b-4df3-8a57-4f68360c7e68%2C3326c48a-b223-49c3-997c-4a2903de57fc%2C869e960e-a4c5-48da-996c-f0ba2b7ab39c | Steel | Channel Bracket | Corrosion-Surface
72f2237d-6e4e-48f9-82f8-1a0b6fe82f35 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 08:32:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 226 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76352 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 226, 11, 12 and 1 O'clock, Channel Anchor Bolts. | Rupture | Rupture |  | Channel anchor bolts have Level 3 Corrosion. |  | Channel anchor bolts have Level 3 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor - isolated corroded bolt only. | Financial | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair Guideline 0136559. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No significant bolt corrosion noted | yes | no |  | yes | Consider deleting this defect, no significant bolt corrosion noted | 3bed9742-a0fd-468c-8752-6858c5d7373f,64bc20fe-f2e1-4c96-a8d6-ef55375095af,6633e60b-9d07-4b6f-baf0-32956f43935a | ,, | https://web.fulcrumapp.com/photos/view?photos=3bed9742-a0fd-468c-8752-6858c5d7373f%2C64bc20fe-f2e1-4c96-a8d6-ef55375095af%2C6633e60b-9d07-4b6f-baf0-32956f43935a | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
2330b2bb-b15b-468d-89aa-b79d21765f32 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 08:30:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 226 | 0 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 36547 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43900.6152 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 226, 2 & 8 O'clock, Segment Bolted Joint (Radial Joint). |  |  |  | Level 3 corrosion at cast in embedded lugs at radial bolted joints. |  | Level 3 corrosion at cast in embedded lugs at radial bolted joints. | Movement of shell segments about joint resulting in leak |  | Movement of shell segments about joint resulting in leak |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | no |  | d9b5ca07-578b-42c8-85a2-161b2ab2c4eb |  | https://web.fulcrumapp.com/photos/view?photos=d9b5ca07-578b-42c8-85a2-161b2ab2c4eb | Concrete | Radial Joint | Drummy
34e06e19-da5f-41e5-a8c4-683a77a13649 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:23:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 226 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36546 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43900.6126 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 226, 2 O'clock, Channel Anchor Bolts. |  |  |  | Channel anchor bolts have Level 2 Corrosion. Some bolts are missing. |  | Channel anchor bolts have Level 2 Corrosion. Some bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 34e72838-dc6e-406f-a46f-38a0c6a910a1,fe707eb2-0c01-47f4-ba50-0504ccee2a56,6959bab7-98f7-4264-b46a-f73577fea112,1919bcf2-1c7c-4441-8dda-e8d4e59b75cf | ,,, | https://web.fulcrumapp.com/photos/view?photos=34e72838-dc6e-406f-a46f-38a0c6a910a1%2Cfe707eb2-0c01-47f4-ba50-0504ccee2a56%2C6959bab7-98f7-4264-b46a-f73577fea112%2C1919bcf2-1c7c-4441-8dda-e8d4e59b75cf | Steel | Channel Bracket-Bolt | Missing
fed66125-e2f1-4fd1-bf29-f0ad4b392319 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 08:33:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 226 | 3 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 101834 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 45554.4712 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 226, 3 O' Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 96e220bd-228d-4bba-8211-19c58042844a,d6a4ab7d-f40a-462b-b897-cd9549800c40 | , | https://web.fulcrumapp.com/photos/view?photos=96e220bd-228d-4bba-8211-19c58042844a%2Cd6a4ab7d-f40a-462b-b897-cd9549800c40 | Concrete | Circular Joint | Drummy
093d3baf-b03d-448f-904c-f51e814b087d | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:24:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 226 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26915 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 226, 3 O'Clock, Steel Channel Bracket and Anchor Botls |  |  |  | Level 1 corrosion of steel channel support and missing bolt at 2 o'clock. |  | Level 1 corrosion of steel channel support and missing bolt at 2 o'clock. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This is a duplication of defect at 2 o'clock |  |  |  | yes | Consider deleting this duplicate defect |  |  |  | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
d67aa73d-eee7-4ed1-a950-6de9f932a736 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 08:36:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 226 | 9 | Grout Injection Hole | Grout Injection Hole |  | 88596 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 226, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak is slow, if active. BHP AIMS agreed on P2 for this category | no | yes |  | no |  | e0411d29-87ed-433d-80ec-1831763586c9,f26655be-b856-476b-bc58-8cef466af992,0be8b3f7-f868-4f1e-b14e-c478dee441cc | ,, | https://web.fulcrumapp.com/photos/view?photos=e0411d29-87ed-433d-80ec-1831763586c9%2Cf26655be-b856-476b-bc58-8cef466af992%2C0be8b3f7-f868-4f1e-b14e-c478dee441cc | Concrete | Grout Hole | Leaks
5bde7b44-c4b1-4feb-a1b8-e0aa675aea74 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:27:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 227 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 101835 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 45554.4744 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 227, 4 O' Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 07d45ac5-fe10-431e-8008-6bf3cac844dd,fe5ee7b2-7882-4194-afdd-14d830299124 | , | https://web.fulcrumapp.com/photos/view?photos=07d45ac5-fe10-431e-8008-6bf3cac844dd%2Cfe5ee7b2-7882-4194-afdd-14d830299124 | Concrete | Circular Joint | Drummy
bf04883b-e086-483b-a5d1-6b8ba5dabfa6 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 08:38:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 227 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36548 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43900.6166 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring: 227, 4, 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 to Level 3 corrosion at sump pump bracket fasterners and steelworks. |  | Level 2 to Level 3 corrosion at sump pump bracket fasterners and steelworks. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | no |  | 3151291e-de6f-4188-a916-e7121676c20f,4ab18e7f-5732-48bc-a05b-3f7d26417165,270ef497-a546-44bd-9227-f25887b8469c | ,, | https://web.fulcrumapp.com/photos/view?photos=3151291e-de6f-4188-a916-e7121676c20f%2C4ab18e7f-5732-48bc-a05b-3f7d26417165%2C270ef497-a546-44bd-9227-f25887b8469c | Steel | Conveyor Support | Drummy |  | Conveyor Support
116a04f2-b6d7-4dcb-b19c-794f5d0b91e6 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 23:28:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 228 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 88597 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4507 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 228, 11 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 Corrosion. Channel anchor bolts has Level 2 Corrosion |  | Steel channel support bracket has Level 1 Corrosion. Channel anchor bolts has Level 2 Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This is a duplicate defect |  |  |  | yes | Delete this duplicate defect |  |  |  | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Duplicate - Remove
d040f5a8-1303-40d5-b187-fded436630e3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:28:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 228 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26916 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 228, 11, 12, 1, 2 & 3 O'clock, Channel Anchor Bolts. |  |  |  | Channel anchor bolts have level 1 corrosion. |  | Channel anchor bolts have level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This is redundant. Suggest deleting this defect | no | yes |  | yes | Consider deleting this defect |  |  |  | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Duplicate - Remove
cfd7f5c8-87da-4440-9509-9a2f6af2c666 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:27:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 228 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36549 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43900.618 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 228, 8 & 11 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 corrosion at conveyor anchor bolts and baseplates. Nuts are loose. |  | Level 2 corrosion at conveyor anchor bolts and baseplates. Nuts are loose. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 103087d2-5326-4152-8876-266cf43ed92e,613af19b-80ba-409c-86d9-64553aa42ea8,3dfed988-37fa-4aea-8ca5-91d4c6c49b8d,740791d7-cfdd-4bd9-808b-9f8d9cf09f80,9a9153ba-26d3-465a-b1f2-d09b49887cdd | ,,,, | https://web.fulcrumapp.com/photos/view?photos=103087d2-5326-4152-8876-266cf43ed92e%2C613af19b-80ba-409c-86d9-64553aa42ea8%2C3dfed988-37fa-4aea-8ca5-91d4c6c49b8d%2C740791d7-cfdd-4bd9-808b-9f8d9cf09f80%2C9a9153ba-26d3-465a-b1f2-d09b49887cdd | Steel | Channel Bracket-Bolt | Loose
537584be-33a3-43e6-9f19-224bc1a1796d | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 08:39:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 229 | 12 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88598 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.453 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 229, 12 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 09977a16-25cf-4c81-9e71-fafb50475aec,acc3fc25-2cd1-4d53-805d-409ec5fe4c0e | , | https://web.fulcrumapp.com/photos/view?photos=09977a16-25cf-4c81-9e71-fafb50475aec%2Cacc3fc25-2cd1-4d53-805d-409ec5fe4c0e | Concrete | Circular Joint | Drummy
21f82bd2-de36-4d02-8af4-82ee4e2c420e | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:29:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 229 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27143 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 229, 3 O'Clock, Cable Tray |  |  |  | Cable tray has Level 2 corrosion |  | Cable tray has Level 2 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | d8d43443-05c8-4ede-816b-debabe012b5a,558966b3-23f5-41ea-885f-9c65115243ff | , | https://web.fulcrumapp.com/photos/view?photos=d8d43443-05c8-4ede-816b-debabe012b5a%2C558966b3-23f5-41ea-885f-9c65115243ff | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
c0498b8d-d864-4b91-81a3-f8e50f564927 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 23:15:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 230 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 88599 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4549 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 230, 11 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 Corrosion. Missing 2 channel anchor bolts. |  | Steel channel support bracket has Level 1 Corrosion. Missing 2 channel anchor bolts. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Appears to be caused by water discharge pipe nearby | no | yes |  | no |  | e4a4a073-c245-467a-a307-0b3fb58d587a,254c01d0-bd6f-4eaf-8519-f12a3a137ec2,07c59028-ec82-4169-84de-612eea6d6a87,67937530-f9ac-4c67-89ae-e1eae644159c | ,,, | https://web.fulcrumapp.com/photos/view?photos=e4a4a073-c245-467a-a307-0b3fb58d587a%2C254c01d0-bd6f-4eaf-8519-f12a3a137ec2%2C07c59028-ec82-4169-84de-612eea6d6a87%2C67937530-f9ac-4c67-89ae-e1eae644159c | Steel | Channel Bracket,Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Missing
2c168330-b438-49ab-9dda-0d2e8268c5e3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:31:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 230 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27145 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 230, 2 & 3 O'clock Channel Anchor Bolts. | Rupture | Rupture |  | Channel anchor bolts have Level 4 Corrosion |  | Channel anchor bolts have Level 4 Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Financial | Priority: P3 |  |  |  | Remove and replace corroded anchor bolt one at a time if possible. If bolt cannot be removed, carry out repair following Steel Corrosion Repair 000-S-12598 corroded anchor bolt details. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair 000-S-12598 corroded anchor bolt details. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | SS |  | Leab behind bracket is causing corrosion | no | yes |  | no |  | 347f9283-3877-4f40-a38c-d1d8a8849904,5dc8814d-f02e-412a-a92e-215daf02085b | , | https://web.fulcrumapp.com/photos/view?photos=347f9283-3877-4f40-a38c-d1d8a8849904%2C5dc8814d-f02e-412a-a92e-215daf02085b | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
ad583a5e-4e21-4027-9ad9-59497bdadd9a | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 08:39:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 230 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36552 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 230, 2 & 3 O'clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak still appears active and is causing corrosion in adjacent steelwork | no | yes |  | no |  | a4b6739c-abe2-42ff-918e-fad40c537281,2ec26df1-e910-4d70-8109-24e020031d9f,ec236f05-bc47-4787-8df0-31527d6b5432 | ,, | https://web.fulcrumapp.com/photos/view?photos=a4b6739c-abe2-42ff-918e-fad40c537281%2C2ec26df1-e910-4d70-8109-24e020031d9f%2Cec236f05-bc47-4787-8df0-31527d6b5432 | Concrete |  | Leaks |  | Not reinforcement
35815c9e-59a2-48f2-a61e-63538f0de569 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:34:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 230 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27144 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 230, 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Steel channel support bracket has Level 3 Corrosion. |  | Steel channel support bracket has Level 3 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Not Specified | Priority: P3 |  |  |  | Replace damaged bolts one at a time as per original design specification. Remove corrosion by abrasive blasting or mechanical means and reinstate protective coatings in accordance with BHP specifications. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair Guideline 0136559. | No | Off-Line | Yes | - | Working at Heights, Confined Space, Hot Work, Excavation | Blast & Paint Repair Competent Supervisor | SS |  | This is a redundant defect, the other channel bracket defect covers this issue |  |  |  | yes | Consider deleting this redundant defect |  |  |  | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface |  | Duplicate - Remove
163978b1-cde7-4209-ab72-3cc6a89670d5 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:31:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 230 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 36550 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43900.6191 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 230, 8 O'clock: Ring (Segmental Concrete) Damage Affecting Single Ring. |  |  |  | Grout Delamination / debonding at segment bolted joints. |  | Grout Delamination / debonding at segment bolted joints. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 2b9b9aed-b0ae-44b8-93e2-bdc591964779,ccf919b7-e6f3-4860-b4a4-07ab2a71e38d | , | https://web.fulcrumapp.com/photos/view?photos=2b9b9aed-b0ae-44b8-93e2-bdc591964779%2Cccf919b7-e6f3-4860-b4a4-07ab2a71e38d | Concrete |  | Drummy
252d7fde-f508-4419-ad12-66704d578590 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:35:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 230 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27447 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 230,3 O'Clock,Stringer,Identified in 2018 |  |  |  | Conveyor frame and guard,Class 4 - Medium high corrosion |  | Conveyor frame and guard,Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | This is not a structural defect |  |  |  | yes | Suggest delete this non-structural defect | 66bafead-6ce8-4497-9f2e-45cba8086557 |  | https://web.fulcrumapp.com/photos/view?photos=66bafead-6ce8-4497-9f2e-45cba8086557 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
ffc2847b-7bd7-4ade-9df4-fc2cc1462c5e | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:37:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 232 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36554 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43900.641 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 232, 2 & 3 O'clock, Channel Anchor Bolts |  |  |  | Level 1 corrosion at anchor bolts of side wall channel. |  | Level 1 corrosion at anchor bolts of side wall channel. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This is not a significant defect |  |  |  | yes | Consider deleting this unnecessary defect | 3f7435d6-3ed4-4377-ac15-6840a579f59c,523c7b7a-262c-46e7-a35f-cf63f15976cd | , | https://web.fulcrumapp.com/photos/view?photos=3f7435d6-3ed4-4377-ac15-6840a579f59c%2C523c7b7a-262c-46e7-a35f-cf63f15976cd | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
15061875-6f57-4781-a1cb-44cb620980a2 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:36:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 232 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36553 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 232, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | b545c941-06ad-4ec8-aa12-fe1fbb6f66fe,c6b1b009-7cca-41e8-aab1-db747d61a2f1,b1c78fb4-15e2-4a91-8ce7-8633984a1d01 | ,, | https://web.fulcrumapp.com/photos/view?photos=b545c941-06ad-4ec8-aa12-fe1fbb6f66fe%2Cc6b1b009-7cca-41e8-aab1-db747d61a2f1%2Cb1c78fb4-15e2-4a91-8ce7-8633984a1d01 | Concrete | Grout Hole | Leaks |  | Not reinforcement
6adb804a-c323-4222-968a-4aaa9e7a718b | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:34:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 232 | 8 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27448 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 232, 8 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [7 empty] | no | yes |  | no |  | 7d92e2d7-2646-4e89-8ba1-65f697d469f3,69e29ffe-29db-4534-ad39-1d7106f80424 | , | https://web.fulcrumapp.com/photos/view?photos=7d92e2d7-2646-4e89-8ba1-65f697d469f3%2C69e29ffe-29db-4534-ad39-1d7106f80424 | Steel | Channel Bracket-Bolt,Walkway Support | Corrosion-Heavy,Corrosion-Surface
eb00acc4-ea08-469b-bd53-9512eff3fdfc | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 23:06:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 233 | 1 | Grout Injection Hole | Grout Injection Hole |  | 76353 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 233, 1 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | No | - | - | Condition Monitoring Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 4f0e812d-2637-4a1b-8a07-6b98c2566a94,95ab70eb-e49c-4d78-9741-5ad690b09342 | , | https://web.fulcrumapp.com/photos/view?photos=4f0e812d-2637-4a1b-8a07-6b98c2566a94%2C95ab70eb-e49c-4d78-9741-5ad690b09342 | Concrete | Grout Hole | Leaks
6d200c7e-a667-4a93-9e30-2afa25cad3f9 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:40:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 233 | 7 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88600 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4566 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 233, 7 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 75mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 75mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | no |  | f0634912-9424-45cf-87f2-f4519ea6d0d7,1fefd952-782e-4093-b1a4-395d8d55eabb | , | https://web.fulcrumapp.com/photos/view?photos=f0634912-9424-45cf-87f2-f4519ea6d0d7%2C1fefd952-782e-4093-b1a4-395d8d55eabb | Concrete | Circular Joint | Drummy
756786e2-e435-4b21-b969-e30811bdcedc | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:42:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 234 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 101836 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 45554.4769 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 234, 9 O' Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 7d1685a5-3a52-495a-8d02-828f2bd7695f,6adf9a58-2294-4782-830e-8527648250aa | , | https://web.fulcrumapp.com/photos/view?photos=7d1685a5-3a52-495a-8d02-828f2bd7695f%2C6adf9a58-2294-4782-830e-8527648250aa | Concrete | Circular Joint | Drummy
a2c5f2fc-5b20-4745-8a0d-2e7281dbb301 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:42:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 234 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36556 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 234, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | b69634bc-59b2-4083-8e0c-37eb2c2845f3,37c2db10-6c09-4cc3-bee0-07c172aa13f9,dd84c4d3-c64f-4663-8568-8cbee0276336 | ,, | https://web.fulcrumapp.com/photos/view?photos=b69634bc-59b2-4083-8e0c-37eb2c2845f3%2C37c2db10-6c09-4cc3-bee0-07c172aa13f9%2Cdd84c4d3-c64f-4663-8568-8cbee0276336 | Concrete | Grout Hole | Leaks |  | Not reinforcement
16cd2f17-71eb-4aa3-9d4d-14f310780cd4 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 23:01:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 234 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 36555 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43900.6437 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring: 234, 9 O'clock: Segment Bolted Joint (Circle Joint). |  |  |  | Grout Delamination / debonding at segment bolted joints. |  | Grout Delamination / debonding at segment bolted joints. | Movement of shell rings about joint resulting in leak |  | Movement of shell rings about joint resulting in leak |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | d74455ba-f042-4be3-87e5-854fd9282a3b,c48751d8-d5e5-4abf-b9d0-ecbf96ed531d | , | https://web.fulcrumapp.com/photos/view?photos=d74455ba-f042-4be3-87e5-854fd9282a3b%2Cc48751d8-d5e5-4abf-b9d0-ecbf96ed531d | Concrete | Circular Joint | Drummy
50b8f73f-9926-4321-8f1f-f7e4c18bdab4 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 23:00:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 235 | 10 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 88601 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4579 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 235, 10 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 7f5d98cd-720c-4b07-b5ce-b2c2eb48c67f,297be487-d9d8-4c93-ae81-ba6d5364212a | , | https://web.fulcrumapp.com/photos/view?photos=7f5d98cd-720c-4b07-b5ce-b2c2eb48c67f%2C297be487-d9d8-4c93-ae81-ba6d5364212a | Concrete | Radial Joint | Drummy
e0b0198e-766f-4d18-8b06-a32ba8898b19 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:40:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 236 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 76354 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.7529 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 236, 1 o'clock. Steel Channel Bracket and Anchor Bolts. |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion and Channel anchor bolts have Level 3 Medium Corrosion. |  | Steel channel support bracket has Level 2 Minor Corrosion and Channel anchor bolts have Level 3 Medium Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | On-Line |  |  |  |  | SS |  | No bracket at this location |  |  |  | yes | Delete this defect | 6c426fd2-8f85-40d4-a36a-9ecc65624957 |  | https://web.fulcrumapp.com/photos/view?photos=6c426fd2-8f85-40d4-a36a-9ecc65624957 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
700e50dd-8c66-466d-9cc4-b471541de9b6 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:58:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 236 | 12 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88603 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4605 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 236, 12 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 7dfdaae0-ee0c-4db3-87a4-a126746b5c7e,dc031b8b-ef4f-462d-bdfb-e3b0e5ce8337 | , | https://web.fulcrumapp.com/photos/view?photos=7dfdaae0-ee0c-4db3-87a4-a126746b5c7e%2Cdc031b8b-ef4f-462d-bdfb-e3b0e5ce8337 | Concrete | Circular Joint | Drummy
d7b50364-d0f8-49cc-9cf1-f025461964b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:41:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 236 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36557 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43900.646 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 236, 3 O'clock, Channel Anchor Bolts |  |  |  | Channel anchor bolt is missing at 3 o'clock. One anchor bolt is loose at 2 o'clock. |  | Channel anchor bolt is missing at 3 o'clock. One anchor bolt is loose at 2 o'clock. | Loss of bolt connection and failure of equipment support. |  | Loss of bolt connection and failure of equipment support. |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | be101c1a-5029-4754-ae9e-6b801f9780a5,f0123697-7138-4433-a3d3-d63e714a5543 | , | https://web.fulcrumapp.com/photos/view?photos=be101c1a-5029-4754-ae9e-6b801f9780a5%2Cf0123697-7138-4433-a3d3-d63e714a5543 | Steel | Channel Bracket-Bolt | Loose,Missing
e134bb39-7ab0-4c18-8629-d806ad3f18f5 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:48:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 236 | 7 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88602 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.459 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 236, 7 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 250mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 0c5acdde-5099-4e6c-938e-117f12f7061f,3027ce17-135a-4bc6-99d6-7b9b51e66301 | , | https://web.fulcrumapp.com/photos/view?photos=0c5acdde-5099-4e6c-938e-117f12f7061f%2C3027ce17-135a-4bc6-99d6-7b9b51e66301 | Concrete | Circular Joint | Drummy
94a51265-82a7-4d91-8590-6502783665d8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:44:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 236 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27209 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 236, 9 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak - Active at time of inspection. |  | Grout injection hole has leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding, Walkway | Hot Work, Excavation | Scheduled Maintenance Competent Supervisor | SS |  | No change, defect to be treated | no | yes |  | no |  | efa90917-c235-4cf9-b323-b8a94e3153d6,c9fdc995-9523-48e3-9c0e-7da09720998d,b9871870-96a4-4a8e-90b9-186c50c26528,7b7c2330-3c0f-4b09-bb38-62213beec020 | ,,, | https://web.fulcrumapp.com/photos/view?photos=efa90917-c235-4cf9-b323-b8a94e3153d6%2Cc9fdc995-9523-48e3-9c0e-7da09720998d%2Cb9871870-96a4-4a8e-90b9-186c50c26528%2C7b7c2330-3c0f-4b09-bb38-62213beec020 | Concrete | Grout Hole | Leaks |  | Not reinforcement
a54d7cb1-1d49-4be4-9973-946d892a0d6f | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:47:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 236 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27449 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 236,7 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | This defect is corrosion of the curver footing plate and bolts of the conveyor support. | no | no |  | yes | Suggest P3 and Cond 3 | 4ec8e0bd-95b8-49a8-a785-75dcb4d905a9,fad21df9-572e-49ad-b755-5942cd811b62,2217f642-97ae-4b41-9b11-483be4d3468d | ,, | https://web.fulcrumapp.com/photos/view?photos=4ec8e0bd-95b8-49a8-a785-75dcb4d905a9%2Cfad21df9-572e-49ad-b755-5942cd811b62%2C2217f642-97ae-4b41-9b11-483be4d3468d | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support
c2f4bae5-0cb5-4204-9f33-f24ee361f5bc | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:33:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 237 | 8 | Grout Injection Hole | Grout Injection Hole |  | 36558 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 237, 8 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - Active at time of inspection. |  | Grout injection hole has leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | f8cdc729-9127-417a-a2d9-b28979935e20,6923a151-569e-4c79-832d-06e2462dd3ef | , | https://web.fulcrumapp.com/photos/view?photos=f8cdc729-9127-417a-a2d9-b28979935e20%2C6923a151-569e-4c79-832d-06e2462dd3ef | Concrete | Grout Hole | Leaks |  | Not reinforcement
c92cc08a-d244-489f-88cb-07371a15d60b | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:42:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 238 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26918 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 238, 1 O'clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | No change, leak requires treatment | no | yes |  | no |  | 2f332b3b-0f57-4137-8cf1-8eaca4ac441b,03932a8d-9de7-4829-b9f7-08f88697847d,aded648d-9798-4c41-bfcc-2010b3a1a3a5,f195d859-821a-4949-b799-c926d65da328 | ,,, | https://web.fulcrumapp.com/photos/view?photos=2f332b3b-0f57-4137-8cf1-8eaca4ac441b%2C03932a8d-9de7-4829-b9f7-08f88697847d%2Caded648d-9798-4c41-bfcc-2010b3a1a3a5%2Cf195d859-821a-4949-b799-c926d65da328 | Concrete |  | Leaks |  | Not reinforcement
980ec971-d4c8-49f5-a95e-cbaa35fee434 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:44:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 238 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27146 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 238, 2 & 3 O'Clock, Channel Anchor Bolts |  |  |  | Steel channel support bracket has Level 1 Corrosion. Channel anchor bolts has Level 2 Corrosion |  | Steel channel support bracket has Level 1 Corrosion. Channel anchor bolts has Level 2 Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change. Leak above causing issue. | no | no |  | yes | Upgrade priority to P3 | f297de7a-8373-4ae7-b272-50b57e5cb77c,3f4e074b-a790-47d3-8c46-071fe2896c38,8691083d-c2e8-472e-9a5d-b6c5b32d9354 | ,, | https://web.fulcrumapp.com/photos/view?photos=f297de7a-8373-4ae7-b272-50b57e5cb77c%2C3f4e074b-a790-47d3-8c46-071fe2896c38%2C8691083d-c2e8-472e-9a5d-b6c5b32d9354 | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks
d762052e-6e86-428d-8622-677206de9a5b | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:46:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 238 | 2 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 101837 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 45554.4791 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 238, 2 O'Clock, Segment Bolted Joint (Radial Joint) |  |  |  | Crack on patch repair of radial joint up to 0.2mm in width. |  | Crack on patch repair of radial joint up to 0.2mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This shrinkage crack in grout patch is not a structural issue | no | yes |  | yes | Consider deleting this low priority defect | 5cf970f2-2e34-4707-94be-5e1cbae5cb03,03534102-9cf3-4c5a-9c51-01e997e0b9c9 | , | https://web.fulcrumapp.com/photos/view?photos=5cf970f2-2e34-4707-94be-5e1cbae5cb03%2C03534102-9cf3-4c5a-9c51-01e997e0b9c9 | Concrete | Radial Joint | Crack
b4c7831e-e651-4f77-a5f9-83449a688a2d | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:47:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 238 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76355 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.7574 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 238, 3 o'clock. Channel Anchor Bolts. |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion and Channel anchor bolts have Level 2 Medium Low Corrosion |  | Steel channel support bracket has Level 2 Minor Corrosion and Channel anchor bolts have Level 2 Medium Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | SS |  | This is a duplication of the defect at 2 o'clock | no | yes |  | yes | Consider deleting this duplicate defect |  |  |  | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface |  | Duplicate - Remove
248ba720-cc0b-4188-913d-deab070d8360 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:40:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 238 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 101838 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 19/09/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Unknown | Unknown |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 238, 7 O' Clock, Ring (Segmental Concrete) - Damage Affecting Single Ring | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 100mm x 300mm adjacent the circle joint. |  | Concrete shell segment has drummy concrete over an area of 100mm x 300mm adjacent the circle joint. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | yes | Priority and risk to be downgraded | 5f0428bf-3f9c-41c5-a3a9-da21b1f1fc3f,81df265b-fd89-49be-aa92-24f1a163e4aa | , | https://web.fulcrumapp.com/photos/view?photos=5f0428bf-3f9c-41c5-a3a9-da21b1f1fc3f%2C81df265b-fd89-49be-aa92-24f1a163e4aa | Concrete | Circular Joint | Drummy |  | Not reinforcement
cb3d4a17-f70a-4f9f-bd7d-06491793a466 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:48:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 238 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26919 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 238,1 O'clock, Steel Channel Bracket and Anchor Bolt | Rupture | Rupture |  | Steel channel support bracket has Level 3 Corrosion. Channel anchor bolts has Level 3 Corrosion |  | Steel channel support bracket has Level 3 Corrosion. Channel anchor bolts has Level 3 Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Financial | Priority: P3 |  |  |  | Replace damaged bolts one at a time as per original design specification. Remove corrosion by abrasive blasting or mechanical means and reinstate protective coatings in accordance with BHP specifications. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair Guideline 0136559. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor | SS |  | Caused by lrak, described in other defect. Treat at same time. | no | yes |  | no |  | bf7f3a66-11e8-49ed-8280-8658aa2c7987,17133cac-e5cd-492e-bc5d-d907cd9ed5f6,15834cc6-47af-4d5b-8796-ec10cb26b044,4e6e80cb-56e2-4e36-81dc-fdc00fbde3d0 | ,,, | https://web.fulcrumapp.com/photos/view?photos=bf7f3a66-11e8-49ed-8280-8658aa2c7987%2C17133cac-e5cd-492e-bc5d-d907cd9ed5f6%2C15834cc6-47af-4d5b-8796-ec10cb26b044%2C4e6e80cb-56e2-4e36-81dc-fdc00fbde3d0 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
07bcca18-294e-4fb8-a094-c1e06be4e229 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:42:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 240 | 0 | Grout Injection Hole | Grout Injection Hole |  | 36559 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 240, 9 to 11 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | It seems that this defect has been discussed with BHP AIMS to define the consequence and priority level. Requires treatment. | no | yes |  | no |  | 8bebc86a-9838-4653-881d-87e533eed31d,a191e094-d7f7-4990-a69e-e0e98314d15a,d4f1213f-0c7f-43e1-a5bd-d2aa48bbb8c4 | ,, | https://web.fulcrumapp.com/photos/view?photos=8bebc86a-9838-4653-881d-87e533eed31d%2Ca191e094-d7f7-4990-a69e-e0e98314d15a%2Cd4f1213f-0c7f-43e1-a5bd-d2aa48bbb8c4 | Concrete | Grout Hole | Leaks |  | Not reinforcement
3617bc9e-e5fe-40aa-a6c6-dbf6bde1f9df | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:42:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 240 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27450 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 240,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [7 empty] | no | yes |  | no |  | 80a41aaf-3302-46f5-a1a3-7a456553b518,281238b1-8a58-4ea0-8e98-3e4ae84f0527,ea7ec02a-7d79-4efb-9d4a-34be517002b8 | ,, | https://web.fulcrumapp.com/photos/view?photos=80a41aaf-3302-46f5-a1a3-7a456553b518%2C281238b1-8a58-4ea0-8e98-3e4ae84f0527%2Cea7ec02a-7d79-4efb-9d4a-34be517002b8 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
1415538f-2a98-4187-b307-3be033015698 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 6 |  |  |  | 2025-07-26 23:16:32 AEST | 2025-07-26 23:24:17 AEST | 30011704-user5@smec.com | james.stone@smec.com | 230 | 12 |  |  | Pipes, rollers and other mech components | [15 empty] | Corrosion due to water spray | 4 | [9 empty] | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Pipes and roller brackets near the spray point |  |  | Pipe or roller failure |  |  | Water spray is degrading all the metal components it reaches |  |  | Loss of services, failure of conveyor | [15 empty] | SS |  | While not explicitly a structural issue, this does affect the conveyor and associated pipework. |  | no |  | yes | Fill blank fields | fc799f51-e6ee-4154-92b0-461f0f1c11b6,4c8c245d-bbc2-4e1b-9cc9-95844e58ae7e,c018b897-3362-4633-9dbc-cd7e8112b3b5,30511d5c-ce7f-4120-aae8-1059814490aa,547b85c0-28fe-48d7-8740-02ad04844dbc,d9e7350a-f787-40ed-8476-69ef2f93d569,8d755b4c-3272-47a3-b958-5e22937ac40c,7db40efa-2081-47d9-9ec3-16d1c99cc5b7,c5e1bdec-9654-4a58-852e-cb5c12aa6630 | ,,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=fc799f51-e6ee-4154-92b0-461f0f1c11b6%2C4c8c245d-bbc2-4e1b-9cc9-95844e58ae7e%2Cc018b897-3362-4633-9dbc-cd7e8112b3b5%2C30511d5c-ce7f-4120-aae8-1059814490aa%2C547b85c0-28fe-48d7-8740-02ad04844dbc%2Cd9e7350a-f787-40ed-8476-69ef2f93d569%2C8d755b4c-3272-47a3-b958-5e22937ac40c%2C7db40efa-2081-47d9-9ec3-16d1c99cc5b7%2Cc5e1bdec-9654-4a58-852e-cb5c12aa6630 | Steel | Misc (Pipes/Cable Tray/etc)
17cd75ea-6dfe-4b79-8c07-da7245e0e89c | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 6 |  |  |  | 2025-07-27 01:31:10 AEST | 2025-07-27 01:31:50 AEST | 30011704-user5@smec.com | james.stone@smec.com | 223 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68896 |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 17/05/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 223, 1 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | Leak still inactive | no | yes |  | no |  | f16a5c29-558a-4699-b145-c5b7b25d3323,eab14e8c-d582-4dc4-86e6-f50fd08fcca4 | , | https://web.fulcrumapp.com/photos/view?photos=f16a5c29-558a-4699-b145-c5b7b25d3323%2Ceab14e8c-d582-4dc4-86e6-f50fd08fcca4 | Concrete | Grout Hole | Leaks |  | Not reinforcement
5db16e24-0cfb-497b-83ab-05f3515ac8f8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 6 |  |  |  | 2025-07-27 03:24:06 AEST | 2025-07-27 05:36:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | 227 | 7 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88598 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.453 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 229, 7 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 1461d16b-d7f5-40b3-bf98-d096e5957c59,8be2038d-95c8-4d8a-80e8-9fbe077f6ddc | , | https://web.fulcrumapp.com/photos/view?photos=1461d16b-d7f5-40b3-bf98-d096e5957c59%2C8be2038d-95c8-4d8a-80e8-9fbe077f6ddc | Concrete | Circular Joint | Drummy
7027d9bd-3298-46d4-8a7d-84c82b24877f | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 6 |  |  |  | 2025-07-27 03:28:55 AEST | 2025-07-27 05:36:45 AEST | 30011704-user5@smec.com | james.stone@smec.com | 229 | 7 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88598 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.453 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 229, 7 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | b9c3f3c9-aa20-4814-b61f-5fb63c582f7a,a678f86a-e273-4903-bac3-b50fab08c023 | , | https://web.fulcrumapp.com/photos/view?photos=b9c3f3c9-aa20-4814-b61f-5fb63c582f7a%2Ca678f86a-e273-4903-bac3-b50fab08c023 | Concrete | Circular Joint | Drummy
a04e54e7-a024-4da2-9b18-bdc704267b57 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 6 |  |  |  | 2025-07-27 03:34:35 AEST | 2025-07-27 05:36:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 232 | 7 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88598 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.453 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 229, 7 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | a2be7122-d394-4d27-bd55-1f1a6d59082a,f8102ca0-525f-45cb-8a81-9297571a1585 | , | https://web.fulcrumapp.com/photos/view?photos=a2be7122-d394-4d27-bd55-1f1a6d59082a%2Cf8102ca0-525f-45cb-8a81-9297571a1585 | Concrete | Circular Joint | Drummy
feb40add-b527-422a-a600-29d9b887b491 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 6 | -20.3216 | 118.5853 | POINT (118.5852986 -20.3215972) | 2025-07-27 03:40:14 AEST | 2025-07-27 03:40:44 AEST | 30011704-user5@smec.com | james.stone@smec.com | 234 | 7 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88600 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4566 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 233, 7 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 75mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 75mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | no |  | no |  | 93beae16-4e76-4353-9ce1-6bb5f18ed8fa,cbaade8e-31fb-48f6-8d60-3182d639f3ac | , | https://web.fulcrumapp.com/photos/view?photos=93beae16-4e76-4353-9ce1-6bb5f18ed8fa%2Ccbaade8e-31fb-48f6-8d60-3182d639f3ac | Concrete | Circular Joint | Drummy
a0a30f49-9ccb-44b6-9907-1d798840f6ae | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 6 |  |  |  | 2025-07-27 05:34:58 AEST | 2025-07-27 05:37:12 AEST | 30011704-user5@smec.com | james.stone@smec.com | 237 | 7 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88598 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.453 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 229, 7 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 6906e034-9233-4c02-b03b-be27b2da4b4d,bf48aec5-0b0f-4147-80d0-453e83e6ff78 | , | https://web.fulcrumapp.com/photos/view?photos=6906e034-9233-4c02-b03b-be27b2da4b4d%2Cbf48aec5-0b0f-4147-80d0-453e83e6ff78 | Concrete | Circular Joint | Drummy
9c860d07-d014-4de6-bdd1-fa4226463efa | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:38:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 242 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27148 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 242, 1 O'clock, Channel Anchor Bolts |  |  |  | Channel anchor bolts have level 1 corrosion. |  | Channel anchor bolts have level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Mild corrosion There is also a level 2 corrosion defect at this location, suspect a duplication. Suggest deleting one. | no | yes |  | yes | Check if one of these defects can be deleted | 984f02ee-2a1c-4ff8-890e-c8700b04a257,d89bc050-6530-4232-9137-da6a7fdd02d8 | , | https://web.fulcrumapp.com/photos/view?photos=984f02ee-2a1c-4ff8-890e-c8700b04a257%2Cd89bc050-6530-4232-9137-da6a7fdd02d8 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
6b75541f-5c11-41a4-a82c-738cb43321b0 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:39:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 242 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76357 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.79 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 242, 1 o'clock. Channel Anchor Bolts. |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | SS |  | There is also a level 1 corrosion defect at this location, suspect a duplication. Suggest deleting one. | no | yes |  | yes | Check if one of these defects can be deleted | ba3b093a-cb07-49d2-b5a9-b28dac953977,c9d8d3a0-698c-4a84-ad26-97ee06622b37 | , | https://web.fulcrumapp.com/photos/view?photos=ba3b093a-cb07-49d2-b5a9-b28dac953977%2Cc9d8d3a0-698c-4a84-ad26-97ee06622b37 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
cf466339-5938-4d6d-9f46-05343dc38d57 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:32:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 242 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 88604 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4635 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 242, 11 O'Clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is missing. |  | One channel anchor bolt is missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Bolt still missing. This is low priority. | no | yes |  | no |  | e28821b2-90f7-4417-b884-a1b09462d85f,4d470387-57b6-487e-87ce-2459b9f8c2c1 | , | https://web.fulcrumapp.com/photos/view?photos=e28821b2-90f7-4417-b884-a1b09462d85f%2C4d470387-57b6-487e-87ce-2459b9f8c2c1 | Steel | Channel Bracket-Bolt | Missing
167827f5-1c66-418c-8bf7-e32049682a23 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 21:49:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 242 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76356 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.7594 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 242, 3 O'Clock, Channel Anchor Bolts |  |  |  | Nut is missing from one channel anchor bolt. |  | Nut is missing from one channel anchor bolt. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Changed to 3 o'clock | no | yes |  | no |  | 9aba1133-461e-4fdd-9fd8-a9624911dd18,cd54aeef-07dd-4cb8-8f4e-a95c4ccb4ef0 | , | https://web.fulcrumapp.com/photos/view?photos=9aba1133-461e-4fdd-9fd8-a9624911dd18%2Ccd54aeef-07dd-4cb8-8f4e-a95c4ccb4ef0 | Steel | Channel Bracket-Bolt | Missing
a7ef5a19-1678-4ead-865e-b4541fa3fc45 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 21:50:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 244 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76358 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.7916 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 244, 2 o'clock. Channel Anchor Bolts. |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | SS |  | Changed to 2 o'clock | no | yes |  | no |  | 962afe5a-9c44-43e6-aaae-bf92e314433c,b012a30f-6f5e-4ad0-a812-c24e87270ab7 | , | https://web.fulcrumapp.com/photos/view?photos=962afe5a-9c44-43e6-aaae-bf92e314433c%2Cb012a30f-6f5e-4ad0-a812-c24e87270ab7 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
655fcb71-a4d4-4e86-ae6d-d4bd9079fbd1 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 21:51:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 244 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76359 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.7931 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 244, 3 O'Clock, Channel Anchor Bolts |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Changed to 3 o'clock | no | yes |  | no |  | 4e29e096-c8eb-4815-89a0-a17a81bdcf5a,07636456-22de-4097-9332-157374290e78 | , | https://web.fulcrumapp.com/photos/view?photos=4e29e096-c8eb-4815-89a0-a17a81bdcf5a%2C07636456-22de-4097-9332-157374290e78 | Steel | Channel Bracket-Bolt | Loose
eca47605-a7d0-40df-985e-2b7d66885717 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:49:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 244 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27451 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 244,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  |  | no | yes |  | no |  | 83bbcd8d-ff33-4c4a-baa1-ca846d88a59c,497dc05a-e619-4e6f-b3a6-13eed9f47704,c3277a55-e4d1-4a44-bb6f-58cebb09b3e0,2f5528ff-85be-4362-9e5f-6a3a6372b0c5 | ,,, | https://web.fulcrumapp.com/photos/view?photos=83bbcd8d-ff33-4c4a-baa1-ca846d88a59c%2C497dc05a-e619-4e6f-b3a6-13eed9f47704%2Cc3277a55-e4d1-4a44-bb6f-58cebb09b3e0%2C2f5528ff-85be-4362-9e5f-6a3a6372b0c5 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
01f41195-7315-4d01-958c-5a1bff8d301f | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 21:54:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 245 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 88605 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4652 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 245, 2 O'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings |  |  |  | Concrete shell segment has Cracking appear to be shrinkage cracks less than 0.3mm. |  | Concrete shell segment has Cracking appear to be shrinkage cracks less than 0.3mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | These minor surface cracks are not considered a structural issue. | no | yes |  | no |  | dceddefa-dda1-4e0d-a3bd-485df490cbec,6c6b123b-54b5-41bc-8b11-00d05b10f225 | , | https://web.fulcrumapp.com/photos/view?photos=dceddefa-dda1-4e0d-a3bd-485df490cbec%2C6c6b123b-54b5-41bc-8b11-00d05b10f225 | Concrete | Grout Hole | Crack |  | Grout Hole
3af08b19-4f25-43b4-844b-e9709027f4eb | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 21:56:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 246 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27452 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 246, 1 O'Clock, Channel Anchor Bolts |  |  |  | Channel anchor of bolts have level 2 corrosion. |  | Channel anchor of bolts have level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Corrosion is noted | no | yes |  | no |  | 38614f9c-41f2-45f5-aa0d-19e9bc21539c,cb56a9f3-69d6-49b1-8dac-91604b61c86d,4689ec45-c59d-4266-806d-65df38b779a0,db65ebf4-e2ca-4cbe-9b7a-10424f35aad3 | ,,, | https://web.fulcrumapp.com/photos/view?photos=38614f9c-41f2-45f5-aa0d-19e9bc21539c%2Ccb56a9f3-69d6-49b1-8dac-91604b61c86d%2C4689ec45-c59d-4266-806d-65df38b779a0%2Cdb65ebf4-e2ca-4cbe-9b7a-10424f35aad3 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
ddd59730-7cfd-42ef-a82f-79b42fa38d20 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:23:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 246 | 11 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88606 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4686 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 246, 11 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 09ab0b22-a9b1-4a03-a5b7-8fd26e7f76e1,1a3f429f-9c6a-4ae4-9e84-fdd12664a800 | , | https://web.fulcrumapp.com/photos/view?photos=09ab0b22-a9b1-4a03-a5b7-8fd26e7f76e1%2C1a3f429f-9c6a-4ae4-9e84-fdd12664a800 | Concrete | Circular Joint | Drummy
f6e56e66-82ea-4d45-a22a-8978c4604368 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 21:58:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 246 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76360 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.7944 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 246, 2 O'Clock, Channel Anchor Bolts |  |  |  | Channel anchor bolt is short with insufficent thread projection past the nut. |  | Channel anchor bolt is short with insufficent thread projection past the nut. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 6817d84e-f214-4e89-ab52-3122832ec6e5,f916d86b-7822-40b4-8c68-9e059645f928 | , | https://web.fulcrumapp.com/photos/view?photos=6817d84e-f214-4e89-ab52-3122832ec6e5%2Cf916d86b-7822-40b4-8c68-9e059645f928 | Steel | Channel Bracket-Bolt
618ea383-ec70-4934-8440-6b9cb143d9c0 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:52:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 248 | 8 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36562 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43900.6503 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 248, 8 O'clock: Loose / missing nuts or bolts - Corrosion is minimal. |  |  |  | Loose conveyor anchor bolt. |  | Loose conveyor anchor bolt. | Loss of bolt connection and failure of equipment support. |  | Loss of bolt connection and failure of equipment support. |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | One missing, one loose | no | yes |  | no |  | ff8382e4-d7a1-40a0-9a0c-ea378f74bbaa,cd3b47ff-973a-4ed1-9d9a-6e4cae713139,c41ea39f-3fd1-4e2b-a717-f1cf744b3ab8 | ,, | https://web.fulcrumapp.com/photos/view?photos=ff8382e4-d7a1-40a0-9a0c-ea378f74bbaa%2Ccd3b47ff-973a-4ed1-9d9a-6e4cae713139%2Cc41ea39f-3fd1-4e2b-a717-f1cf744b3ab8 | Steel | Channel Bracket-Bolt | Loose,Missing
71ccb188-16f0-496f-9fac-a5f4763a9fad | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:14:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 248 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27453 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 248,7 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | No close access | no | yes |  | no |  | 93b64c34-c1f4-459e-b146-0a2cc0742958,c06c3820-24ac-42b3-964a-ade2bc076f01,176674d4-cfe6-4aa7-a058-a06acaee8fb4 | ,, | https://web.fulcrumapp.com/photos/view?photos=93b64c34-c1f4-459e-b146-0a2cc0742958%2Cc06c3820-24ac-42b3-964a-ade2bc076f01%2C176674d4-cfe6-4aa7-a058-a06acaee8fb4 | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support
69c3f624-cf37-474c-ae41-5441f017061c | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:01:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 249 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36563 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 249, 2 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | a07371c2-e127-48b8-8a98-75f83253997d,c3d5e7b3-d8c0-41c2-84ca-43c6b06c1c4b | , | https://web.fulcrumapp.com/photos/view?photos=a07371c2-e127-48b8-8a98-75f83253997d%2Cc3d5e7b3-d8c0-41c2-84ca-43c6b06c1c4b | Concrete | Grout Hole | Leaks |  | Not Reinforcement
df0bed4d-72a9-4328-83db-d8f571075bd9 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:02:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 250 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 88607 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4697 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 250, 1 & 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support have Level 2 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support have Level 2 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 71b520f4-7edf-4b59-9515-7e593f1d16c9,cc430494-8c6a-44ac-9b17-2db723c2a343,93998521-9246-4237-b7ff-5e3ef2b5e613,95cbde84-902b-4674-9cd6-58203e609052,e3b253db-e5b2-4f2f-9cf4-3c5433b56518 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=71b520f4-7edf-4b59-9515-7e593f1d16c9%2Ccc430494-8c6a-44ac-9b17-2db723c2a343%2C93998521-9246-4237-b7ff-5e3ef2b5e613%2C95cbde84-902b-4674-9cd6-58203e609052%2Ce3b253db-e5b2-4f2f-9cf4-3c5433b56518 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
4e84d3ba-a99d-46fe-abb4-8c306d18a8a3 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:17:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 250 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36564 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 250, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Leak is inactive | yes | yes |  | yes | Reduce condition to 3 | 471273b1-9ae5-4845-92f1-b98e831b3e98,27275457-dead-4ffd-b18a-2f7ff4293a5d,75b9ddfe-cfb5-4df9-b1f9-2e38e1eab4be,79224409-e4de-4604-92d9-7abf4adea341 | ,,, | https://web.fulcrumapp.com/photos/view?photos=471273b1-9ae5-4845-92f1-b98e831b3e98%2C27275457-dead-4ffd-b18a-2f7ff4293a5d%2C75b9ddfe-cfb5-4df9-b1f9-2e38e1eab4be%2C79224409-e4de-4604-92d9-7abf4adea341 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
8faf8f48-8505-47db-960d-f4d905bc1492 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:25:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 251 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27208 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 251, 1 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak - Active at time of inspection. |  | Grout injection hole has leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | No change. Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 9fc87f08-4351-4d1f-b304-6d15129f629c,e5fc0dad-eb41-4f7f-90c4-d8d3978bbeb7,b61030aa-00ae-4093-bd88-d1c49cebc605 | ,, | https://web.fulcrumapp.com/photos/view?photos=9fc87f08-4351-4d1f-b304-6d15129f629c%2Ce5fc0dad-eb41-4f7f-90c4-d8d3978bbeb7%2Cb61030aa-00ae-4093-bd88-d1c49cebc605 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
409a4c4e-2876-4c85-9427-8fabec177a79 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:26:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 251 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26922 |  | 8517 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 25/01/2023 |  | 17/10/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring: 251, 12 O'clock: Grout Injection Hole. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. Duplicate of defect 27208. Marked as repair verified to manage duplicate defects LC 9/10/24 | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Engineering Repair Methodology Required Competent Engineer | [6 empty] | yes | This is a duplicate of the grout injection hole defect at 1 o'clock. Suggest delete. |  |  |  | Concrete | Grout Hole,Reinforcement | Leaks
e305bccb-5a49-4398-b39b-91105db42fc7 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:16:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 252 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36569 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 252, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 17e761a9-0223-47a5-a6f3-f3d886047add,0c4f37e8-6f35-4502-975c-562b6eca1885 | , | https://web.fulcrumapp.com/photos/view?photos=17e761a9-0223-47a5-a6f3-f3d886047add%2C0c4f37e8-6f35-4502-975c-562b6eca1885 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
73ef0c9b-fcff-4c79-a7bc-600557f3f637 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:17:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 252 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76361 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.7971 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 252, 3 O'Clock, Channel Anchor Bolts. |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Minor | no | yes |  | no |  | 73d84000-f6c3-4c08-a2bd-bffe6cd1bad6,1bddcc10-7632-4b83-9e3f-add06f7d947e | , | https://web.fulcrumapp.com/photos/view?photos=73d84000-f6c3-4c08-a2bd-bffe6cd1bad6%2C1bddcc10-7632-4b83-9e3f-add06f7d947e | Steel | Channel Bracket-Bolt | Loose
11cbbde1-7d4e-476a-ab4d-e949e6f8339f | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:24:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 252 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36567 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 252, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 8a8810a2-f00a-43f1-a1a1-d757bcf6ef0b,9aebc5a9-572e-4ee8-a7ad-fa90a5a70df3,b5ec1712-cd72-411a-adc9-47ddb2fa0f7a | ,, | https://web.fulcrumapp.com/photos/view?photos=8a8810a2-f00a-43f1-a1a1-d757bcf6ef0b%2C9aebc5a9-572e-4ee8-a7ad-fa90a5a70df3%2Cb5ec1712-cd72-411a-adc9-47ddb2fa0f7a | Concrete | Grout Hole | Leaks |  | Not Reinforcement
103e7623-43eb-486a-99c2-aeb1dfd5f9f1 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:13:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 252 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27454 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 252,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | No close access | no | yes |  | no |  | 4c9cf11c-b796-4930-8b02-0e0ef1521cc2,5dd1cb86-34f1-4840-9767-0ff297e09ccd | , | https://web.fulcrumapp.com/photos/view?photos=4c9cf11c-b796-4930-8b02-0e0ef1521cc2%2C5dd1cb86-34f1-4840-9767-0ff297e09ccd | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
10978bbb-206f-44a8-b9a6-690cd51fdf37 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:19:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 253 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 26923 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Almost Certain (Failure within 1 year) |  | Almost Certain (Failure within 1 year) | Ring 253, 2 O'Clock, Cable Tray |  |  |  | Cable tray has Level 4 corrosion. |  | Cable tray has Level 4 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 3 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | yes | Suggest update priority and risk to low. | 6542efdb-6cbe-4132-8adc-7cc76f562702,44ae40f8-88d6-4f0f-aa98-8ab6683ccf3a | , | https://web.fulcrumapp.com/photos/view?photos=6542efdb-6cbe-4132-8adc-7cc76f562702%2C44ae40f8-88d6-4f0f-aa98-8ab6683ccf3a | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
f33834dc-3dfe-4b6b-aa70-f2735395bdc0 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:20:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 253 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36570 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 253, 2 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No change | no | yes |  | no |  | 59ecd503-e5a6-415d-a069-f3be4de1e9a0,f5242f12-ab1d-4d4a-8fea-b155a639e4db,9d5d99c0-0136-4b7d-95b8-450e58ec473c | ,, | https://web.fulcrumapp.com/photos/view?photos=59ecd503-e5a6-415d-a069-f3be4de1e9a0%2Cf5242f12-ab1d-4d4a-8fea-b155a639e4db%2C9d5d99c0-0136-4b7d-95b8-450e58ec473c | Concrete | Grout Hole | Leaks |  | Not Reinforcement
18b3d8e0-af5b-452d-8135-8381914ed814 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:23:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 253 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 27149 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 253,2 O'clock,Support Bracket,New Defect 2017 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | There is no bracket at this location. Suggest delete this defect. | no | no |  | yes | There is no bracket at this location. Suggest delete this defect. | ef033478-a702-4b5d-a2dc-c26da66bf360 |  | https://web.fulcrumapp.com/photos/view?photos=ef033478-a702-4b5d-a2dc-c26da66bf360 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
9f17639c-be4b-4ec1-b01a-d6d67b83e0a6 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:26:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 254 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76362 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.7997 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 254, 3 O'Clock, Channel Anchor Bolts. |  |  |  | Nut missing at one channel anchor bolt |  | Nut missing at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 54c1cdf5-1f7f-4fdc-ba5b-c49a00ad9d67,01503858-34eb-494a-bf64-b6208c373a36 | , | https://web.fulcrumapp.com/photos/view?photos=54c1cdf5-1f7f-4fdc-ba5b-c49a00ad9d67%2C01503858-34eb-494a-bf64-b6208c373a36 | Steel | Channel Bracket-Bolt | Missing
bc85619e-240a-430c-9af2-f86b0fea7fd9 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:25:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 254 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36571 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 254, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | no |  | yes | Downgrade priority to P3 | 7a3747fe-5eaa-4240-a6da-94be3f6d9f53,f7e8cffb-7cb4-46a5-8f26-80699660dda2,b1b5a0de-e345-4660-aacf-f3e03f884ab6 | ,, | https://web.fulcrumapp.com/photos/view?photos=7a3747fe-5eaa-4240-a6da-94be3f6d9f53%2Cf7e8cffb-7cb4-46a5-8f26-80699660dda2%2Cb1b5a0de-e345-4660-aacf-f3e03f884ab6 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
57140360-22ce-4bb7-bab1-d203ca59643a | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:07:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 255 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 88608 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 255, 12 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 350mm x 150mm. |  | Concrete shell segment has drummy concrete over an area of 350mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | This is a duplicate of a defect on 10 o'clock |  |  |  | yes | This is a duplicate of a defect on 10 o'clock . Suggest delete this one |  |  |  | Concrete |  | Drummy
3a2cc4f2-7861-4221-90e4-c92ef9f18ad1 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:32:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 255 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36572 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 255, 2 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No change | no | yes |  | no |  | 75362b22-ad93-4b9c-b58c-1668c70453fe,aa7a1afd-37d9-4756-a072-a4503da6e63e | , | https://web.fulcrumapp.com/photos/view?photos=75362b22-ad93-4b9c-b58c-1668c70453fe%2Caa7a1afd-37d9-4756-a072-a4503da6e63e | Concrete | Grout Hole | Leaks |  | Not Reinforcement
35d09041-d1a2-47f5-93d0-793b33f07590 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:36:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 256 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36574 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 256, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | This appears to be a duplicate. |  |  |  | yes | This appears to be a duplicate. Suggest deleting this one and keeping the other. No pics taken. |  |  |  | Concrete | Grout Hole,Reinforcement | Leaks
0944d654-dcde-4307-9453-abfc530c3644 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:35:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 256 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26924 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 256, 12 O'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No change | no | yes |  | yes | This appears to be a duplicate. Suggest keeping this one and deleting the other | 8743ac15-faf3-40cb-b2f5-4a20886ef8e4,db308a49-0a89-461d-8a44-847d5f77f661 | , | https://web.fulcrumapp.com/photos/view?photos=8743ac15-faf3-40cb-b2f5-4a20886ef8e4%2Cdb308a49-0a89-461d-8a44-847d5f77f661 | Concrete | Grout Hole,Reinforcement | Leaks
0d15539c-363f-4c4e-95d1-7fae08950c94 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:32:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 256 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36573 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 256, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No change Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 5b1c7faa-71ad-458a-a937-52bd42528f18,536137ed-370d-4370-8de7-2d516595ab28,0720f0da-f3a2-413a-93bf-0a47ad62fd7b | ,, | https://web.fulcrumapp.com/photos/view?photos=5b1c7faa-71ad-458a-a937-52bd42528f18%2C536137ed-370d-4370-8de7-2d516595ab28%2C0720f0da-f3a2-413a-93bf-0a47ad62fd7b | Concrete | Grout Hole | Leaks |  | Not Reinforcement
32d2cd4f-f50e-4d04-b3c3-bcea633c0e74 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:34:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 256 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27455 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 256,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | Typical corrosion for these brackets | no | yes |  | no |  | 22ebf617-018a-4040-a239-c716b44b6cd5,9ed16d22-863f-41a8-971c-c5a9b9ace31b | , | https://web.fulcrumapp.com/photos/view?photos=22ebf617-018a-4040-a239-c716b44b6cd5%2C9ed16d22-863f-41a8-971c-c5a9b9ace31b | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
5f1acd7f-d268-4657-97eb-b5455b771081 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:38:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 257 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36575 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 257, 2 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 3a84c15b-d332-455a-9061-c1c3304c3cba,5e500e18-f8c0-4af1-8e91-7d4d9c77f401,33f79bff-3c47-4c69-963f-a8839e348e07 | ,, | https://web.fulcrumapp.com/photos/view?photos=3a84c15b-d332-455a-9061-c1c3304c3cba%2C5e500e18-f8c0-4af1-8e91-7d4d9c77f401%2C33f79bff-3c47-4c69-963f-a8839e348e07 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
219ff816-2d4b-43a4-8f60-118b0e50bc89 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:39:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 262 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36576 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 262, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Does not appear active Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 702e1a79-0d23-4cf0-85ea-19767289ceb4,423dd4db-1506-450d-82c3-5e9761a49ad4,2008b203-1f14-4e94-8fb6-cadcfe2cc011 | ,, | https://web.fulcrumapp.com/photos/view?photos=702e1a79-0d23-4cf0-85ea-19767289ceb4%2C423dd4db-1506-450d-82c3-5e9761a49ad4%2C2008b203-1f14-4e94-8fb6-cadcfe2cc011 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
392f5f41-0fa9-4039-9bd4-5650a8d14037 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:42:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 258 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 88609 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4772 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 258, 1 & 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support have Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support have Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 2e0a0073-e129-42e2-9ac5-d7c733b2a3af,bda8d309-7277-4a04-a191-f6ec3db16a7b,0c7843ba-9f2e-4e73-bb0e-338c8d013839,a49f32e4-15dc-4e89-9855-e78efb7d9ac3 | ,,, | https://web.fulcrumapp.com/photos/view?photos=2e0a0073-e129-42e2-9ac5-d7c733b2a3af%2Cbda8d309-7277-4a04-a191-f6ec3db16a7b%2C0c7843ba-9f2e-4e73-bb0e-338c8d013839%2Ca49f32e4-15dc-4e89-9855-e78efb7d9ac3 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
8b2c10de-a122-44bd-9adb-f2d2940b39a0 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:40:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 258 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 101850 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 45554.5353 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 258, 1 O'clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is missing. |  | One channel anchor bolt is missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 08b89a3d-3674-46b4-9e8f-8aab9abfab66,c9d96dbb-b3db-43e9-a146-bd8c971851c8 | , | https://web.fulcrumapp.com/photos/view?photos=08b89a3d-3674-46b4-9e8f-8aab9abfab66%2Cc9d96dbb-b3db-43e9-a146-bd8c971851c8 | Steel | Channel Bracket-Bolt | Missing
a379e392-3cc9-4d55-b3f5-d5b316daf689 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:02:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 260-261 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 88611 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 260 & 261, 1 O'Clock, Hydrophilic Joint Seal (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Active at time of inspection. |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Active at time of inspection. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Component should be "Hydrophilic Joint Seal (Circle Joint)". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | SS |  | Leak does not seem active at time of inspection. It appears that it has been previously treated. If this is not the case, this should still be addressed. | yes | yes |  | yes | Reduce priority to P3 | fda781ed-eacf-44d0-a7cc-2bfb6def7cfe,988a177b-129c-4126-af68-af18f9babc55,cca3cef5-8719-4aee-8e4c-015b08ff9519,819cc128-3186-4e58-bb5e-24984b35299b,4d382461-5805-44a8-85af-c06fed5e8830 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=fda781ed-eacf-44d0-a7cc-2bfb6def7cfe%2C988a177b-129c-4126-af68-af18f9babc55%2Ccca3cef5-8719-4aee-8e4c-015b08ff9519%2C819cc128-3186-4e58-bb5e-24984b35299b%2C4d382461-5805-44a8-85af-c06fed5e8830 | Concrete | Circular Joint | Leaks
c675c41d-91ea-4f87-8d64-1fb9df1b06ca | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 21:58:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 260 | 1 | Grout Injection Hole | Grout Injection Hole |  | 88610 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 260, 1 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | Leak is inactive at the time of the inspection. | no | yes |  |  |  | 921573a0-7ed2-446e-9b37-dc2444a25a5a,af0ab754-bc70-4761-99ef-ddebde533d9e | , | https://web.fulcrumapp.com/photos/view?photos=921573a0-7ed2-446e-9b37-dc2444a25a5a%2Caf0ab754-bc70-4761-99ef-ddebde533d9e | Concrete | Grout Hole | Leaks
e690b152-66f5-47ea-af18-749027e82655 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:45:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 260 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 88612 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 260, 3 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Behind cable tray and bracket | no | yes |  | no |  | 98c244b4-9c54-4caa-b0b6-d77cd8321882,8d255c49-933b-4b67-8b81-ab4c4a8d24bf,5378b326-d1ef-4e0b-a0d0-a1c752de16ce | ,, | https://web.fulcrumapp.com/photos/view?photos=98c244b4-9c54-4caa-b0b6-d77cd8321882%2C8d255c49-933b-4b67-8b81-ab4c4a8d24bf%2C5378b326-d1ef-4e0b-a0d0-a1c752de16ce | Concrete | Misc (Pipes/Cable Tray/etc) | Leaks
35df76bd-6240-498f-a1cc-c259ee754f00 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:47:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 260 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 88613 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4849 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 260, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Corrosion |  | Steel channel support bracket has Level 2 Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Due to leak defect behind bracket | no | no |  | yes | Suggest up grade to P3 | 4c05f142-447d-4838-8364-720f1420669c,6a30cbc7-413f-4bcc-bc98-ba5bdf81811c,bb8b997b-e187-4012-bb07-0a5d294aa6ed,438fcf24-fd7b-4465-bbc9-5f834072079c,580e7bc0-2597-4b56-a960-77befaa06f69 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=4c05f142-447d-4838-8364-720f1420669c%2C6a30cbc7-413f-4bcc-bc98-ba5bdf81811c%2Cbb8b997b-e187-4012-bb07-0a5d294aa6ed%2C438fcf24-fd7b-4465-bbc9-5f834072079c%2C580e7bc0-2597-4b56-a960-77befaa06f69 | Steel | Channel Bracket | Leaks
c5b5ddf5-6bb5-4aa0-875f-c596d474c5eb | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:42:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 260 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27456 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 260,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | Typical corrosion for these footings | no | yes |  | no |  | afd14c40-65a3-41b6-9974-6b4ca6f17acf,3ff55805-43f0-44b8-9486-75c32f0ef684 | , | https://web.fulcrumapp.com/photos/view?photos=afd14c40-65a3-41b6-9974-6b4ca6f17acf%2C3ff55805-43f0-44b8-9486-75c32f0ef684 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
09524689-2c77-42d6-afd1-2ba1223c74d0 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:56:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 262 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 88614 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4863 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 262, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 corrosion Channel anchor bolts have Level 2 corrosion |  | Steel channel support bracket has Level 2 corrosion Channel anchor bolts have Level 2 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  |  | no | yes |  | no |  | 2b5560b9-6386-40a5-9a20-b7c5bc8a8a30,4929202f-6dd4-478a-90a9-5963ee2c4fd5,f92073d2-34bd-40e4-ad35-6a98f1430c1f | ,, | https://web.fulcrumapp.com/photos/view?photos=2b5560b9-6386-40a5-9a20-b7c5bc8a8a30%2C4929202f-6dd4-478a-90a9-5963ee2c4fd5%2Cf92073d2-34bd-40e4-ad35-6a98f1430c1f | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
183ecd2c-74a8-499e-96f4-578ce8d27e36 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:00:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 264 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26927 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 264, 1 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 160801b1-24e0-45a4-bc5b-c9ad928b4eb4,54660b4b-57a3-4117-a746-1d780ae3f40d | , | https://web.fulcrumapp.com/photos/view?photos=160801b1-24e0-45a4-bc5b-c9ad928b4eb4%2C54660b4b-57a3-4117-a746-1d780ae3f40d | Concrete | Grout Hole | Leaks |  | Not Reinforcement
079df888-b0a7-4d5b-9332-9f453e489f60 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 264 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36579 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 264, 11 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Grout Hole | Leaks |  | Not Reinforcement
21c786e2-f3f3-498a-9dd0-8c525259d4ff | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:07:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 264 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76363 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8014 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 264, 2 O'Clock, Channel Anchor Bolts. |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | No change | no | yes |  | no |  | 9cb52d1d-2176-462e-b181-e4a2f9828f44,e8a6501f-8725-4109-a02c-eaf0fec5fdff | , | https://web.fulcrumapp.com/photos/view?photos=9cb52d1d-2176-462e-b181-e4a2f9828f44%2Ce8a6501f-8725-4109-a02c-eaf0fec5fdff | Steel | Channel Bracket-Bolt | Loose
0ee490b8-78e8-40b7-b465-6d39e52c98f9 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:47:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 264 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27457 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 264, 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 corrosion at anchor bolts of coveyor support. |  | Level 3 corrosion at anchor bolts of coveyor support. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [10 empty] | yes | This is a duplicate, suggest deleting. |  |  |  | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
a4fdbc63-87c9-401a-8af5-7d5726ec73e2 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 02:49:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 264 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36577 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43900.6675 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 264, 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 corrosion at anchor bolts of coveyor support. |  | Level 3 corrosion at anchor bolts of coveyor support. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | Typical corrosion for these footings | no | yes |  | no |  | 70276a1d-085f-4047-8b05-fc78bc0f18db,e5544d05-79ae-4d2e-b9b7-1aa7c8b47983,0be16f23-e20c-42f6-b8b6-1fc2447066b1 | ,, | https://web.fulcrumapp.com/photos/view?photos=70276a1d-085f-4047-8b05-fc78bc0f18db%2Ce5544d05-79ae-4d2e-b9b7-1aa7c8b47983%2C0be16f23-e20c-42f6-b8b6-1fc2447066b1 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
ed2c0311-014a-4b1e-99e9-80e44a31b67e | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:13:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 264 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27206 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 264,1 O'Clock,Concrete Element,New Defect 2017 |  |  |  | Leak at grout hole. |  | Leak at grout hole. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [10 empty] | yes | This is a duplicate of the existing 1 o'clock leak at grout hole defect. Suggest delete |  |  |  | Concrete | Grout Hole | Leaks
f80bad3f-7020-4f83-beca-4605384a9b98 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:15:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 266 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 88615 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4886 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 266, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion |  | Steel channel support bracket has Level 1 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Veryinor corrosion | no | yes |  | no |  | 24eb7d8a-dcc9-4c8c-8496-15c8a4cc7b51,8e532e32-bf74-49ea-a462-ff27b71d834c | , | https://web.fulcrumapp.com/photos/view?photos=24eb7d8a-dcc9-4c8c-8496-15c8a4cc7b51%2C8e532e32-bf74-49ea-a462-ff27b71d834c | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
0f4ebf43-58e4-4ece-a639-c8e69e1a3d64 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:16:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 266 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27458 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 266,1 O'Clock,Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion and Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion and Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Corrosion is minor | no | yes |  | no |  | a169ba72-c623-4d58-bb12-a810837f6888,127d324c-6e88-4cb5-8ebb-d4c27d23081b,b06a6995-38d4-4094-b41a-b1c3b3ef47e1 | ,, | https://web.fulcrumapp.com/photos/view?photos=a169ba72-c623-4d58-bb12-a810837f6888%2C127d324c-6e88-4cb5-8ebb-d4c27d23081b%2Cb06a6995-38d4-4094-b41a-b1c3b3ef47e1 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
c160b4a9-4e7d-41dc-8cbb-ddb71c88e986 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 10:10:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 266 | 11 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 36580 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43900.67 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring: 266, 11 O'clock: Segment Bolted Joint (Radial Joint). |  |  |  | Crack at radial bolted joint grout patch. |  | Crack at radial bolted joint grout patch. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | This minor cracking at bolted connection grout pad joints is not considered a significant defect. | no | yes |  | yes | Suggest deleting this defect | ac476691-b8fc-4ecc-845b-68866fe78e0e |  | https://web.fulcrumapp.com/photos/view?photos=ac476691-b8fc-4ecc-845b-68866fe78e0e | Concrete | Radial Joint | Crack
8c310d8f-1500-4485-96d9-f08151552dab | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 10 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 268 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27459 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 268,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [15 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
a48f656b-f0f2-4786-ad4f-8107bdf1c3e2 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 10:10:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 268 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27460 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 268,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | Typical corrosion for these footings | no | yes |  | no |  | 05ecf512-0d5a-4b35-b41c-9f91a401a5d6,ea043fdb-f378-475b-9de5-1dbff85fe87a,1be65abe-fc21-4a6e-b4a5-114dc50f56b8 | ,, | https://web.fulcrumapp.com/photos/view?photos=05ecf512-0d5a-4b35-b41c-9f91a401a5d6%2Cea043fdb-f378-475b-9de5-1dbff85fe87a%2C1be65abe-fc21-4a6e-b4a5-114dc50f56b8 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
5bca04f1-19b4-4c94-b828-280d818164aa | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 7 |  |  |  | 2025-07-27 05:45:42 AEST | 2025-07-27 05:47:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 243 | 8 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 36580 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43900.67 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring: 243, 8 O'clock: Segment Bolted Joint (Circle Joint). |  |  |  | Crack at radial bolted joint grout patch. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | no |  | feadb338-455a-4bf2-8ae4-464a46f27e98,0e05fae5-b03b-4084-9971-e60e7e46722c | , | https://web.fulcrumapp.com/photos/view?photos=feadb338-455a-4bf2-8ae4-464a46f27e98%2C0e05fae5-b03b-4084-9971-e60e7e46722c | Concrete | Circular Joint,Radial Joint | Drummy
01067606-6019-4037-8664-d46a2bdefa20 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 7 |  |  |  | 2025-07-27 05:54:28 AEST | 2025-07-27 05:56:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 249 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27208 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 249, 9 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak - Active at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | no |  | yes | Priority and risk to be downgraded | f511aaae-154d-407f-91dd-2f39b17b3630,2c6e0be8-133c-451a-8c2a-9a21af5be6be | , | https://web.fulcrumapp.com/photos/view?photos=f511aaae-154d-407f-91dd-2f39b17b3630%2C2c6e0be8-133c-451a-8c2a-9a21af5be6be | Concrete | Grout Hole | Leaks |  | Not Reinforcement
312d1faf-d7d2-4236-b8b4-42a74918ee78 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 7 |  |  |  | 2025-07-27 05:57:43 AEST | 2025-07-29 10:07:08 AEST | 30011704-user5@smec.com | james.stone@smec.com | 249 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Radial Joint) |  | 88606 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4686 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) | Unlikely (Failure within 20 years) |  | Ring 249, 7 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 4168c8fe-80ab-43a0-bc50-eab7efc2a041,c58faec0-34c4-44b8-b280-6c1b7111f37b,975f0eb0-5909-4a31-a77b-984c2cd142f9 | ,, | https://web.fulcrumapp.com/photos/view?photos=4168c8fe-80ab-43a0-bc50-eab7efc2a041%2Cc58faec0-34c4-44b8-b280-6c1b7111f37b%2C975f0eb0-5909-4a31-a77b-984c2cd142f9 | Concrete | Circular Joint,Radial Joint | Drummy
3593bb5d-248f-4602-89ba-41236107c01c | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-27 22:12:38 AEST | 2025-07-27 22:14:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 251 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27208 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | 4 |  | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 251, 2 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak - Active at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | No change. Priority level has been previously agreed with BHP AIMS. | no | yes |  | yes | Reduce priority to P3 | 3e4192f8-8e05-4c28-bf0e-a4c72cc05375,ba2f061b-e124-415b-8b42-c174f4bf786f,d99a5b78-09ed-43de-bb30-4d1a67b1bd38 | ,, | https://web.fulcrumapp.com/photos/view?photos=3e4192f8-8e05-4c28-bf0e-a4c72cc05375%2Cba2f061b-e124-415b-8b42-c174f4bf786f%2Cd99a5b78-09ed-43de-bb30-4d1a67b1bd38 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
16662d39-e963-4015-bf3b-493dd3711be9 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-27 23:01:28 AEST | 2025-07-29 10:06:05 AEST | 30011704-user5@smec.com | james.stone@smec.com | 262 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 88612 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 262, 3 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Behind cable tray and bracket | no | yes |  | no |  | 57bea739-57d6-4351-a657-8cd83aa8599f,5e8f0ebb-ed16-4ba6-9d14-a851a700000e,73acfa7b-fb8e-4cdd-8172-46b87f9f6994,ce13bf6d-ffa0-4bce-96e4-de848acc0672,8bc74156-1719-4fd6-96c9-40f17afc2373 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=57bea739-57d6-4351-a657-8cd83aa8599f%2C5e8f0ebb-ed16-4ba6-9d14-a851a700000e%2C73acfa7b-fb8e-4cdd-8172-46b87f9f6994%2Cce13bf6d-ffa0-4bce-96e4-de848acc0672%2C8bc74156-1719-4fd6-96c9-40f17afc2373 | Concrete | Misc (Pipes/Cable Tray/etc) | Leaks
2d8bd334-9b78-4585-8298-1d9a6212c2c3 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-27 23:34:26 AEST | 2025-07-29 10:05:50 AEST | 30011704-user5@smec.com | james.stone@smec.com | 255 | 10 | Grout Injection Hole |  | Patched bracket mounting hole | 36574 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 255, 10 O'clock, Bracket mount hole | Break up of grout and water leaks |  |  | Grout injection hole has Leak Inactive at time of inspection. |  | Patch on bracket anchor hole is drummy | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | Drummy previous patch | no | no |  | yes | Suggest downgrade to P4 | be8304bb-b288-4822-88e3-b37cf0cc9341,e18e6087-2f7b-4362-af0c-4be35ec0ebfc | , | https://web.fulcrumapp.com/photos/view?photos=be8304bb-b288-4822-88e3-b37cf0cc9341%2Ce18e6087-2f7b-4362-af0c-4be35ec0ebfc | Concrete | Grout Hole | Drummy |  | Not Reinforcement. Grout hole
974e830c-e91d-43d2-aa1e-225fa32e8223 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-27 23:41:14 AEST | 2025-07-29 10:05:27 AEST | 30011704-user5@smec.com | james.stone@smec.com | 256 | 10 | Grout Injection Hole | Grout Injection Hole |  | 36573 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 256, 10 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No change Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 3d8e9cc8-716d-449c-9aac-5bc30142281a,004acd31-7880-44ed-b55f-3e13e153b73d | , | https://web.fulcrumapp.com/photos/view?photos=3d8e9cc8-716d-449c-9aac-5bc30142281a%2C004acd31-7880-44ed-b55f-3e13e153b73d | Concrete | Grout Hole | Leaks |  | Not Reinforcement
ae8474ca-f44c-486d-a258-cf3f6a66c6ae | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-27 23:52:58 AEST | 2025-07-29 10:04:57 AEST | 30011704-user5@smec.com | james.stone@smec.com | 264 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36576 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 264, 11 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Does not appear active Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | f99d2f14-ce49-45a7-9b27-1cda8bceb610,3cd57bed-7ab9-4342-8f00-fff2269f4ec1 | , | https://web.fulcrumapp.com/photos/view?photos=f99d2f14-ce49-45a7-9b27-1cda8bceb610%2C3cd57bed-7ab9-4342-8f00-fff2269f4ec1 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
bd6df794-bf08-4020-9c65-5346019733b3 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-27 23:57:21 AEST | 2025-07-29 10:03:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 268 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27208 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 268, 9 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak - Active at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | no |  | yes | Priority and risk to be downgraded | 7e7686ef-8433-49c3-93e9-23e3bd7ed432,5fae4e41-2475-475f-958e-62e411e8a39a,2a40e9cf-61fd-427f-bc5e-1405da346872 | ,, | https://web.fulcrumapp.com/photos/view?photos=7e7686ef-8433-49c3-93e9-23e3bd7ed432%2C5fae4e41-2475-475f-958e-62e411e8a39a%2C2a40e9cf-61fd-427f-bc5e-1405da346872 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
aec7f09a-44c6-4266-a3d1-270e290c4883 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-27 23:59:20 AEST | 2025-07-29 10:03:17 AEST | 30011704-user5@smec.com | james.stone@smec.com | 270 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27208 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 270, 9 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak - Active at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | SS |  | Priority level has been previously agreed with BHP AIMS. | no | no |  | yes | Priority and risk to be downgraded | b85cd198-243f-46c7-8751-6c3ae486fafb,8be0a45c-6854-4391-a047-a201e418c2df,1b1b8bec-dbc2-4ead-9730-4a7f5c12282e | ,, | https://web.fulcrumapp.com/photos/view?photos=b85cd198-243f-46c7-8751-6c3ae486fafb%2C8be0a45c-6854-4391-a047-a201e418c2df%2C1b1b8bec-dbc2-4ead-9730-4a7f5c12282e | Concrete | Grout Hole | Leaks |  | Not Reinforcement
c146911a-c041-4fd9-8850-744b25a10afb | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-28 02:19:15 AEST | 2025-07-28 02:21:16 AEST | 30011704-user5@smec.com | james.stone@smec.com | 251 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Radial Joint) |  | 88606 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4686 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) | Unlikely (Failure within 20 years) |  | Ring 251, 7 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 24ba0884-cc9a-4e65-94a3-810f0566760b,4248fead-7b75-4eec-89c9-5aceed2190ea,2afdbd94-b1d6-4c35-bdd4-4fec52da182a | ,, | https://web.fulcrumapp.com/photos/view?photos=24ba0884-cc9a-4e65-94a3-810f0566760b%2C4248fead-7b75-4eec-89c9-5aceed2190ea%2C2afdbd94-b1d6-4c35-bdd4-4fec52da182a | Concrete | Circular Joint,Radial Joint | Drummy
5d4fac42-c616-46ec-876e-21c3a581e672 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-28 02:28:52 AEST | 2025-07-28 02:30:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | 255 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Radial Joint) |  | 88606 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4686 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 255, 7 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Grout debonding over these connection plates is considered a cosmetic issue with no structural impact. | no | yes |  | yes | Update description | 81375657-7e2b-45db-b321-572c5cd608d3,91db03b8-b529-4c56-b3f0-dbb561235c4c | , | https://web.fulcrumapp.com/photos/view?photos=81375657-7e2b-45db-b321-572c5cd608d3%2C91db03b8-b529-4c56-b3f0-dbb561235c4c | Concrete | Circular Joint,Radial Joint | Drummy
814c4b13-8c46-4471-bf8f-cfdc33d3b983 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 0a69fbad-efd1-4d3a-bd86-3e3525881922 | 6 |  |  |  | 2025-07-28 02:35:01 AEST | 2025-07-28 02:35:40 AEST | 30011704-user5@smec.com | james.stone@smec.com | 257 | 8 | Grout Injection Hole | Grout Injection Hole |  | 36573 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 256, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | No change Priority level has been previously agreed with BHP AIMS. | no | yes |  | no |  | 82ae9bf7-733a-4f2e-a5c9-0dced435d3cf,a2ea687b-d19a-4c1e-89dc-37022e8c948d | , | https://web.fulcrumapp.com/photos/view?photos=82ae9bf7-733a-4f2e-a5c9-0dced435d3cf%2Ca2ea687b-d19a-4c1e-89dc-37022e8c948d | Concrete | Grout Hole | Leaks |  | Not Reinforcement
f1407566-0bbc-4393-87b1-e2703a76f202 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:14:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 271 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 76364 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8033 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 271, 9 o'clock. Segmented Bolted Joint (Circle Joint). |  |  |  | Steel bar insert exposed from Segmented Bolted Joint (Circle Joint) |  | Steel bar insert exposed from Segmented Bolted Joint (Circle Joint) | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | RT |  | Steel bar insert exposed from segmented bolted joint. | no |  |  |  |  | 3885db35-7c69-4d5c-9154-7c6666ea465e,17b4a9f2-2b3f-4456-813b-53de2af2ab20,06046ea8-74ee-4c15-9eab-cdb43e8dd20e | ,, | https://web.fulcrumapp.com/photos/view?photos=3885db35-7c69-4d5c-9154-7c6666ea465e%2C17b4a9f2-2b3f-4456-813b-53de2af2ab20%2C06046ea8-74ee-4c15-9eab-cdb43e8dd20e | Steel | Reinforcement |  |  | Reinforcement
031469f2-1af3-43b0-9ea1-f6dce03b258f | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:16:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 271 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26929 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 271,3 O'Clock,Ducting,Still existing in 2017. |  |  |  | Cable tray, Class 4 - Medium high corrosion |  | Cable tray, Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | The cable tray has been replaced | yes |  |  |  |  | 604f0e73-e926-47d5-b15a-de948b1d137f |  | https://web.fulcrumapp.com/photos/view?photos=604f0e73-e926-47d5-b15a-de948b1d137f | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
4379f011-ffc7-4454-ab38-2b94648f9177 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 10:58:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 272 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 88616 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4904 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 272, 2 O'Clock, Channel Anchor Bolts |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Appears to have no loose nuts anymore | yes |  |  |  |  | 4edd1c96-e1d3-416b-ad80-0c906989d84a |  | https://web.fulcrumapp.com/photos/view?photos=4edd1c96-e1d3-416b-ad80-0c906989d84a | Steel | Channel Bracket-Bolt | Loose
4ca145a8-89c0-413a-91b7-a76af863f889 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:57:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 272 | 7 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 76365 |  | 6655 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 18/06/2022 |  | 4/04/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 272, 7 o'clock. Hydrophyllic Joint Seal (Circle Joint). | Failure to seal joint | Failure to seal joint |  | Circle joint seal has Leak Active at time of inspection. |  | Circle joint seal has Leak Active at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | HSE | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | On-Line | No | Walkway | - | Engineering Repair Methodology Required Competent Supervisor | [11 empty] | Concrete | Circular Joint | Leaks
5a8e9681-e8db-4fba-b86d-0f0296840a96 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:16:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 273 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27150 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 273,3 O'Clock,Ducting,New Defect 2017 |  |  |  | Cable tray, Class 4 - Medium high corrosion |  | Cable tray, Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | The steel cable try has been replaced | yes |  |  |  |  | d22d0194-c8b8-4e25-a14b-e69551fc6ae2 |  | https://web.fulcrumapp.com/photos/view?photos=d22d0194-c8b8-4e25-a14b-e69551fc6ae2 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
e711616d-be00-45ae-99d1-c2a2b4bc9480 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:06:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 274 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26931 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 274, 1 O'clock, Hydrophilic Joint Seal (Circle Joint). | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | 200mm long minor crack. Hydrophilic Joint Seal (Circle Joint) has leak - Inactive at the time of inspection. |  | 200mm long minor crack. Hydrophilic Joint Seal (Circle Joint) has leak - Inactive at the time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Hydraulic joint had inactive leak with delaminated/ drummy grout | yes |  |  |  |  | d8afd857-7f01-4f54-beef-33f180f1e0dd,c49bc35e-1936-41cd-99a3-fb2c130cd152 | , | https://web.fulcrumapp.com/photos/view?photos=d8afd857-7f01-4f54-beef-33f180f1e0dd%2Cc49bc35e-1936-41cd-99a3-fb2c130cd152 | Concrete | Circular Joint | Crack,Drummy,Leaks |  | Not Reinforcement
b7293a2b-fa03-4770-926c-c3fe6b18f092 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:18:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 274 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 88617 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4926 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 274, 2 & 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion. One channel anchor bolt is missing. |  | Steel channel support bracket has Level 1 corrosion. One channel anchor bolt is missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, actively correcting | no |  |  |  |  | 5da691c6-1bb0-43bb-9026-1c5cf52b58f8,49f8fd0d-a0aa-40a9-a2f1-7592a6ff8972 | , | https://web.fulcrumapp.com/photos/view?photos=5da691c6-1bb0-43bb-9026-1c5cf52b58f8%2C49f8fd0d-a0aa-40a9-a2f1-7592a6ff8972 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
b39d1348-4ef0-4db7-b003-221725fc4bde | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:18:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 274 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27151 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 274, 3 O'Clock, Cable Tray |  |  |  | Cable tray has level 2 corrosion. |  | Cable tray has level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Cable tray still got the surface corrosion | no |  |  |  |  | 57b7b547-d738-4e08-b40a-ebad0ca81f46 |  | https://web.fulcrumapp.com/photos/view?photos=57b7b547-d738-4e08-b40a-ebad0ca81f46 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Surface
47ee7d24-8472-411b-af01-ea77e1bbe0a4 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:18:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 274 | 7 | Grout Injection Hole | Grout Injection Hole |  | 76366 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 4. >= US$250 million, < US$2 billion |  | Severity Level 4. >= US$250 million, < US$2 billion | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 274, 7 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | No signs of leak at grout injection hole | yes |  |  |  |  | 074865ea-f90a-4157-b758-27e9a1e70492,22788743-1382-496e-88fc-4401058f171d,6837036b-9024-425f-984f-eb500ad84194 | ,, | https://web.fulcrumapp.com/photos/view?photos=074865ea-f90a-4157-b758-27e9a1e70492%2C22788743-1382-496e-88fc-4401058f171d%2C6837036b-9024-425f-984f-eb500ad84194 | Concrete | Grout Hole | Leaks
138471bb-3f4b-49d6-ac50-28336a517c87 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:18:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 275 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27152 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 275, 3 O'Clock, Cable Tray |  |  |  | Cable tray has level 2 corrosion. |  | Cable tray has level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Cable try at 3 o’clock is heavily corroded | yes |  |  |  |  | c22ee302-8834-4045-9354-643e7afc6c63 |  | https://web.fulcrumapp.com/photos/view?photos=c22ee302-8834-4045-9354-643e7afc6c63 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
b6763fd3-f590-4091-8335-608cba2e0b7a | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:14:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 275 | 7 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 101839 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 45554.4902 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 275, 7 O'clock, Segment Bolted Joint (Radial Joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Radial joint has drummy concrete over an area of 250 mm x 250 mm. | no |  |  |  |  | 4ea18064-9bc6-4a9d-a224-70392acbb383,dfd3e9cf-8dcb-42b2-9955-93f0029eae05 | , | https://web.fulcrumapp.com/photos/view?photos=4ea18064-9bc6-4a9d-a224-70392acbb383%2Cdfd3e9cf-8dcb-42b2-9955-93f0029eae05 | Concrete | Circular Joint | Drummy |  | Circular Joint
d054ebfe-2006-4f62-addc-4758cd8200f8 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:21:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 276 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76367 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8078 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 276, 1 O'clock, Channel Anchor Bolts. |  |  |  | Nut missing at one channel anchor bolt at 1 O'clock, |  | Nut missing at one channel anchor bolt at 1 O'clock, | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still nut is missing with bolt being getting corroded | no |  |  |  |  | 0ae40846-f228-4c21-a429-96ea4dfb7816 |  | https://web.fulcrumapp.com/photos/view?photos=0ae40846-f228-4c21-a429-96ea4dfb7816 | Steel | Channel Bracket-Bolt | Missing
12515aff-d5d1-4a43-9d09-f69f24eca864 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 | -20.3218 | 118.5857 | POINT (118.5856675 -20.3217821) | 2025-05-27 20:13:18 AEST | 2025-07-29 11:21:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 276 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36582 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 276, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole at inactive leak at the time of inspection , no change in the condition | no |  |  |  |  | 49f88095-5bf4-4c2a-82e2-7b2c1b326e7b |  | https://web.fulcrumapp.com/photos/view?photos=49f88095-5bf4-4c2a-82e2-7b2c1b326e7b | Concrete | Grout Hole | Leaks |  | Not Reinforcement
6d0eb2ce-7ae6-4109-b973-510aaafcd8ce | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:22:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 276 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 88618 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.494 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 276, 2 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Steel channel and the bolts are severely corroded | yes |  |  |  |  | fc324cb7-8ec3-48de-935d-086ee06c01f8,b8745bb3-035b-429b-98c8-48d614e9247e | , | https://web.fulcrumapp.com/photos/view?photos=fc324cb7-8ec3-48de-935d-086ee06c01f8%2Cb8745bb3-035b-429b-98c8-48d614e9247e | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
5f88b0c0-b58e-4ece-92ea-27d544db2056 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:13:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 276 | 9 | Grout Injection Hole | Grout Injection Hole |  | 76368 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 276, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | RT |  | Trail of dry leak are present. No active leakage at time of inspection. | no |  |  |  |  | 1f8088fa-c6af-4ded-b884-fc82b3e1d9fd,25b4ab65-9a27-403f-b521-ef791e314ac7 | , | https://web.fulcrumapp.com/photos/view?photos=1f8088fa-c6af-4ded-b884-fc82b3e1d9fd%2C25b4ab65-9a27-403f-b521-ef791e314ac7 | Concrete | Grout Hole | Leaks
6e880d6a-a9f0-4c5e-8fda-fa4f205632a1 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:11:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 276 | 9 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 36581 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 4. >= US$250 million, < US$2 billion |  | Severity Level 4. >= US$250 million, < US$2 billion | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 276, 9 O'clock, Segmented Bolted Joint (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Component should be "Segmented Bolted Joint (Circle Joint)". Adopted the default consequence Financial - Level 3. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | RT |  | No presence of Drummy concrete. Etched surface with delaminated concrete section. | yes |  |  |  |  | 651be905-f828-4155-ad59-8fb926d1079f,cbd605d7-505d-4440-9d01-3c52674f1d77,66a46c2a-5135-449f-80fc-d07a69208c85 | ,, | https://web.fulcrumapp.com/photos/view?photos=651be905-f828-4155-ad59-8fb926d1079f%2Ccbd605d7-505d-4440-9d01-3c52674f1d77%2C66a46c2a-5135-449f-80fc-d07a69208c85 | Concrete | Circular Joint | Drummy |  | Not Reinforcement
5ec9fa01-3f82-46b7-9116-1c356a45855b | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:18:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 276 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27463 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 276, 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 corrosion at anchor bolts of coveyor support. |  | Level 3 corrosion at anchor bolts of coveyor support. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | RT |  | Corrosion on conveyor support footing. | no |  |  |  |  | b4f4f822-90b1-4a26-a2e7-7824807ce9ca,cc506c90-f57d-49be-b93c-8149e45f5610 | , | https://web.fulcrumapp.com/photos/view?photos=b4f4f822-90b1-4a26-a2e7-7824807ce9ca%2Ccc506c90-f57d-49be-b93c-8149e45f5610 | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support not channel bracket
68d7f517-b828-4af9-a9fb-53e493d0bd52 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:26:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 276 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27462 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 276,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | No change in the condition, actively corroding base plate and bolts | yes |  |  |  |  | e5dbf056-48cf-43f0-9c50-b93e696ef8c1,05721f7a-c81d-44de-b8d1-5168cf817697 | , | https://web.fulcrumapp.com/photos/view?photos=e5dbf056-48cf-43f0-9c50-b93e696ef8c1%2C05721f7a-c81d-44de-b8d1-5168cf817697 | Steel | Centre Support,Centre Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Centre support and bolt no Channel bracket
6963823b-a983-452b-b8f1-bdeef0b652b0 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:16:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 277 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26932 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 277, 3 O'Clock, Cable Tray |  |  |  | Cable tray has level 2 corrosion. |  | Cable tray has level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Cable try had severely corroded | yes |  |  |  |  | f9d6cbf5-b715-4d88-9187-0fea4e7e3022 |  | https://web.fulcrumapp.com/photos/view?photos=f9d6cbf5-b715-4d88-9187-0fea4e7e3022 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
d8995e5c-fc94-4613-ac43-b8a61812b622 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 18:06:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 277 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27205 |  | 8517 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 25/01/2023 |  | 17/10/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Structure,Ring 277,11 O'Clock,Concrete Element,New Defect 2017 | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Dry leak and salt deposits. |  | Dry leak and salt deposits. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. Repair verified LC 9/10/24 | Not Specified | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Engineering Repair Methodology Required Competent Engineer | RT |  | No signs of chloride induced leaks or corrosion. | yes |  |  |  |  | 920290a9-f390-4ff2-9beb-ee07a8e39628,ba84adab-d6ac-47bd-87a6-a6c2b7956fe0,2b78ec09-c4f7-4b48-b12f-f9988e75f576,c2e883f0-e6be-45e2-8d8b-941d90ee1560,9558e867-9e17-49d5-a397-23608a29ba75 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=920290a9-f390-4ff2-9beb-ee07a8e39628%2Cba84adab-d6ac-47bd-87a6-a6c2b7956fe0%2C2b78ec09-c4f7-4b48-b12f-f9988e75f576%2Cc2e883f0-e6be-45e2-8d8b-941d90ee1560%2C9558e867-9e17-49d5-a397-23608a29ba75 | Concrete |  | Leaks |  | Not Reinforcement
e32f692a-63e3-450f-845f-53a821012079 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:37:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 278 | 2 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 88620 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.4972 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 278, 2 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Crack on patch repair of radial joint up to 0.25mm in width. |  | Crack on patch repair of radial joint up to 0.25mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | The radial grout still had 0.25mm crack at the time of inspection, no change in condition | no |  |  |  |  | d447ee16-6115-44b0-9ae9-6783145ef66f |  | https://web.fulcrumapp.com/photos/view?photos=d447ee16-6115-44b0-9ae9-6783145ef66f | Concrete | Radial Joint | Crack
edda3b1f-25b4-4f79-91d3-143c4fc19661 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:45:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 278 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 88619 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 4. >= US$250 million, < US$2 billion |  | Severity Level 4. >= US$250 million, < US$2 billion | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 278, 5 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400mm x 250mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Safety | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | KP |  | The delaminated/ drummy grout still present at the radial joint | no |  |  |  |  | a80a909d-a624-4974-a15b-5abbc3494efe |  | https://web.fulcrumapp.com/photos/view?photos=a80a909d-a624-4974-a15b-5abbc3494efe | Concrete | Circular Joint | Drummy |  | Not radial
8e1907c3-82de-4c9b-b464-3c22e515a049 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:55:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 280 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 88622 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5002 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 280, 2 O'Clock, Channel Anchor Bolts |  |  |  | Channel anchor bolts have Level 1 corrosion |  | Channel anchor bolts have Level 1 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | The anchor bolt and nut is severely corroded | no |  |  |  |  | e9362b6a-7900-4334-9003-e1429ff2386b |  | https://web.fulcrumapp.com/photos/view?photos=e9362b6a-7900-4334-9003-e1429ff2386b | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
c16cba2a-839f-4b72-b59d-4c7094b1c93f | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:13:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 280 | 9 | Grout Injection Hole | Grout Injection Hole |  | 88621 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 280, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | On-Line | No | - | - | Condition Monitoring Competent Supervisor | RT |  | Trails of dry leak present. Ni changes | no |  |  |  |  | 98f57c20-91f7-4623-ba4c-ac31651755d1,b93c96d9-5a37-49b9-b5a6-edb09795ce17 | , | https://web.fulcrumapp.com/photos/view?photos=98f57c20-91f7-4623-ba4c-ac31651755d1%2Cb93c96d9-5a37-49b9-b5a6-edb09795ce17 | Concrete | Grout Hole | Leaks
3ce35cc2-3fd8-4e72-a7dc-e074464efc16 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:54:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 280 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27464 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 280, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | The steel channel and bolts are severely corroded, no change in condition | no |  |  |  |  | f4f87f48-1fbd-4a4c-ba8f-403f7d7c5219,ecb697f8-ec96-49cd-89b8-c302657ee46e,01b8e626-211a-4f5c-bfa7-473e30445ae6,2a38a7b6-23fa-420a-ac10-c5096e9127bd | ,,, | https://web.fulcrumapp.com/photos/view?photos=f4f87f48-1fbd-4a4c-ba8f-403f7d7c5219%2Cecb697f8-ec96-49cd-89b8-c302657ee46e%2C01b8e626-211a-4f5c-bfa7-473e30445ae6%2C2a38a7b6-23fa-420a-ac10-c5096e9127bd | Steel | Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Not channel bracket/ bolt
74933805-b2df-42a5-af32-3a615529f783 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:15:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 281 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27153 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 281,3 O'Clock,Ducting,New Defect 2017 |  |  |  | Cable tray, Class 3 - Medium corrosion |  | Cable tray, Class 3 - Medium corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | Cable tray has been replaced | yes |  |  |  |  | 7026f692-2c09-4ed8-95f5-a80743819d99 |  | https://web.fulcrumapp.com/photos/view?photos=7026f692-2c09-4ed8-95f5-a80743819d99 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
c4d8d92a-86e2-4fad-baac-6140956ece8a | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:04:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 282 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 88625 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5042 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 282, 1 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion Channel anchor bolts have Level 1 corrosion |  | Steel channel support bracket has Level 1 corrosion Channel anchor bolts have Level 1 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | The steel channel has some surface corrosion and anchor bolt is heavily corroded | yes |  |  |  |  | de6e9305-db1f-47e9-a487-62058c6c89a2,c2a15d9a-b4c7-4470-871f-5d6f4bdf38cf | , | https://web.fulcrumapp.com/photos/view?photos=de6e9305-db1f-47e9-a487-62058c6c89a2%2Cc2a15d9a-b4c7-4470-871f-5d6f4bdf38cf | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
dff28d85-4691-44fb-813b-d241b59637a5 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:05:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 282 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 88624 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5026 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 282, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion |  | Steel channel support bracket has Level 1 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | The steel channel and anchor bolt is heavily corroded | yes |  |  |  |  | 8a9a777f-7511-498f-b645-f3b44586fcec,60f17b86-dc29-4bb4-b473-b9256735f5eb | , | https://web.fulcrumapp.com/photos/view?photos=8a9a777f-7511-498f-b645-f3b44586fcec%2C60f17b86-dc29-4bb4-b473-b9256735f5eb | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
6f2ebbe0-aa93-4f0d-8069-9d88f87ad3f9 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:13:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 282 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88623 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5015 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 282, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack around patch repair |  | Crack around patch repair | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Unable to confirm condition change. Can not confirm propagation of crack since size of crack is not mentioned in earlier inspection. | [5 empty] | 99d5ed23-1baf-4a8d-a6f0-5ccee458fcaa,54ec05fa-e880-41f5-ab6f-66a14e628833,d46ccbb5-d4ba-45e1-9253-38bb044dead0,64aa32d2-8299-4599-a9ca-00b9fb166b3f,02b5cac4-ebbf-494c-be8e-1b115d3ef6f0 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=99d5ed23-1baf-4a8d-a6f0-5ccee458fcaa%2C54ec05fa-e880-41f5-ab6f-66a14e628833%2Cd46ccbb5-d4ba-45e1-9253-38bb044dead0%2C64aa32d2-8299-4599-a9ca-00b9fb166b3f%2C02b5cac4-ebbf-494c-be8e-1b115d3ef6f0 | Concrete | Circular Joint | Crack
5f33a21d-2a69-4e42-9d2c-52f1bc566204 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:15:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 282 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27154 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 282,3 O'Clock,Ducting,New Defect 2017 |  |  |  | Cable tray, Class 3 - Medium corrosion |  | Cable tray, Class 3 - Medium corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | Cable tray has been replaced | yes |  |  |  |  | 7425158a-8bfc-43a2-a050-3f1d4095c2ad |  | https://web.fulcrumapp.com/photos/view?photos=7425158a-8bfc-43a2-a050-3f1d4095c2ad | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
b1ab16b0-815b-4829-9c46-ff5c3205b53b | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:53:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 283 | 5 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88626 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5058 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 283, 5 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Delaminated/ drummy grout along the circumferential joint still present, no change in area of drumminess | no |  |  |  |  | 17275653-ec1d-4e66-9d58-6b2395259f87,864fab8b-e579-43e5-b155-fd02c4561dde | , | https://web.fulcrumapp.com/photos/view?photos=17275653-ec1d-4e66-9d58-6b2395259f87%2C864fab8b-e579-43e5-b155-fd02c4561dde | Concrete | Circular Connection,Circular Joint | Drummy
48a0e26f-e1bb-4130-8b6a-f3f1d8873e7a | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:15:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 283 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26933 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 283,3 O'Clock,Ducting,Still existing in 2017. |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | The cable tray has been replaced | yes |  |  |  |  | 76058680-db9d-4390-99aa-80fb26e07f1b |  | https://web.fulcrumapp.com/photos/view?photos=76058680-db9d-4390-99aa-80fb26e07f1b | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
8795106d-f8f0-4eb7-9164-6f0c5b274101 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 18:19:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 284 | 12 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36588 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 284, 12 O'clock, Anchor bolt of pipe support bracket | Rupture | Rupture |  | Anchor bolt of pipe support detached. |  | Anchor bolt of pipe support detached. | Loss of minor services (NOT water pipe). Loss of bolt connection and failure of equipment support. |  | Loss of minor services (NOT water pipe). Loss of bolt connection and failure of equipment support. | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Not Specified | Priority: P3 |  |  |  | Re-instate pipe support | AIMS structural inspector. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | KP |  | Bo change in the condition | no |  |  |  |  | 16bc0f55-f8da-4f17-9ba6-4e58295db8b9 |  | https://web.fulcrumapp.com/photos/view?photos=16bc0f55-f8da-4f17-9ba6-4e58295db8b9 | Steel | Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Missing
0c7ccc3c-0111-4ce6-ac8b-79af16ffff59 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:13:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 284 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88627 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5079 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 284, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack and minor spalling on repair patch of circle joint. |  | Crack and minor spalling on repair patch of circle joint. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | No visible cracks present. Signs of minor spalling. | yes |  |  |  |  | 1f8c669d-9b6e-4afc-9251-d5315757b4dd,abc07c88-a20e-4096-80f7-f4907d90b95f | , | https://web.fulcrumapp.com/photos/view?photos=1f8c669d-9b6e-4afc-9251-d5315757b4dd%2Cabc07c88-a20e-4096-80f7-f4907d90b95f | Concrete | Circular Joint | Crack,Surface Damage
d3163e36-1b05-406c-a358-52da5f22a016 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:22:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 284 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27465 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 284, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 1 to Level 2 corrosion at anchor bolts of walkway support. |  | Level 1 to Level 2 corrosion at anchor bolts of walkway support. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | The anchor bolt and steel channel of walkway support as well as belt support is severely corroded | yes |  |  |  |  | 31f1e52d-997f-4b96-b8ea-fa1728d863e8,db260632-6055-402c-922c-8ed7cd95db65 | , | https://web.fulcrumapp.com/photos/view?photos=31f1e52d-997f-4b96-b8ea-fa1728d863e8%2Cdb260632-6055-402c-922c-8ed7cd95db65 | Steel | Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Not channel bracket or bolt
d8799d0f-2e25-4786-b794-314e17289f4b | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:15:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 284 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27155 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 284,3 O'Clock,Ducting,New Defect 2017 |  |  |  | Cable tray, Class 3 - Medium corrosion |  | Cable tray, Class 3 - Medium corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | Cable tray has been replaced | yes |  |  |  |  | 127bced5-30e6-4693-9c68-2d34ac76020b |  | https://web.fulcrumapp.com/photos/view?photos=127bced5-30e6-4693-9c68-2d34ac76020b | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
70abf455-4d9d-432d-b7db-934db3adff9e | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:28:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 285 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27156 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 285,3 O'Clock,Ducting,New Defect 2017 |  |  |  | Cable tray, Class 3 - Medium corrosion |  | Cable tray, Class 3 - Medium corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | Cable tray has been replaced | yes |  |  |  |  | 00114446-13df-40e8-89ea-3034c75e2da9 |  | https://web.fulcrumapp.com/photos/view?photos=00114446-13df-40e8-89ea-3034c75e2da9 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
0bd6bba4-c59f-4fc4-91e3-36fa6d8da450 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:12:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 286 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88628 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5092 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 286, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack on patch repair of circle joint. |  | Crack on patch repair of circle joint. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Unsure about condition change. Crack is present on patch repair unable to confirm whether crack has propagated any further. Crack size at time of inspection is 170mm | [5 empty] | bb79e15e-a75d-4262-840e-524f0549285b,37460eba-bb69-4ecd-9d98-e13d3d877535 | , | https://web.fulcrumapp.com/photos/view?photos=bb79e15e-a75d-4262-840e-524f0549285b%2C37460eba-bb69-4ecd-9d98-e13d3d877535 | Concrete | Circular Joint | Crack
86b9ef95-c411-44f1-a3c8-7fe39702f556 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:04:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 287 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26934 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 287, 8 O'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak - Active at time of inspection. Evidence of erosion |  | Grout injection hole has leak - Active at time of inspection. Evidence of erosion | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | RT |  | Active leak chloride induced. Leak has not stopped. Hole is completely covered in seepage | yes |  |  |  |  | 2d09fe99-69dd-4dbc-a322-035ec0a4a32f,43ea84a0-8daf-4bed-8e75-43f2e419e75e,4b0f2429-d095-4197-ac25-15cd5955e927,c63d1c46-f65a-4671-997c-f2bf1e4b874d | ,,, | https://web.fulcrumapp.com/photos/view?photos=2d09fe99-69dd-4dbc-a322-035ec0a4a32f%2C43ea84a0-8daf-4bed-8e75-43f2e419e75e%2C4b0f2429-d095-4197-ac25-15cd5955e927%2Cc63d1c46-f65a-4671-997c-f2bf1e4b874d | Concrete | Grout Hole | Leaks |  | Not Reinforcement
d6435b27-4605-4c97-ade0-89b9d742d6d5 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:11:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 287 | 9 | Grout Injection Hole | Grout Injection Hole |  | 101840 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 19/09/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 287, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Active at time of inspection. |  | Grout injection hole has leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | RT |  | Leak has not been repaired. Wet leak chloride induced with big built up of salt | yes |  |  |  |  | 0c2c2fb7-769b-4599-bec8-6aa80522ad0b,cd178a20-acf1-408c-bd4e-47e390e9955e | , | https://web.fulcrumapp.com/photos/view?photos=0c2c2fb7-769b-4599-bec8-6aa80522ad0b%2Ccd178a20-acf1-408c-bd4e-47e390e9955e | Concrete | Grout Hole | Leaks
209798a5-877e-4bfc-8c9b-bf3f426443d7 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:53:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 288 | 5 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27466 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 288, 5 O'clock: Steel Anchor Bolts.w |  |  |  | Level 3 corrosion at anchor bolts of walkway support. |  | Level 3 corrosion at anchor bolts of walkway support. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | The anchor bolt of walkway support is severely corroded | no |  |  |  |  | 21fc855d-714a-4386-85d1-5ae507fccff1 |  | https://web.fulcrumapp.com/photos/view?photos=21fc855d-714a-4386-85d1-5ae507fccff1 | Steel | Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Not Channel Bracket
5297b5cb-f623-41de-9134-dfeca3213187 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:38:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 288 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27467 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 288,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | No change in the condition, heavily corroded | no |  |  |  |  | 8d31ec22-213c-4301-a9cd-9783ee11a6ad |  | https://web.fulcrumapp.com/photos/view?photos=8d31ec22-213c-4301-a9cd-9783ee11a6ad | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support not channel bracket
d37db267-cd13-4655-ba32-40fc7d3aa7e7 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:41:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 289 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76371 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8144 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 289, 1 o'clock. Channel Anchor Bolts. |  |  |  | Steel channel support bracket has Level 1 Surface Corrosion and Channel anchor bolts have Level 1 Low Corrosion. |  | Steel channel support bracket has Level 1 Surface Corrosion and Channel anchor bolts have Level 1 Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | Update the ring number as ring 289 has no steel channel and channel bolt at 1 o’clock | yes |  |  |  |  | 252d5cab-5cde-4f46-9221-72152185a303,db961418-d8b6-434f-a6a0-045b65f1a64f | , | https://web.fulcrumapp.com/photos/view?photos=252d5cab-5cde-4f46-9221-72152185a303%2Cdb961418-d8b6-434f-a6a0-045b65f1a64f | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
ebd7ed5c-1d8f-4b20-9c2e-738a72e04b65 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:44:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 290 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76372 |  | 8517 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Repair Verified | 25/01/2023 |  | 17/10/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Loose Bolt |  | Loose Bolt | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 290, 3 o'clock. Channel Anchor Bolts. | Rupture | Rupture |  | Loose nut at channel anchor bolts |  | Loose nut at channel anchor bolts | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Repair verified LC 9/10/24 | Financial | Priority: P3 |  |  |  | Retighten the nuts | Remediation Crew | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the existing condition | no |  |  |  |  | 368c39a4-a388-48a7-b357-a9c31a5a3c7b,d1a47002-5e2a-41ce-9eb3-e1c61691df2e | , | https://web.fulcrumapp.com/photos/view?photos=368c39a4-a388-48a7-b357-a9c31a5a3c7b%2Cd1a47002-5e2a-41ce-9eb3-e1c61691df2e | Steel | Channel Bracket-Bolt | Loose
8f04aedb-d0a9-406d-b694-ab05515f9791 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:52:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 290 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 76373 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 290, 4 O'Clock, Segmented Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint seal has leak Inactive at time of inspection. |  | Circle joint seal has leak Inactive at time of inspection. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for HSE | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | No accessed, | [8 empty] | Concrete | Circular Joint | Leaks
866a4160-f977-485d-9af5-f96cbd84760f | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 18:04:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 291 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26935 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 291, 11 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights, Confined Space | Condition Monitoring Competent Supervisor |  |  | Grout injection hole had inactive leak | no |  |  |  |  | a92f87a7-38f6-401f-b4cd-f32a293b9e6f |  | https://web.fulcrumapp.com/photos/view?photos=a92f87a7-38f6-401f-b4cd-f32a293b9e6f | Concrete | Grout Hole | Leaks |  | Not Reinforcement
302cdd08-435a-4777-b8a3-7ab70a380644 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:49:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 291 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 88629 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Possible (Failure within 5 Years) |  | Ring 291, 3 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 300mm x 150mm. |  | Concrete shell segment has drummy concrete over an area of 300mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | Walkway | Excavation | Standard Repair Detail Competent Supervisor | KP |  | Drummy/ delaminated grout along the circumferential joint still present | no |  |  |  |  | 1dda8dba-2a34-4557-9234-14a5ffa825ad,89375cec-fb2a-4343-9167-0b88c2c71f68 | , | https://web.fulcrumapp.com/photos/view?photos=1dda8dba-2a34-4557-9234-14a5ffa825ad%2C89375cec-fb2a-4343-9167-0b88c2c71f68 | Concrete | Circular Connection,Circular Joint | Drummy
2ec1de52-15ba-41ef-8ecb-0d13e0613e30 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:52:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 291 | 5 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 76374 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 291, 4 O'Clock, Hydrophyllic Joint Seal (Circle Joint). | Failure to seal joint | Failure to seal joint |  | Circle joint seal has Leak Inactive at time of inspection. |  | Circle joint seal has Leak Inactive at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | HSE | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | On-Line | No | - | - | Condition Monitoring Competent Supervisor | KP |  | Drummy/ delimitated grouting was present with inactive leak | yes |  |  |  |  | 57231063-4ca6-49e1-8229-e08e4303a7ab,28e08f56-0435-46aa-8553-45ed42ae25d8 | , | https://web.fulcrumapp.com/photos/view?photos=57231063-4ca6-49e1-8229-e08e4303a7ab%2C28e08f56-0435-46aa-8553-45ed42ae25d8 | Concrete | Circular Joint | Drummy,Leaks
76e60c0e-2476-4631-96e8-b981c822a313 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:56:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 292 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27204 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 292, 3 O'Clock, Channel Anchor Bolts |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still had loose nut | no |  |  |  |  | f7e7e6d6-33ae-4482-8986-3d811d2ce19f |  | https://web.fulcrumapp.com/photos/view?photos=f7e7e6d6-33ae-4482-8986-3d811d2ce19f | Steel | Channel Bracket-Bolt | Loose
b2f7fbcf-ff32-490c-8943-4e695326caed | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:25:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 292 | 8 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 88630 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5135 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 292, 8 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Drummy concrete on radial joint over areas 250mm x 250mm and 150mm x 200mm | no |  |  |  |  | 6c02b533-5c64-4043-944c-10b9df1c96c6,da5377b5-88a7-494f-ae76-70b2c09198fc,9a464088-4734-4e53-a09b-90a640ae6146,6035afeb-0339-48bb-852d-e060065d0d02 | ,,, | https://web.fulcrumapp.com/photos/view?photos=6c02b533-5c64-4043-944c-10b9df1c96c6%2Cda5377b5-88a7-494f-ae76-70b2c09198fc%2C9a464088-4734-4e53-a09b-90a640ae6146%2C6035afeb-0339-48bb-852d-e060065d0d02 | Concrete | Radial Joint | Drummy
fe77b0e5-0822-4048-998b-3ef1e2935e31 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:32:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 292 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36617 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 292, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | RT |  | Dry leak chloride induced. Grout injection hole has built of chloride inside the hole. | no |  |  |  |  | 557e8648-7ffe-4eed-b134-3b15754ce877,ef019a7b-7865-4db7-882e-1d2d5329e3d2 | , | https://web.fulcrumapp.com/photos/view?photos=557e8648-7ffe-4eed-b134-3b15754ce877%2Cef019a7b-7865-4db7-882e-1d2d5329e3d2 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
a37d00e2-758e-4b43-8d43-b3d26ea055a7 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:00:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 292 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36618 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3406 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 292, 5 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | Anchor bolt at 5 o’clock and 7 o’clock is heavily corroded and steel channel plates are also corroding | yes |  |  |  |  | 29a9b38f-2192-4814-abb3-8fef306c7dc8,e36e606f-0359-4599-b55b-d41962891819,1f5d1cd8-288d-4d8a-9480-a94f1d128a85 | ,, | https://web.fulcrumapp.com/photos/view?photos=29a9b38f-2192-4814-abb3-8fef306c7dc8%2Ce36e606f-0359-4599-b55b-d41962891819%2C1f5d1cd8-288d-4d8a-9480-a94f1d128a85 | Steel | Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | not channel bracket
774cc9c2-f01b-48bd-828d-f7f40f490acb | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:07:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 293 | 5 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88631 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5165 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 293, 5 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Delaminated/ drummed grout along the circumferential joint still present | no |  |  |  |  | 1e0d5587-f077-414b-9fd7-c7cb4797c7e9,05a44d5a-3589-428e-be64-612246cb1e14 | , | https://web.fulcrumapp.com/photos/view?photos=1e0d5587-f077-414b-9fd7-c7cb4797c7e9%2C05a44d5a-3589-428e-be64-612246cb1e14 | Concrete | Circular Connection,Circular Joint | Drummy
5b63615b-81cb-4ed5-ac85-dea6c62dbb05 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:05:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 294 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36621 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 294, 12 O'clock, Ring (Segmental Concrete) Damage Affecting Single Ring | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Vertical crack due to construction approximately 0.5mm wide and 350mm long. Drummy Concrete over an area of 150mm x 350mm either due to corrosion of embedded steel or poor bond. |  | Vertical crack due to construction approximately 0.5mm wide and 350mm long. Drummy Concrete over an area of 150mm x 350mm either due to corrosion of embedded steel or poor bond. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | KP |  | Delaminated/ drumminess in grout as well as cracks still appear to be of same size | no |  |  |  |  | 1f29b358-097a-4de9-b47d-a9d59346b7f5,9e421fc1-1ebc-494b-863a-930cf6af00fc | , | https://web.fulcrumapp.com/photos/view?photos=1f29b358-097a-4de9-b47d-a9d59346b7f5%2C9e421fc1-1ebc-494b-863a-930cf6af00fc | Concrete,Steel |  | Crack,Drummy |  | Not Reinforcement
a1577f0f-0cbc-42fa-b780-376898c374ee | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:07:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 294 | 5 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88632 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.519 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 294, 5 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | Drummy/ delaminated area is the same. Concrete has cracked and spalling. | yes | no |  |  |  | 6cb34ab9-9147-44b3-bac5-23827e7efae0,1b0f79e0-1e23-479d-b391-0cccca19292f,b3365833-824e-48d4-8f72-3d19c22a5f4d | ,, | https://web.fulcrumapp.com/photos/view?photos=6cb34ab9-9147-44b3-bac5-23827e7efae0%2C1b0f79e0-1e23-479d-b391-0cccca19292f%2Cb3365833-824e-48d4-8f72-3d19c22a5f4d | Concrete | Circular Joint | Crack,Drummy,Surface Damage
c3ca9ffc-f251-47d8-858a-8f12d12df402 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:07:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 295 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 76376 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 295, 4 O'Clock, Segmented Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint seal has Leak Inactive at time of inspection. |  | Circle joint seal has Leak Inactive at time of inspection. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor | DR |  | Leak is still inactive. No change to condition. | no | yes |  |  |  | 63abbc0b-14f5-4160-bd29-34b6b961d764,fc4ddbda-dc0a-4b39-bf56-811baa7eb125 | , | https://web.fulcrumapp.com/photos/view?photos=63abbc0b-14f5-4160-bd29-34b6b961d764%2Cfc4ddbda-dc0a-4b39-bf56-811baa7eb125 | Concrete | Circular Joint | Leaks
b0f12107-c57d-4302-8445-20f585e7433d | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:37:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 296 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76377 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8341 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 296, 3 O'Clock, Channel Anchor Bolts |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Anchor nut was loose at the time of inspection. | no |  |  |  |  | 0e22dfed-c6c8-4616-bedb-ed353ee0ad3e,aa1a73be-f9c1-4145-b62a-d6c3cbf8c4be | , | https://web.fulcrumapp.com/photos/view?photos=0e22dfed-c6c8-4616-bedb-ed353ee0ad3e%2Caa1a73be-f9c1-4145-b62a-d6c3cbf8c4be | Steel | Channel Bracket-Bolt | Loose
f1d5b2fd-dcdb-4419-9943-2d1a12e52527 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:34:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 296 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27468 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 296, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The base plate is as per previous inspection. the nut has advanced corrosion with the nut fully corrected. Medium priority. | yes | no |  | no |  | 967e6abe-cd67-4b15-a574-37b05204b15b,656ae6cf-af19-43dd-98db-2af7854c1f87,6169d0fe-6ee4-43ee-aa85-1b369239e1ec,d7f122f5-881b-45cf-a33b-170e83a25715 | 7 o'clock base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=967e6abe-cd67-4b15-a574-37b05204b15b%2C656ae6cf-af19-43dd-98db-2af7854c1f87%2C6169d0fe-6ee4-43ee-aa85-1b369239e1ec%2Cd7f122f5-881b-45cf-a33b-170e83a25715 | Steel | Walkway Support,Walkway Support-Bolt,Conveyor Support,Conveyor Support-Bolt | Corrosion-Heavy |  | Not channel bracket. Walkway support and bolt. Conveyor SUpport and Bolt
375d7c65-37d4-419b-820f-a46d4ee606d4 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 03:20:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 296 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27469 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 296,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel presents surface corrosion with loss of section up to 1mm. The bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. | yes | no |  | no |  | 1ddc880f-b8e9-4326-a350-d003849fe5bd,d89a6669-7eb2-4977-adb9-924cc54bf0c8,c48a53bf-76e9-45b8-b78d-e067dcbe2bce | 5 o'clock structural steel general condition ,Bolt condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=1ddc880f-b8e9-4326-a350-d003849fe5bd%2Cd89a6669-7eb2-4977-adb9-924cc54bf0c8%2Cc48a53bf-76e9-45b8-b78d-e067dcbe2bce | Steel | Walkway Support,Walkway Support-Bolt,Conveyor Support,Conveyor Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Not channel bracket. Walkway support and bolt. Conveyor SUpport and Bolt
6a831240-31fb-4717-b3a6-6d29f6ea1730 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:07:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 298 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 88634 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5253 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 298, 11 O'Clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is loose |  | One channel anchor bolt is loose | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | The bolt is still loose at 10 o’clock position | no |  |  |  |  | beb50eba-9b56-49d2-b512-f6f4ed606596,76e0b69b-73df-4de2-82e7-4a04150627f4 | , | https://web.fulcrumapp.com/photos/view?photos=beb50eba-9b56-49d2-b512-f6f4ed606596%2C76e0b69b-73df-4de2-82e7-4a04150627f4 | Steel | Channel Bracket-Bolt | Loose
d64e8236-46a0-4b6a-9a7f-ece0d4eb8503 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:14:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 298 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88633 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5204 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 298, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack on and around repair patch up to 0.4mm in width. |  | Crack on and around repair patch up to 0.4mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Crack is present 0.4mm wide. | no |  |  |  |  | 2d3e3fe4-1b86-48e1-9db8-1ede446f1b85,25b36095-941e-4c3b-8214-49cc469768e0,791c9caa-0bea-42f9-a3c7-87e51a2ce15a | ,, | https://web.fulcrumapp.com/photos/view?photos=2d3e3fe4-1b86-48e1-9db8-1ede446f1b85%2C25b36095-941e-4c3b-8214-49cc469768e0%2C791c9caa-0bea-42f9-a3c7-87e51a2ce15a | Concrete | Circular Joint | Crack
ac03f4a6-05c0-48c4-8d41-7293e9f5653c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 03:06:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 300 | 4 | Steel Channel Bracket | Steel Channel Bracket |  | 27470 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 300, 4 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of walkway support. |  | Level 3 to Level 4 corrosion at anchor bolts of walkway support. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel has surface corrosion with loss of section up to 1mm. Bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. | yes | no |  | no |  | 7f8be584-ffa1-4724-8b0e-38f6086d77cd,33824783-5ebf-4a48-9404-23bdef094362 | 5 o'clock structural steel general condition ,Bolt condition | https://web.fulcrumapp.com/photos/view?photos=7f8be584-ffa1-4724-8b0e-38f6086d77cd%2C33824783-5ebf-4a48-9404-23bdef094362 | Steel | Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Walkway support and bolt
f50bf748-5e29-4e40-87ff-14d2816a833d | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:18:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 300 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27471 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 300,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The base plate is as per previous inspection. The bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. | yes | no |  | no |  | 6e55c064-962a-4629-8f9a-f379019bb841,99c7cc3c-460f-42e2-a57b-6796df1b5a01,c755a7a3-3801-404f-84df-963615bbb130,c80e8ad9-50ae-4805-b0e4-500fb4054e50 | 7 o'clock base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=6e55c064-962a-4629-8f9a-f379019bb841%2C99c7cc3c-460f-42e2-a57b-6796df1b5a01%2Cc755a7a3-3801-404f-84df-963615bbb130%2Cc80e8ad9-50ae-4805-b0e4-500fb4054e50 | Steel | Conveyor Support,Conveyor Support-Bolt | Corrosion-Heavy |  | Conveyor Support and bolt not channel bracket
ceb45e26-af7b-4a2c-9ba8-41167b68ab9c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 14 |  |  |  | 2025-07-28 17:51:41 AEST | 2025-07-29 16:08:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 295 | 12 |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Delaminated/ Drummed grout 50x50mm. | [5 empty] | 9018ffc6-41b0-4c27-a94a-8677b2d478ec |  | https://web.fulcrumapp.com/photos/view?photos=9018ffc6-41b0-4c27-a94a-8677b2d478ec | Concrete | Radial Joint | Drummy
5b0a96d9-9e07-4dbd-b2fa-a7b9cab35252 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 14 |  |  |  | 2025-07-28 17:55:22 AEST | 2025-07-28 17:57:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 295 | 12 o’clock, 11 o’clock,10 o’clock | [59 empty] | KP |  | Steel channel has coating delamination and some surface corrosion | [5 empty] | 1f92197d-eb9e-42f7-9337-25c556921f76 |  | https://web.fulcrumapp.com/photos/view?photos=1f92197d-eb9e-42f7-9337-25c556921f76 | Steel | Channel Bracket | Coating Failure,Corrosion-Surface,Drummy |  | Channel Bracket
214503c4-683a-436f-b064-0fd61b1b792f | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 14 |  |  |  | 2025-07-28 17:59:35 AEST | 2025-07-28 18:00:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 293 | 10 o’clock |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Delaminated/ drummy grout 100x200 mm | [5 empty] | a34d86d2-5225-4cd5-9d5c-bcc14836ca18 |  | https://web.fulcrumapp.com/photos/view?photos=a34d86d2-5225-4cd5-9d5c-bcc14836ca18 | Concrete | Radial Joint | Drummy
f714bdeb-f9f5-4d2e-962e-bace9fdd63dd | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 14 |  |  |  | 2025-07-28 18:07:35 AEST | 2025-07-28 18:08:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 289 | 12 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Delaminated/Drummy grout 50x50mm | [5 empty] | 6538084f-e434-4fca-a471-c323cb6e2401 |  | https://web.fulcrumapp.com/photos/view?photos=6538084f-e434-4fca-a471-c323cb6e2401 | Concrete | Circular Joint | Drummy
752b8e21-4c04-41d5-98d0-64d1121aab5a | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 14 |  |  |  | 2025-07-28 18:11:29 AEST | 2025-07-28 18:12:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | 288 | 11 |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | 2x drummy / delaminated grout 50x50mm each | [5 empty] | 8c0818ce-7610-46f1-b26b-60fb786c509e |  | https://web.fulcrumapp.com/photos/view?photos=8c0818ce-7610-46f1-b26b-60fb786c509e | Concrete | Radial Joint | Drummy
6044a993-c776-418e-ab5d-04dc9b36be93 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 14 |  |  |  | 2025-07-28 18:15:10 AEST | 2025-07-28 18:17:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 286 | 10 |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Fine 0.3mm hairline crack along the grout | [5 empty] | 82d60bcf-82c1-4678-aec9-fe6c146a8984 |  | https://web.fulcrumapp.com/photos/view?photos=82d60bcf-82c1-4678-aec9-fe6c146a8984 | Concrete | Radial Joint | Crack
bd6f30d9-b70e-437a-8385-2e1b2a876538 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 14 |  |  |  | 2025-07-28 18:17:27 AEST | 2025-07-28 18:18:16 AEST | 30011704-user5@smec.com | james.stone@smec.com | 285 | 11 |  | Grout Injection Hole | [57 empty] | KP |  | Active leak from grout injection hole | [5 empty] | b4885c26-3776-4005-9c96-cb3dfc339024 |  | https://web.fulcrumapp.com/photos/view?photos=b4885c26-3776-4005-9c96-cb3dfc339024 | Concrete | Grout Hole | Leaks
85f112eb-c8fe-4f95-b87e-a375de4d859f | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 15 |  |  |  | 2025-07-28 17:43:18 AEST | 2025-07-28 17:46:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 276 | 11 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Grout delamination / Drummy concrete at radial joint over an area of 100mm x 150mm. Priority medium | [5 empty] | 58d94b1d-63d8-4613-b8f5-6842a909bbac,a9ad4496-599b-4596-92c5-b53441fccc62,d3535aaa-4918-4678-8594-d397eceeb28c | ,, | https://web.fulcrumapp.com/photos/view?photos=58d94b1d-63d8-4613-b8f5-6842a909bbac%2Ca9ad4496-599b-4596-92c5-b53441fccc62%2Cd3535aaa-4918-4678-8594-d397eceeb28c | Concrete | Circular Joint,Radial Joint | Drummy
fe787dc1-5012-4d53-befd-ea7edd4412a6 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 15 |  |  |  | 2025-07-28 17:47:37 AEST | 2025-07-28 17:51:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 276-277 | 11 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Offset of 4 mm in between rings 276-277 | [5 empty] | 44df4089-6bbd-4321-8432-074eb743ceb4,c0644986-81b6-40fa-8210-080eec0a9c8f | , | https://web.fulcrumapp.com/photos/view?photos=44df4089-6bbd-4321-8432-074eb743ceb4%2Cc0644986-81b6-40fa-8210-080eec0a9c8f | Concrete | Circular Joint | Displacement
173eb08e-b5f2-475f-8590-0b139496da8a | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6 |  |  |  | 2025-07-29 11:06:57 AEST | 2025-07-29 11:08:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 274 | 4 o’clock , 3 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Steel channel and bolt are corroding and coating delaminating | [5 empty] | d707d2e4-16c2-42e0-b5f3-daba78b165d9,e103955f-6ebd-4f15-9098-dfed4f64d31b | , | https://web.fulcrumapp.com/photos/view?photos=d707d2e4-16c2-42e0-b5f3-daba78b165d9%2Ce103955f-6ebd-4f15-9098-dfed4f64d31b | Steel | Channel Bracket,Channel Bracket-Bolt | Coating Failure,Drummy
65d4af45-ca9f-4f7a-af8e-1fd385646c92 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6 |  |  |  | 2025-07-29 11:26:46 AEST | 2025-07-29 11:29:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 276 | 4 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The steel support , supporting the walkway is severely corroded | [5 empty] | 0530da59-12ad-4307-9df0-3319327f7b5c |  | https://web.fulcrumapp.com/photos/view?photos=0530da59-12ad-4307-9df0-3319327f7b5c | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
bd093e21-5010-47ee-b45a-2ccdaf8b195a | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6 |  |  |  | 2025-07-29 11:39:37 AEST | 2025-07-29 11:40:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 278 | 1 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Delaminated/ drummy grout along the circumferential joint 50x 150mm | [5 empty] | 6e0e0da9-8167-48e4-ad21-ed18a52fe8d1 |  | https://web.fulcrumapp.com/photos/view?photos=6e0e0da9-8167-48e4-ad21-ed18a52fe8d1 | Concrete | Circular Connection,Circular Joint | Drummy
c5cf8462-bd8f-47e6-af25-e6de23021d9a | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6 |  |  |  | 2025-07-29 12:23:08 AEST | 2025-07-29 12:24:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | 284 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Delaminated/ drummy grout along the circumferential joint 100x100mm | [5 empty] | 09337a34-62f6-42b4-b5f0-bf45af110750,9f5404da-fd04-4b3a-9b4c-7e44f2dfcf3c | , | https://web.fulcrumapp.com/photos/view?photos=09337a34-62f6-42b4-b5f0-bf45af110750%2C9f5404da-fd04-4b3a-9b4c-7e44f2dfcf3c | Concrete | Circular Connection,Circular Joint | Drummy
72dd2611-6cc5-462c-8576-8a24badd22c6 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6 |  |  |  | 2025-07-29 12:24:59 AEST | 2025-07-29 12:26:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 284 | 3 o’clock, 2 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Steel channel had surface corrosion | [5 empty] | 28a82f01-cd5f-42b4-97bc-848f18b48719,721cdb56-a709-42bd-beee-75c10d67924a | , | https://web.fulcrumapp.com/photos/view?photos=28a82f01-cd5f-42b4-97bc-848f18b48719%2C721cdb56-a709-42bd-beee-75c10d67924a | Steel | Channel Bracket | Corrosion-Surface
26725aa2-3a23-46bb-b825-a42cdf520b47 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 5 |  |  |  | 2025-07-29 17:45:01 AEST | 2025-07-29 17:47:35 AEST | 30011704-user5@smec.com | james.stone@smec.com | 300 | 2 |  | Channel Anchor Bolts | [57 empty] | RT |  | Low surface corrosion on the channel anchor bolt. | [5 empty] | 2083d474-cffe-480b-a24e-b4ba8bd04e30,96056373-70fc-4a09-819d-50f21dbeb439 | , | https://web.fulcrumapp.com/photos/view?photos=2083d474-cffe-480b-a24e-b4ba8bd04e30%2C96056373-70fc-4a09-819d-50f21dbeb439 | Steel | Channel Bracket-Bolt | Corrosion-Surface
be2571ff-e060-44f4-89ed-7ef86d63d1e1 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6 |  |  |  | 2025-07-29 13:12:59 AEST | 2025-07-29 13:17:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 276 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Base plate and bolts are severely corroded | [5 empty] | 0147a851-4a20-45e9-a68c-b08434bed53d,ba5e1e8b-7b45-463e-ae50-7e9008e53a21 | , | https://web.fulcrumapp.com/photos/view?photos=0147a851-4a20-45e9-a68c-b08434bed53d%2Cba5e1e8b-7b45-463e-ae50-7e9008e53a21 | Steel | Centre Support,Centre Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Centre Support and Bolt not channel bracket
32ba1fc2-7888-473a-9bc0-7c73fe6cbc28 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6 |  |  |  | 2025-07-29 13:38:22 AEST | 2025-07-29 13:41:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 271 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Advanced corrosion to the walkway steel member due to the constant water logging and sludge buildup . High priority |  | yes |  |  |  | cd0ac093-53f7-47e0-8ef9-c489e5c8a939,d5d2868d-a5bc-4baa-b630-5eccb25ba921,82b8af7d-136c-45c7-8d54-3ec5d908ab92,db19c5fb-3079-4109-bbeb-6328014fa909,28ce7ec7-3e91-4ea0-a6e1-1bf4c256332b | ,,,, | https://web.fulcrumapp.com/photos/view?photos=cd0ac093-53f7-47e0-8ef9-c489e5c8a939%2Cd5d2868d-a5bc-4baa-b630-5eccb25ba921%2C82b8af7d-136c-45c7-8d54-3ec5d908ab92%2Cdb19c5fb-3079-4109-bbeb-6328014fa909%2C28ce7ec7-3e91-4ea0-a6e1-1bf4c256332b | Steel | Centre Support,Centre Support-Bolt | Corrosion-Heavy |  | Centre Support and Bolt not channel bracket
96137c3a-2f6b-4461-9283-be8578cc9c45 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 9 |  |  |  | 2025-07-29 11:06:55 AEST | 2025-07-29 11:09:24 AEST | 30011704-user5@smec.com | james.stone@smec.com | 293 | 10 |  | Hydrophilic Joint Seal (Radial Joint) | [57 empty] | RT |  | Drummy concrete on radial joint over area of 100mm x 100mm. Low priority | [5 empty] | 511d7a56-a6ef-417f-9335-f55776a4565a,20ac648e-eea3-412b-8ed5-1a4c893b80b3 | , | https://web.fulcrumapp.com/photos/view?photos=511d7a56-a6ef-417f-9335-f55776a4565a%2C20ac648e-eea3-412b-8ed5-1a4c893b80b3 | Concrete | Radial Joint | Drummy
c7147d9a-c400-4faf-8bdc-45ca40e2d73f | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 9 |  |  |  | 2025-07-29 11:33:36 AEST | 2025-07-29 11:37:39 AEST | 30011704-user5@smec.com | james.stone@smec.com | 290 | 8 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Drummy concrete on circular joint over an area of 150mm x 200mm. | [5 empty] | 5e4596ad-be0d-4a15-aed7-94e162cf4ac0,fea8d588-e4fe-4a14-8b63-16d14f7fb72f | , | https://web.fulcrumapp.com/photos/view?photos=5e4596ad-be0d-4a15-aed7-94e162cf4ac0%2Cfea8d588-e4fe-4a14-8b63-16d14f7fb72f | Concrete | Circular Connection,Circular Joint | Drummy
391f4217-c419-438c-b3c9-b06d3c539da6 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 9 |  |  |  | 2025-07-29 11:49:17 AEST | 2025-07-29 11:54:50 AEST | 30011704-user5@smec.com | james.stone@smec.com | 288 | 10 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Grout delamination / Drummy concrete at circular joint over an area of 100mm x 150mm. | [5 empty] | f27278c4-c57d-4c57-b6ce-4ab71419327a,5e6a594d-85dc-4a16-a8b4-25bb41403729 | , | https://web.fulcrumapp.com/photos/view?photos=f27278c4-c57d-4c57-b6ce-4ab71419327a%2C5e6a594d-85dc-4a16-a8b4-25bb41403729 | Concrete | Circular Connection,Circular Joint | Drummy
91bc0629-a27e-433a-a46c-bad48bcd54ab | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 9 |  |  |  | 2025-07-29 12:23:59 AEST | 2025-07-29 12:31:40 AEST | 30011704-user5@smec.com | james.stone@smec.com | 284 | 9 |  |  | Steel support structure | [56 empty] | RT |  | Beam support bolts have moved and sheared the holes. | [5 empty] | b7f05b3b-0d76-46a8-9df1-75674436e53a,577e1f4f-a368-41e5-bd1a-ec5dcdc453bd | , | https://web.fulcrumapp.com/photos/view?photos=b7f05b3b-0d76-46a8-9df1-75674436e53a%2C577e1f4f-a368-41e5-bd1a-ec5dcdc453bd | Steel | Centre Support
405e95ef-ccb2-4177-ad89-acde3c169381 | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 4 |  |  |  | 2025-07-29 16:11:25 AEST | 2025-07-29 16:12:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 300 | 11 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Delaminated/Drummy grout along circumferential joints | [5 empty] | 929d92c4-c835-4340-a76a-f8e6b516cce2 |  | https://web.fulcrumapp.com/photos/view?photos=929d92c4-c835-4340-a76a-f8e6b516cce2 | Concrete | Circular Connection,Circular Joint | Drummy
9e49c1a4-36c0-4bc9-8a20-53c58a9fad7f | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 6e355a6c-8469-4ed4-a402-41fb8116b58c | 9 |  |  |  | 2025-07-29 13:45:34 AEST | 2025-07-29 13:48:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 273 | 8 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Grout delamination / Drummy concrete at circular joint over an area of 50mm x150mm | [5 empty] | 6047b9ce-19f8-499f-8484-bac63e36b0fb,eed84312-0d94-45b5-8152-65db6f929c62 | , | https://web.fulcrumapp.com/photos/view?photos=6047b9ce-19f8-499f-8484-bac63e36b0fb%2Ceed84312-0d94-45b5-8152-65db6f929c62 | Concrete | Circular Connection,Circular Joint | Drummy
a85b1ca0-3ee3-40b9-9537-7732fd084eef | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:27:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 301 | 7 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88635 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5274 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 301, 7 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect condition is as per previous inspection. The defect is considered superficial with no structural implication. Low priority. | no | yes |  | no |  | bbee1663-05ef-4592-9e32-1c7a1a742138 |  | https://web.fulcrumapp.com/photos/view?photos=bbee1663-05ef-4592-9e32-1c7a1a742138 | Concrete | Circular Joint | Drummy
1cb3b75f-e5fe-488b-a51a-4efa725eabec | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 | -20.3216 | 118.5853 | POINT (118.5853257 -20.3216462) | 2025-05-27 20:13:18 AEST | 2025-07-29 17:37:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 304 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76379 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8376 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 304, 3 O'Clock, Channel Anchor Bolts |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Anchor bolt is still loose at 3 o’clock on steel channel. | no |  |  |  |  | 42ae7c20-68a1-4fa0-ac6d-decc84c5ea31,c81bf7ed-893c-4b9c-9370-60b5940ca372 | , | https://web.fulcrumapp.com/photos/view?photos=42ae7c20-68a1-4fa0-ac6d-decc84c5ea31%2Cc81bf7ed-893c-4b9c-9370-60b5940ca372 | Steel | Channel Bracket-Bolt | Loose
0c21f569-34d2-45b9-86ee-2461d52a847d | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:14:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 304 | 4 | Steel Channel Bracket | Steel Channel Bracket |  | 27472 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 304, 4 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 to Level 3 corrosion at anchor bolts of walkway support. |  | Level 2 to Level 3 corrosion at anchor bolts of walkway support. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel has surface corrosion with loss of section up to 1mm. The bolt and nut has advanced corrosion with the nut fully corrected. Medium priority. | yes | no |  | no |  | f5041e4b-e121-41cb-8219-0530fc931a1c,693b9643-c34a-476b-98d1-3faf95607462 | 5 o'clock structural steel general condition ,Bolt condition | https://web.fulcrumapp.com/photos/view?photos=f5041e4b-e121-41cb-8219-0530fc931a1c%2C693b9643-c34a-476b-98d1-3faf95607462 | Steel | Channel Bracket,Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface
f7f4b61c-c373-41ff-b250-4df75c4691fe | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:31:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 304 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27473 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 304,7 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock base plate is as per previous inspection. The bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. | yes | no |  | no |  | 87c433f7-0a74-46ee-b038-2433a7b336dd,565041c1-71d6-4df5-a6a8-45ed6a726f60,b3623c9a-3dbd-4c6d-b568-0efcf2608302,c14ab28f-9232-4f8d-ab4f-e7ab3dad17c0 | 7 o'clock base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=87c433f7-0a74-46ee-b038-2433a7b336dd%2C565041c1-71d6-4df5-a6a8-45ed6a726f60%2Cb3623c9a-3dbd-4c6d-b568-0efcf2608302%2Cc14ab28f-9232-4f8d-ab4f-e7ab3dad17c0 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
4c436536-70dd-43a7-b43c-4fa566e551f6 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 02:41:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 305 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 76380 |  | 6655 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 18/06/2022 |  | 4/04/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 305, 4 o'clock. Segmented Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint seal has Leak Inactive at time of inspection. |  | Circle joint seal has Leak Inactive at time of inspection. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Monitor leak condition at the next inspection if it is still dry then monitor. If active the update to P2 and fixed | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor | DR |  | Leak is still inactive at time of inspection. No change to condition. | no | yes |  |  |  | 7d40a759-1a38-40cd-9e17-7097527a1eac |  | https://web.fulcrumapp.com/photos/view?photos=7d40a759-1a38-40cd-9e17-7097527a1eac | Concrete | Circular Joint | Leaks
d26532f4-aa72-4391-97fd-a5eefe6099bf | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:33:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 306 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26938 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 306, 2 O'Clock, Segmental Concrete | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Active leak within segmental concrete adjacent the circle joint seal. |  | Active leak within segmental concrete adjacent the circle joint seal. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | KP |  | Apprears to have active chloride buildup | no |  |  |  |  | 98365518-0dda-4d4a-9acb-055d3ec1f56e |  | https://web.fulcrumapp.com/photos/view?photos=98365518-0dda-4d4a-9acb-055d3ec1f56e | Concrete | Circular Joint | Leaks |  | Not Reinforcement
5be85e19-03dd-42fb-916a-67cc2a7b0204 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:31:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 306 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 88636 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 306, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 400mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 400mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Safety | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | Excavation | Standard Repair Detail Competent Supervisor | KP |  | Delaminated/ drummed grout along radial joint same size as found previously. | no |  |  |  |  | 3f206f30-18ea-4fc4-8695-df4bd006ef99,1813858f-c37b-41ec-bfef-e2f41f8a5009,a739fbb5-c876-4b28-8163-e7e72adc468c | ,, | https://web.fulcrumapp.com/photos/view?photos=3f206f30-18ea-4fc4-8695-df4bd006ef99%2C1813858f-c37b-41ec-bfef-e2f41f8a5009%2Ca739fbb5-c876-4b28-8163-e7e72adc468c | Concrete | Radial Joint | Drummy
e4ab3e64-b868-46a7-87c4-c4f46aa5b0bf | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:22:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 306 | 3 - consider removing this defect | Steel Channel Bracket | Steel Channel Bracket |  | 26937 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 306,3 O'Clock,Ducting,Still existing in 2017. |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | The cable tray has been replaced | yes |  |  |  |  | fa6d1484-57f2-449a-a095-6820310a1628 |  | https://web.fulcrumapp.com/photos/view?photos=fa6d1484-57f2-449a-a095-6820310a1628 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
992927d9-562d-4181-b861-94bd96f51790 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:03:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 307 | 8 | Grout Injection Hole | Grout Injection Hole |  | 101841 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 19/09/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 307, 8 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. The plug bolt is in good condition. | no | yes |  | no |  | b08f1527-4744-4806-84d6-bbc6e01b3109,9072c0db-8bde-4d95-8c60-521a3bb87a3c | , | https://web.fulcrumapp.com/photos/view?photos=b08f1527-4744-4806-84d6-bbc6e01b3109%2C9072c0db-8bde-4d95-8c60-521a3bb87a3c | Concrete | Grout Hole | Leaks
63a6fca8-3015-4a22-962e-0b95f9e7456d | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:23:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 308 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26940 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 308, 11 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection point had inactive leak, no change in condition | no |  |  |  |  | 7c5b5ea2-de55-4a2d-af17-7aba1f6d403f,f1f93deb-073b-4b28-bf9c-53fe71bc842b,d7867439-4882-473a-8161-eb01ca361781,b4be9ecf-3c99-4af6-8980-395251763048 | ,,, | https://web.fulcrumapp.com/photos/view?photos=7c5b5ea2-de55-4a2d-af17-7aba1f6d403f%2Cf1f93deb-073b-4b28-bf9c-53fe71bc842b%2Cd7867439-4882-473a-8161-eb01ca361781%2Cb4be9ecf-3c99-4af6-8980-395251763048 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
24c06c7e-f597-451b-8d6f-b70fbd6316df | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 02:37:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 308 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88637 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.532 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 308, 4 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Area of drummy concrete is the same. Concrete has cracked and broken down around circular joint. High priority | yes | no |  | no |  | 19465178-09a2-48e2-a1da-dacdbf32270f |  | https://web.fulcrumapp.com/photos/view?photos=19465178-09a2-48e2-a1da-dacdbf32270f | Concrete | Circular Connection,Circular Joint | Crack,Drummy
d14c51fb-9691-4d8b-958e-373da7aa22cc | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:56:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 308 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36624 |  | 8517 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 25/01/2023 |  | 17/10/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring: 308, 9 O'clock: Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Non-active leak and excessive corrosion around the leak. |  | Non-active leak and excessive corrosion around the leak. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. Duplicate of defect 26940. Marked as repair verified to manage duplicate defects LC 9/10/24 | HSE | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Engineering Repair Methodology Required Competent Engineer | RT |  | Leak inactive at the time of inspection. Condition unchanged | no |  |  |  |  | 7673afaa-2fb5-475b-8396-16ed16e2fd70,799f2fc0-f1a4-4cb4-a542-1a942cb2694d | , | https://web.fulcrumapp.com/photos/view?photos=7673afaa-2fb5-475b-8396-16ed16e2fd70%2C799f2fc0-f1a4-4cb4-a542-1a942cb2694d | Concrete | Grout Hole | Leaks |  | Not Reinforcement
427c6941-ec2e-4eeb-9e22-746149c58990 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:12:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 308 | 3 - consider removing this defect | Steel Channel Bracket | Steel Channel Bracket |  | 27158 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 308,3 O'Clock,Ducting,New Defect 2017 |  |  |  | Cable tray, Class 3 - Medium corrosion |  | Cable tray, Class 3 - Medium corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Cable tray has been replaced | yes |  |  |  |  | 1f322e67-9785-4f59-9c36-5ef28960bd7b |  | https://web.fulcrumapp.com/photos/view?photos=1f322e67-9785-4f59-9c36-5ef28960bd7b | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
22014f05-be9b-4526-aa69-3b346805abc8 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:14:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 308 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27474 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 308,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock base plate is as per previous inspection. Bolts and nuts have advanced corrosion with nuts fully corroded. Medium priority. | yes | no |  | no |  | aec97744-1a69-424c-bdbc-f2578faa123a,56d4cb8f-afe1-40e8-834a-f87dc5d3ad3c,a42a03e5-1c37-4049-8a50-8974d4c6135d,a1b3dfa7-fb07-4f8e-854a-760cecad1d3c | 7 o'clock base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=aec97744-1a69-424c-bdbc-f2578faa123a%2C56d4cb8f-afe1-40e8-834a-f87dc5d3ad3c%2Ca42a03e5-1c37-4049-8a50-8974d4c6135d%2Ca1b3dfa7-fb07-4f8e-854a-760cecad1d3c | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
320fbdbb-bb00-44e8-82e9-b04ddb2c0812 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 02:33:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 309 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88638 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5335 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 309, 4 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | No change to condition of defect. | no | yes |  |  |  | 6d226709-c406-4752-92bc-93608df329de,7bdcf7c6-3d0f-413d-9450-97332f6b75bc | , | https://web.fulcrumapp.com/photos/view?photos=6d226709-c406-4752-92bc-93608df329de%2C7bdcf7c6-3d0f-413d-9450-97332f6b75bc | Concrete | Circular Joint | Drummy
3cb4ee11-0910-4b7b-89a7-ad57c97c266e | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:10:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 312 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76382 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8431 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 312, 3 O'Clock, Channel Anchor Bolts |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Nut still appears to be loose no change | no |  |  |  |  | d45a9f6c-cd5c-4373-9939-68a808b92886,a4952c5f-f3b6-413c-b5a0-b0fcb236f14e | , | https://web.fulcrumapp.com/photos/view?photos=d45a9f6c-cd5c-4373-9939-68a808b92886%2Ca4952c5f-f3b6-413c-b5a0-b0fcb236f14e | Steel | Channel Bracket-Bolt | Loose
323cd889-cd01-422a-a0e3-f18f7e9989e6 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:20:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 312 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36626 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 312, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Active at time of inspection. |  | Grout injection hole has leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | RT |  | Grout injection hole is filled with chloride, leak was in active at time of inspection. | yes |  |  |  |  | 3b4c779a-818b-4acf-8fcc-486898b8903b,04a04cfd-c61b-4ce6-87bd-7e8a248b67f0 | , | https://web.fulcrumapp.com/photos/view?photos=3b4c779a-818b-4acf-8fcc-486898b8903b%2C04a04cfd-c61b-4ce6-87bd-7e8a248b67f0 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
3a3a5b67-9188-45e7-bc07-3c776dd9f224 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 00:05:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 312 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27475 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 312, 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 corrosion at anchor bolts of conveyor support. |  | Level 3 corrosion at anchor bolts of conveyor support. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock base plate is as per previous inspection. The bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. | yes | no |  | no |  | 0c81ea9e-4ad3-4fcd-b87d-d8e85bfa973e,deef2a6a-ab1a-4322-a200-4518dc334217,5ab7f6c6-dbf5-4893-a829-de88a50c1302,f8fe791e-6195-4727-a6c1-17c54ce24825 | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=0c81ea9e-4ad3-4fcd-b87d-d8e85bfa973e%2Cdeef2a6a-ab1a-4322-a200-4518dc334217%2C5ab7f6c6-dbf5-4893-a829-de88a50c1302%2Cf8fe791e-6195-4727-a6c1-17c54ce24825 | Steel | Channel Bracket,Channel Bracket-Bolt,Conveyor Support-Bolt | Corrosion-Heavy
f4a8c734-fae0-4609-8698-11dbdfc3588b | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:05:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 313 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 36627 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3568 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 313, 1 O'clock Ring (Segmental Concrete) Damage Affecting Single Ring |  |  |  | One crack of 50mm long at the corner of concrete segment. |  | One crack of 50mm long at the corner of concrete segment. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in size and length of crack | no |  |  |  |  | d391e5ef-f6ca-4c2b-aadb-485c0d1e5bf9 |  | https://web.fulcrumapp.com/photos/view?photos=d391e5ef-f6ca-4c2b-aadb-485c0d1e5bf9 | Concrete | Corner | Crack
dc593d23-30d6-42f7-95a8-9707f6949e6c | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:07:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 313 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 88639 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5354 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 313, 2 O'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings |  |  |  | Concrete shell segment has Cracking - Shrinkage crack extending 50mm and up to 0.5 mm in width. |  | Concrete shell segment has Cracking - Shrinkage crack extending 50mm and up to 0.5 mm in width. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Appear to have no crack at 2 o’clock | [5 empty] | 350f7bee-8a71-4699-867b-9ebbe245cf47 |  | https://web.fulcrumapp.com/photos/view?photos=350f7bee-8a71-4699-867b-9ebbe245cf47 | Concrete | Middle of Panel | Crack |  | Middle of Panel
bf4e232f-77cb-4041-8520-8cbc76c10e8b | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:59:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 313 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27159 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 313, 2 O'clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Crack on patch repair of radial joint up to 0.25mm in width. |  | Crack on patch repair of radial joint up to 0.25mm in width. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Crack still present. No change to defect. | no | no | Low |  |  | bcb676c7-12e0-4c7d-8d1d-156f7369dd20,eec292ee-922b-43e0-8dfa-97323d474f3c | , | https://web.fulcrumapp.com/photos/view?photos=bcb676c7-12e0-4c7d-8d1d-156f7369dd20%2Ceec292ee-922b-43e0-8dfa-97323d474f3c | Concrete | Middle of Panel | Crack |  | MIddle of PAnel not Radial Joint
82debcef-cd5e-4e3d-8fb5-25b9bf3005d2 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:20:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 313 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 76383 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 313, 7 O'clock, Ring (Segmental Concrete)- Damage Affecting Single Rings. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Drilled hole was not filled. |  | Drilled hole was not filled. | Accelerate reinforcement corrosion. Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Accelerate reinforcement corrosion. Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Remediation Crew | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The drill hole is still not fixed. The area is dry with no signs of deterioration. Low priority. | no | yes |  | no |  | b5c027bd-9b28-4497-af18-032e0d7b25ef,95e4c96d-616f-444d-8b0b-f0c1cfb99390 | , | https://web.fulcrumapp.com/photos/view?photos=b5c027bd-9b28-4497-af18-032e0d7b25ef%2C95e4c96d-616f-444d-8b0b-f0c1cfb99390 | Concrete |  | Test Hole
29c826ab-2e9c-470a-b488-736fbb2493dd | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:43:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 314 | 10 o’clock and 11 o’clock | Channel Anchor Bolts | Channel Anchor Bolts |  | 88640 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5377 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 314, 11 O'Clock and 10 o’clock, Channel Anchor Bolts |  |  |  | Channel anchor bolts have Level 1 corrosion |  | Channel anchor bolts have Level 1 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | Steel channel anchor bolt had surface corrosion | no |  |  |  |  | 995680bb-5726-4cfa-923b-c7c0085c24f9 |  | https://web.fulcrumapp.com/photos/view?photos=995680bb-5726-4cfa-923b-c7c0085c24f9 | Steel | Channel Bracket-Bolt | Corrosion-Surface
6c294ffa-cf13-45d4-a7d3-404162d41d7b | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:41:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 314 | 11 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 76385 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8499 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 314, 11 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Crack on patch repair of radial joint up to 0.25mm in width. |  | Crack on patch repair of radial joint up to 0.25mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Crack appear to be not present when inspected | yes |  |  |  |  | 6956e963-6bf1-4e36-ae65-cc0ca29010f8 |  | https://web.fulcrumapp.com/photos/view?photos=6956e963-6bf1-4e36-ae65-cc0ca29010f8 | Concrete | Radial Joint | Crack
847ac3d7-8b92-46b8-ada5-f38bc528b073 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:58:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 314 | 3- consider removing this defect | Steel Channel Bracket | Steel Channel Bracket |  | 27160 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 314, 3 O'Clock, Cable Tray |  |  |  | Cable tray has level 2 corrosion. |  | Cable tray has level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | In same condition | no |  |  |  |  | fd12d0ff-d1fa-43d3-be03-8e799b9d2705 |  | https://web.fulcrumapp.com/photos/view?photos=fd12d0ff-d1fa-43d3-be03-8e799b9d2705 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
001c7e0b-8142-40c5-ae7b-9186314dab6b | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:00:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 314 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 101842 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 45554.5055 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 314, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Not Specified |  |  |  |  | KP |  | The steel channel and bolt is heavily corroded | no |  |  |  |  | 360960ac-6633-48d5-a967-29d574e6c185,e7571af1-36a6-496f-ac3d-d9dea5567f17 | , | https://web.fulcrumapp.com/photos/view?photos=360960ac-6633-48d5-a967-29d574e6c185%2Ce7571af1-36a6-496f-ac3d-d9dea5567f17 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
687a5313-186b-4446-98cc-35638e49d46c | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:29:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 314 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 76384 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Erosion/Abrasion of Concrete Cover |  | Erosion/Abrasion of Concrete Cover | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Spillage |  | Spillage | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 314, 9 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Leak inactive at time of inspection. Grout injection bolt in good condition | no |  |  |  |  | 200fe228-4500-4c6b-9cc3-e187a9c7175f,b62c8e38-ea3b-48cb-bbff-2d742846bbeb,e2d3141b-0346-448a-95b4-56b9420649b8,806b6aeb-1d24-4179-860b-de4f902b4816 | ,,, | https://web.fulcrumapp.com/photos/view?photos=200fe228-4500-4c6b-9cc3-e187a9c7175f%2Cb62c8e38-ea3b-48cb-bbff-2d742846bbeb%2Ce2d3141b-0346-448a-95b4-56b9420649b8%2C806b6aeb-1d24-4179-860b-de4f902b4816 | Concrete | Grout Hole | Leaks
65e12daf-a089-46bd-8836-d055ffc03204 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:26:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 314 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88641 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5392 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 314, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack on patch repair of circle joint up to 0.2mm in width. |  | Crack on patch repair of circle joint up to 0.2mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Crack is present at time of inspection. | no |  |  |  |  | 3001147d-7166-42cc-843d-01c46f2e75ae,57663b03-157f-42a1-be78-75ef1a47d0e2 | , | https://web.fulcrumapp.com/photos/view?photos=3001147d-7166-42cc-843d-01c46f2e75ae%2C57663b03-157f-42a1-be78-75ef1a47d0e2 | Concrete | Circular Joint | Crack
ed91d338-fa1f-48bc-9a68-23eca8f51991 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:02:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 315 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27476 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 315, 1 O'clock Ring (Segmental Concrete) Damage Affecting Single Ring |  |  |  | Cracks on the corner of the panel due to construction. Two cracks are: 100mm long and 0.25mm wide 100mm long and 0.5mm wide |  | Cracks on the corner of the panel due to construction. Two cracks are: 100mm long and 0.25mm wide 100mm long and 0.5mm wide | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still same size of crack | no |  |  |  |  | e910a795-b7cb-4068-87d6-f656c0166806 |  | https://web.fulcrumapp.com/photos/view?photos=e910a795-b7cb-4068-87d6-f656c0166806 | Concrete | Corner | Crack
b37b93e1-ccd6-40eb-9125-70d7553eae05 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:29:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 315 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26941 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 315, 11 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak Active at time of inspection. |  | Grout injection hole has leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Major leak still active at time of inspection. Large deposits of salt on the grout injection hole. High priority. | yes | no |  |  |  | ad419b2a-f20a-4a7f-b4f7-40d344b4934c,60d4ebbc-9dcd-4fd6-9889-ee5afe6594cf,cfe54ede-ee42-4751-89af-6c13a85cea5d,ccc3ded3-fdf1-47e3-ac1c-da0b9500d3a0 | ,,, | https://web.fulcrumapp.com/photos/view?photos=ad419b2a-f20a-4a7f-b4f7-40d344b4934c%2C60d4ebbc-9dcd-4fd6-9889-ee5afe6594cf%2Ccfe54ede-ee42-4751-89af-6c13a85cea5d%2Cccc3ded3-fdf1-47e3-ac1c-da0b9500d3a0 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
1c8beab5-764d-411a-958e-f4b6c0e4f4de | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:30:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 315 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 88642 |  | 8517 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/02/2023 |  | 17/10/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 315, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | Repair verified LC 9/10/24 | Not Specified | Priority: P3 |  |  |  | Break out grout locally, abrasive blast steelwork, and inspect by competent engineer to develop repair detail. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | Excavation | Standard Repair Detail Competent Supervisor | Dr |  | No change to defect | no | yes |  | no |  | 2457aace-1cb4-4d7a-b206-2ee0b971153a |  | https://web.fulcrumapp.com/photos/view?photos=2457aace-1cb4-4d7a-b206-2ee0b971153a | Concrete | Radial Joint | Drummy
f0959c68-7e6d-4ae2-9624-7180b4376877 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 02:30:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 315 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 101843 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 45554.5144 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 315, 4 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | No change to defect. Location incorrect | no | yes |  | yes | Defect at ring 316, not 315. | 803c5567-a255-40ed-8fdd-7a92837b0679,f4d4a02f-1c39-4688-a3b8-bc9614ac6330 | , | https://web.fulcrumapp.com/photos/view?photos=803c5567-a255-40ed-8fdd-7a92837b0679%2Cf4d4a02f-1c39-4688-a3b8-bc9614ac6330 | Concrete | Circular Joint | Drummy
79c23b6e-cf0a-457f-81a5-6b5dd4dd1de7 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:17:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 315 | 8 | Grout Injection Hole | Grout Injection Hole |  | 76386 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 315, 8 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. The plug bolt is in good condition. Low priority | yes | no |  | no |  | 75a9863f-af23-4bec-961e-585a4eeeb201,b6323063-ce3a-4b65-ab1c-e557defd594d | , | https://web.fulcrumapp.com/photos/view?photos=75a9863f-af23-4bec-961e-585a4eeeb201%2Cb6323063-ce3a-4b65-ab1c-e557defd594d | Concrete | Grout Hole | Leaks
d99e7dbc-c0f5-4fa9-91e8-508941eba8e1 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:56:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 316 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27203 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 316, 1 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive at time of inspection. No change to the condition. | no | no | Medium | no |  | 6ce8bba4-d93c-476d-abea-dd9259d3b51f,80382224-d374-4a64-9964-7b968a37e80a | , | https://web.fulcrumapp.com/photos/view?photos=6ce8bba4-d93c-476d-abea-dd9259d3b51f%2C80382224-d374-4a64-9964-7b968a37e80a | Concrete | Grout Hole | Leaks |  | Not Reinforcement
2280ba33-80cc-48a4-a6e5-11873dfa22b5 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:27:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 316 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88643 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5451 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 316, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack on patch repair of circle joint up to 0.4mm in width. |  | Crack on patch repair of circle joint up to 0.4mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change to defect | no | yes |  |  |  | cef958a6-8b90-4f5b-8b20-c0de1dd2b334,2b0ed64c-504b-42f0-aa74-072cee478691 | , | https://web.fulcrumapp.com/photos/view?photos=cef958a6-8b90-4f5b-8b20-c0de1dd2b334%2C2b0ed64c-504b-42f0-aa74-072cee478691 | Concrete | Circular Joint | Crack
95a81c76-0888-4346-83ed-9c1c2d196eaa | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:49:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 316 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27477 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 316,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel general condition as per previous inspection. Loss of section up to 1mm at the lower end. The bolt and nut corrosion has advanced with the nut fully corroded. Medium priority. | yes | no |  | no |  | 3447ebfc-8e10-4dcc-9e02-4063a055cffb,309bd8cd-ff07-4602-8d2a-71b121a22f05,02af49d8-859a-4143-9c09-85fe9b1d3e60 | 5 o'clock structural steel general condition ,Bolt and nut condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=3447ebfc-8e10-4dcc-9e02-4063a055cffb%2C309bd8cd-ff07-4602-8d2a-71b121a22f05%2C02af49d8-859a-4143-9c09-85fe9b1d3e60 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support
65238040-5ecd-47cf-a579-3bf1468a35f3 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:17:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 316 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27478 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 316,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock Base plate general condition as per previous inspection. The bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. | yes | no |  | no |  | c0634c36-e3e3-4d42-907a-219e1ec6bd84,b861b991-6da1-456d-a4d3-1b23f60835b9,5d82cd2a-a9d4-4a0a-9817-8728a9b0c3c9,1347ba85-e902-4115-b86a-56181afdafc8 | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=c0634c36-e3e3-4d42-907a-219e1ec6bd84%2Cb861b991-6da1-456d-a4d3-1b23f60835b9%2C5d82cd2a-a9d4-4a0a-9817-8728a9b0c3c9%2C1347ba85-e902-4115-b86a-56181afdafc8 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
dd7d3193-3558-496f-a7a3-8b5dcc87bf8e | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:25:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 317 | 11 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88644 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5476 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 317, 11 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change to defect. | no | yes |  |  |  | 43e0f9d6-f12e-4999-abf8-544ce869911d,756a30b7-9d7b-4a96-b1cc-4ecdb9dff49e | , | https://web.fulcrumapp.com/photos/view?photos=43e0f9d6-f12e-4999-abf8-544ce869911d%2C756a30b7-9d7b-4a96-b1cc-4ecdb9dff49e | Concrete | Circular Joint | Drummy
45f1587c-472f-4c60-ba39-c81ce1840fbc | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:23:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 318 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 76388 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 318, 11 O'Clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak is still active at time of inspection causing the steel bracket to corrode heavily. High priority. | yes | no | High |  |  | 6c6060a5-6ce4-4745-b665-b06087543ccc,646206d4-add6-4996-8850-9a8d67a187eb | , | https://web.fulcrumapp.com/photos/view?photos=6c6060a5-6ce4-4745-b665-b06087543ccc%2C646206d4-add6-4996-8850-9a8d67a187eb | Concrete,Steel | Channel Bracket | Leaks |  | Channel Bracket
5e10b7f0-4245-45f4-b1c0-7ad686c3cc56 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:21:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 318 | 11 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 76390 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44730.86 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 318, 11 O'Clock, Segmented Bolted Joint (Radial Joint). |  |  |  | Crack on patch repair of radial joint up to 0.25mm in width. |  | Crack on patch repair of radial joint up to 0.25mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Crack on patch repair with the same size is still present. Drumminess observed at the location. | yes | yes |  |  |  | 8b212480-badb-4190-8ac5-c2504adafaaf,3a20a52f-aab8-4048-bdf5-7a9c03406457 | , | https://web.fulcrumapp.com/photos/view?photos=8b212480-badb-4190-8ac5-c2504adafaaf%2C3a20a52f-aab8-4048-bdf5-7a9c03406457 | Concrete | Radial Joint | Crack,Drummy
f4765976-2109-4d7c-81c3-b21df772cb9d | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:20:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 318 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 101845 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 45554.5273 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 318, 11 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 Corrosion. Channel anchor bolt has Level 2 corrosion. |  | Steel channel support bracket has Level 1 Corrosion. Channel anchor bolt has Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Channel anchor bolts have level 4 corrosion. High priority. Corrosion has advanced | yes | no | High |  |  | 2b66253b-3f0d-4d1f-9592-a28470612fbc |  | https://web.fulcrumapp.com/photos/view?photos=2b66253b-3f0d-4d1f-9592-a28470612fbc | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
168bf06d-2f61-4e87-9400-ca93b33cfa59 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:19:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 318 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 76389 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8569 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 318, 11 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 corrosion. |  | Steel channel support bracket has Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Steel channel bracket is heavily corroded and must be replaced. Level 4 corrosion. High repair. | yes | no | High | no |  | dc99e5e8-f8cd-4045-a94b-1514d0afe38b,bb48fcf7-ecf5-4ea3-8497-e9e1f3424a1e,13448950-cafa-43fe-89f7-25b5dfee2b8a | ,, | https://web.fulcrumapp.com/photos/view?photos=dc99e5e8-f8cd-4045-a94b-1514d0afe38b%2Cbb48fcf7-ecf5-4ea3-8497-e9e1f3424a1e%2C13448950-cafa-43fe-89f7-25b5dfee2b8a | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
1aa55322-86d3-40fc-b61a-c2d0d9317bcd | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:16:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 318 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 101846 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 45554.5285 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 318, 11 O'clock, Channel Anchor Bolts |  |  |  | Missing 2 fasterners at channel bracket. |  | Missing 2 fasterners at channel bracket. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Two bolts still missing. No change to defect. | no | yes |  |  |  | eb4ebb15-547d-470e-a6f0-477deda17495 |  | https://web.fulcrumapp.com/photos/view?photos=eb4ebb15-547d-470e-a6f0-477deda17495 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
b69f6a85-6480-4f78-ad61-4b404860469f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:50:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 318 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 101844 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 45554.5254 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 318, 3 O'clock, Channel Anchor Bolts |  |  |  | Channel anchor bolts have level 1 corrosion. |  | Channel anchor bolts have level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Very minor corrosion on the bolt. Low priority defect. | no | no | Low | no |  | d2b4056e-5c80-4c58-915e-70cac21917ef,6f6d8331-bf9d-4057-b972-2340421e774d | , | https://web.fulcrumapp.com/photos/view?photos=d2b4056e-5c80-4c58-915e-70cac21917ef%2C6f6d8331-bf9d-4057-b972-2340421e774d | Steel | Channel Bracket-Bolt | Corrosion-Surface
ba3dbdc5-48c3-4149-992d-b3acecb925f6 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:19:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 318 | 9 | Grout Injection Hole | Grout Injection Hole |  | 76387 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 318, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | On-Line | No | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak still inactive at time of inspection. No change to defect b | no |  |  |  |  | 24997392-3dad-4ea5-8d93-681f75479d82,8894df84-1863-4dec-a114-8e3a7b9833a4 | , | https://web.fulcrumapp.com/photos/view?photos=24997392-3dad-4ea5-8d93-681f75479d82%2C8894df84-1863-4dec-a114-8e3a7b9833a4 | Concrete | Grout Hole | Leaks
6ab2e579-c867-4a80-b21b-ee5b0f2d286f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:37:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 319 | 8 | Grout Injection Hole | Grout Injection Hole |  | 76392 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 319, 8 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Active at time of inspection. |  | Grout injection hole has leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Bogdan Stanca |  | The leak is active at the time of inspection. The previous repair has failed to control the leak. | no | yes |  | no |  | f74256da-d7cd-455d-9433-5392dfb6e9e8,1dcbae1b-b69b-4470-a674-2be5e6245d71 | , | https://web.fulcrumapp.com/photos/view?photos=f74256da-d7cd-455d-9433-5392dfb6e9e8%2C1dcbae1b-b69b-4470-a674-2be5e6245d71 | Concrete | Grout Hole | Leaks
02afc350-7278-41ce-93f3-54dfbbf6ee47 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:13:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 319 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88645 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5489 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 319, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack on patch repair of circle joint up to 0.2mm in width. |  | Crack on patch repair of circle joint up to 0.2mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Unable to identify crack on patch repair. | [8 empty] | Concrete | Circular Joint | Crack
ef759400-5cf4-4136-8851-3db41b1a61fe | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:11:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 320 | 11 | Grout Injection Hole | Grout Injection Hole |  | 76393 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 320, 11 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Dr |  | Leak still inactive at time of inspection. Grout injection hole in good condition. No change to defect. Low priority | no | yes |  | no |  | 402415c0-7dd1-4ff5-8502-025142656c7e,cfc7e04f-5a3a-4eb3-aa07-2ca0c9a5e5e4 | , | https://web.fulcrumapp.com/photos/view?photos=402415c0-7dd1-4ff5-8502-025142656c7e%2Ccfc7e04f-5a3a-4eb3-aa07-2ca0c9a5e5e4 | Concrete | Grout Hole | Leaks
fe06c1ca-ec19-4b6b-9bff-c7ce3c1c1854 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:46:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 320 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 36629 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3586 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 320, 2 O'clock, Channel Anchor Bolts |  |  |  | Missing nut from anchor bolt of steel bracket. |  | Missing nut from anchor bolt of steel bracket. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Bolt is still missing. No change to defect. | no |  |  |  |  | 6293fa50-a11e-480f-a81a-3cf959288845 |  | https://web.fulcrumapp.com/photos/view?photos=6293fa50-a11e-480f-a81a-3cf959288845 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
920e49ab-fdd5-41ff-bf9a-f5f26708d039 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:46:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 320 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36631 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 320, 3 O'clock, Channel Anchor Bolts | Rupture | Rupture |  | Level 5 corrosion at side wall channel. |  | Level 5 corrosion at side wall channel. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Not Specified | Priority: P3 |  |  |  | Replace steel channel support bracket with original design. Remove and replace corroded anchor bolt one at a time if possible. If bolt cannot be removed, carry out repair following Steel Corrosion Repair 000-S-12598 corroded anchor bolt details. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair 000-S-12598 corroded anchor bolt details. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | Dr |  | Corrosion has advanced due to active leak. High priority | yes | no | High |  |  | 165121b3-5f75-4144-8997-f7d8358f60dc,9c8d8083-f64f-4bf5-a048-07beeb7b66a5 | , | https://web.fulcrumapp.com/photos/view?photos=165121b3-5f75-4144-8997-f7d8358f60dc%2C9c8d8083-f64f-4bf5-a048-07beeb7b66a5 | Steel | Channel Bracket-Bolt | Leaks
963ff9e2-faa3-46ff-95f6-fc7f5abbc44b | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:42:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 320 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36630 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 320, 3 O'clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak seems to still be active behind the steel channel bracket. Level 5 corrosion on the steel channel bracket. High priority | yes | no | High |  |  | 08c5660f-edde-446d-9b6a-7c8b21e13653,5e6478d9-7a00-4a38-9adf-0f9bc5149f26,3f0b6a62-ed54-4a00-bde9-8c0267b296ba | ,, | https://web.fulcrumapp.com/photos/view?photos=08c5660f-edde-446d-9b6a-7c8b21e13653%2C5e6478d9-7a00-4a38-9adf-0f9bc5149f26%2C3f0b6a62-ed54-4a00-bde9-8c0267b296ba | Concrete,Steel | Channel Bracket | Leaks |  | Not Reinforcement
53f11ea0-12fa-4631-b8db-78c4208cfb84 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:27:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 320 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27479 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 320, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The 7 o'clock base plate is as per previous inspection. The bolt and nut has advanced corrosion with the nut fully corroded. The 5 o'clock structural steel has surface corrosion with loss of section up to 1mm at the lower end. The bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. | yes | no |  | no |  | a9e02df9-ba95-4e84-bc86-e627732e5ae0,455c03f4-1d9a-48c5-9cbe-891054373164,517ae374-1eb3-493d-bd40-e6ec6f10bd69,b91e62f5-d04b-4dd8-aadd-5b771eed8cdc,97999293-da11-4fdf-831b-b769b3c58682,f72a2fc8-2f98-4012-a46c-f75a173758a0 | 7 o'clock base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition ,5 o'clock structural steel general condition ,Bolt condition | https://web.fulcrumapp.com/photos/view?photos=a9e02df9-ba95-4e84-bc86-e627732e5ae0%2C455c03f4-1d9a-48c5-9cbe-891054373164%2C517ae374-1eb3-493d-bd40-e6ec6f10bd69%2Cb91e62f5-d04b-4dd8-aadd-5b771eed8cdc%2C97999293-da11-4fdf-831b-b769b3c58682%2Cf72a2fc8-2f98-4012-a46c-f75a173758a0 | Steel | Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface
f6c39fc3-1cbb-4448-8b55-13f20356b286 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:28:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 320 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27480 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Structure,Ring 320,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 2 - Medium low corrosion |  | Class 2 - Medium low corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | Defect not identified during this inspection. | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
01ecaa99-75ea-4662-a12d-d46c60b5c1da | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 06:05:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 321 | 11 | Grout Injection Hole | Grout Injection Hole |  | 76394 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 321, 11 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak inactive at time of inspection. Grout injection hole in good condition. Low priority | no | no | Low | no |  | 1e47093c-07f9-4123-8760-06cf3bf63298,ec253a60-4034-4057-bd21-a30315431d3e | , | https://web.fulcrumapp.com/photos/view?photos=1e47093c-07f9-4123-8760-06cf3bf63298%2Cec253a60-4034-4057-bd21-a30315431d3e | Concrete | Grout Hole | Leaks
32021acf-ef8c-40e9-bd46-f00a2bd96226 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:37:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 321 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 76395 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44730.8683 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 321, 2 O'clock, Ring (Segmental Concrete) Damage Affecting Single Ring. |  |  |  | Concrete shell segment has erosion damage. |  | Concrete shell segment has erosion damage. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change. Low priority | no |  |  |  |  | 8eabd866-ebb6-4ac2-a0a0-ba9c53fa255d |  | https://web.fulcrumapp.com/photos/view?photos=8eabd866-ebb6-4ac2-a0a0-ba9c53fa255d | Concrete
92ef6432-ab9a-4699-a13a-cce3ca223aa4 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:33:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 323 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27202 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 323, 12 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | Dr |  | Leak still inactive at time of inspection. | no | yes |  |  |  | 81fa1b1c-c417-4b62-bef9-4e609c2f63f4,278988cc-fae9-4ef5-a38c-7b3b321e36f0 | , | https://web.fulcrumapp.com/photos/view?photos=81fa1b1c-c417-4b62-bef9-4e609c2f63f4%2C278988cc-fae9-4ef5-a38c-7b3b321e36f0 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
3241b9e8-43db-4563-abbc-ab3b42fa6dac | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:10:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 324 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36633 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3642 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 324, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock Base plate is as per previous inspection with estimated loss of section up to 1mm. The bolt and nut corrosion has advanced with the nut fully corroded. 5 o'clock structural steel corrosion has advanced especially at the lower end with loss of section up to 1mm. Bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. | yes | no |  | no |  | f4bc0bb7-ee3d-43d2-b6b5-88941b5a2224,630439e8-5fae-4f49-968f-65cc8ee8f469,ec1ca2e7-4640-4b12-93f6-4e7903c1bea3,db81e682-bbe2-4bae-8683-afae4c045967,0fc95b69-25f8-4b8d-bdb7-112d63da2785,4deeda9f-0aa8-43cd-9882-9bb556841981,b135d2f2-96d3-405f-b6ad-35808403f494 | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition ,5 o'clock structural steel general condition ,Bolt and nut condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=f4bc0bb7-ee3d-43d2-b6b5-88941b5a2224%2C630439e8-5fae-4f49-968f-65cc8ee8f469%2Cec1ca2e7-4640-4b12-93f6-4e7903c1bea3%2Cdb81e682-bbe2-4bae-8683-afae4c045967%2C0fc95b69-25f8-4b8d-bdb7-112d63da2785%2C4deeda9f-0aa8-43cd-9882-9bb556841981%2Cb135d2f2-96d3-405f-b6ad-35808403f494 | Steel | Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Corrosion-Heavy
5fc7c589-a722-4179-a5f4-2e58cb19ad33 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:31:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 325 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26943 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 325, 2 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive at time of inspection. | no | no |  |  |  | c4d2a7ef-6618-4c16-b253-099ea9073213,afc06911-d9c8-4afe-93cc-de3e9d91a96e | , | https://web.fulcrumapp.com/photos/view?photos=c4d2a7ef-6618-4c16-b253-099ea9073213%2Cafc06911-d9c8-4afe-93cc-de3e9d91a96e | Concrete | Grout Hole | Leaks |  | Not Reinforcement
1d0789cc-1f0b-4d8d-b866-8b41b0ff0d49 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 17:00:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 326 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 88646 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5534 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 326, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion |  | Steel channel support bracket has Level 1 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | BP -AA |  | Bolt and nut on channel wrapped with protective tape. Observe item. | [5 empty] | 98badd24-f965-47a3-ac6a-606a392dd3c4,e6d0b046-c104-467e-93ae-434b56a52fa7 | , | https://web.fulcrumapp.com/photos/view?photos=98badd24-f965-47a3-ac6a-606a392dd3c4%2Ce6d0b046-c104-467e-93ae-434b56a52fa7 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
a34b2657-4318-474b-8a05-322cd7c11962 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:53:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 327 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88647 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5548 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 327, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack on patch repair of circle joint up to 0.2mm in width. |  | Crack on patch repair of circle joint up to 0.2mm in width. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change to the crack on the patchwork repair of circle joint. Low risk | no | yes |  |  |  | f5b5ed77-58f2-4418-84f6-49c0ca6664bc,446e1692-4fa7-42b2-b9f7-9456e6b94f46,f8dc620f-e1c9-447b-89f4-032d3faa60a3 | ,, | https://web.fulcrumapp.com/photos/view?photos=f5b5ed77-58f2-4418-84f6-49c0ca6664bc%2C446e1692-4fa7-42b2-b9f7-9456e6b94f46%2Cf8dc620f-e1c9-447b-89f4-032d3faa60a3 | Concrete | Circular Joint | Crack
b859af0e-a614-4e29-bfd3-4fec7fe6a1c2 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 16:51:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 328 | 5 to 7 O’clock | Channel Anchor Bolts | Channel Anchor Bolts |  | 27481 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The 7 o'clock steel base plate is as per previous inspection. The bolt and nut corrosion has advanced with the nut fully corrected. Medium priority. The 5 o'clock structural steel corrosion has advanced with the nut fully corroded. Structural Steel has section loss up to 1mm. Medium priority. | yes | no |  | no |  | 2dfc3129-85e0-43b0-bf98-7ce54e6c235d,1360742d-a6c7-4cb9-a840-aa494ac28b47,a54b5bbf-57c6-4856-af60-9a796bab12ec,d662db2f-0e3e-44e8-ab0c-423809ccbd83,25f574dc-3557-4b59-b839-c4a4d9c20cbc,4c31ab2e-7217-4e96-a426-d1b9a6d4a801,1f89c951-6cea-44ad-8532-c8d6292f78ec | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition ,5 o'clock structural steel general condition ,Bolt condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=2dfc3129-85e0-43b0-bf98-7ce54e6c235d%2C1360742d-a6c7-4cb9-a840-aa494ac28b47%2Ca54b5bbf-57c6-4856-af60-9a796bab12ec%2Cd662db2f-0e3e-44e8-ab0c-423809ccbd83%2C25f574dc-3557-4b59-b839-c4a4d9c20cbc%2C4c31ab2e-7217-4e96-a426-d1b9a6d4a801%2C1f89c951-6cea-44ad-8532-c8d6292f78ec | Steel | Conveyor Support,Conveyor Support-Bolt | Corrosion-Heavy |  | Not walkway support. Conveyor Support
631106d9-d2c1-4717-a1dd-7b8f2de20d7a | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:24:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 330 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76400 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44732.2285 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 330, 3 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Corrosion of bolt has advanced. Medium priority | no | no | Medium |  |  | 9b76d8ad-9a2d-4dc8-bba3-f9959cb43286,db42a6b8-4587-448c-b751-0298b03315b9 | , | https://web.fulcrumapp.com/photos/view?photos=9b76d8ad-9a2d-4dc8-bba3-f9959cb43286%2Cdb42a6b8-4587-448c-b751-0298b03315b9 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
e5c0a955-ac00-400c-abd4-6cf44850c673 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:20:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 330 | 4 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 88649 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5572 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 330, 4 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | No change to condition of defect. | no | yes |  | no |  | 180e43dd-13a4-41f5-83e6-c2dbfd49e893,8548298a-aba9-4833-bfe3-b2c7ee31798d | , | https://web.fulcrumapp.com/photos/view?photos=180e43dd-13a4-41f5-83e6-c2dbfd49e893%2C8548298a-aba9-4833-bfe3-b2c7ee31798d | Concrete | Radial Joint | Drummy
168cf105-7d81-496d-8815-b706f6a2a7ba | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 15 |  |  |  | 2025-07-28 01:52:09 AEST | 2025-07-29 09:20:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 312 | 5 o'clock |  |  | Structural Steel walkway bracket | [56 empty] | Bogdan Stanca |  | 5 o'clock structural steel presents surface corrosion with the bolt and nut having advanced corrosion. Nut fully corrected. Medium priority. |  |  |  | no |  | e467ae4e-ebb2-4be7-bf4a-b1e398d94a7c,c19ad88a-b5bb-492e-ac6e-54eecb8e69b3,5094a322-1f15-4982-80c0-8c5e5a02386b,0675a122-8247-4e69-a206-c8f946a795b3 | 5 o'clock structural steel general condition ,Bolt condition ,Bolt condition after corrosion removed ,Upper bolt condition | https://web.fulcrumapp.com/photos/view?photos=e467ae4e-ebb2-4be7-bf4a-b1e398d94a7c%2Cc19ad88a-b5bb-492e-ac6e-54eecb8e69b3%2C5094a322-1f15-4982-80c0-8c5e5a02386b%2C0675a122-8247-4e69-a206-c8f946a795b3 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface
f6126e98-a793-4218-a376-26b846ef52b7 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 15 |  |  |  | 2025-07-28 02:34:12 AEST | 2025-07-28 02:38:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 308 | 5 o'clock |  |  | Structural Steel supporting the walkway. | [56 empty] | Bogdan Stanca |  | 5 o'clock structural steel has surface corrosion with loss of section up to 1mm. Bolt and nut has advanced corrosion with the nut fully corroded. Medium priority. |  |  |  | no |  | 72552cf4-8c70-4422-bb95-2ea929db6bcb,613835f5-a3a1-4940-b339-2c44163b0947,d6770064-10d0-46eb-8248-e8e3cf83b93b | 5 o'clock structural steel general condition ,Bolt and nut condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=72552cf4-8c70-4422-bb95-2ea929db6bcb%2C613835f5-a3a1-4940-b339-2c44163b0947%2Cd6770064-10d0-46eb-8248-e8e3cf83b93b | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface
830f2989-50d3-44c4-87fb-5e4b465feef5 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 12 |  |  |  | 2025-07-29 06:02:35 AEST | 2025-07-29 06:03:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 323 | 11 O clock |  | Grout Injection Hole | [57 empty] | Dr |  | Previous leak location. Inactive at time of inspection. Grout injection hole in good condition. Low priority. |  | yes |  | no |  | f94d9340-f3a6-4be8-a2b2-68013d194291 |  | https://web.fulcrumapp.com/photos/view?photos=f94d9340-f3a6-4be8-a2b2-68013d194291 | Concrete | Grout Hole | Leaks
43601d1f-6ee6-464c-9f3e-3215d97353be | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 12 |  |  |  | 2025-07-29 06:07:54 AEST | 2025-07-29 16:48:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 321 | 9 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | Dr |  | Delaminated and drummy concrete 100x100mm at the circumferential joint. Low risk | [5 empty] | e80ca2f9-2d54-47a1-bf4f-8a4c0dd831b3,7893f5ef-21a3-4591-9f36-309987b4b63a,aab2d9ce-e098-43dd-a9ab-4fbe43d858f0,194b57ac-3b2d-45d4-a943-479daeb20012 | ,,, | https://web.fulcrumapp.com/photos/view?photos=e80ca2f9-2d54-47a1-bf4f-8a4c0dd831b3%2C7893f5ef-21a3-4591-9f36-309987b4b63a%2Caab2d9ce-e098-43dd-a9ab-4fbe43d858f0%2C194b57ac-3b2d-45d4-a943-479daeb20012 | Concrete | Circular Connection,Circular Joint | Drummy
b5294b88-a1ce-43b6-995b-4f64ac87e6f7 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 12 |  |  |  | 2025-07-29 06:23:17 AEST | 2025-07-29 06:24:02 AEST | 30011704-user5@smec.com | james.stone@smec.com | 318 | 11 |  | Segment Bolted Joint (Radial Joint) | [57 empty] | Dr |  | 0.2 mm crack on patch repair. | [5 empty] | 11aa859f-b985-42dd-bfec-d61bfb09d603 |  | https://web.fulcrumapp.com/photos/view?photos=11aa859f-b985-42dd-bfec-d61bfb09d603 | Concrete | Radial Joint | Crack
885fc004-b020-472f-9f76-647324cb00da | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 5 |  |  |  | 2025-07-29 16:24:46 AEST | 2025-07-29 16:26:31 AEST | 30011704-user5@smec.com | james.stone@smec.com | 308 | 11 |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Drummy/Delaminated grout along the circumferential joint 50x 50mm | [5 empty] | 1f94f063-98d7-47cc-a508-5383eb303109 |  | https://web.fulcrumapp.com/photos/view?photos=1f94f063-98d7-47cc-a508-5383eb303109 | Concrete | Circular Connection,Circular Joint,Radial Joint | Drummy
f8799343-75bd-4420-a500-5b03d8f1f967 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 5 |  |  |  | 2025-07-29 17:16:23 AEST | 2025-07-29 17:18:00 AEST | 30011704-user5@smec.com | james.stone@smec.com | 307 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Delaminated/ drummy grout along circumferential joint | [5 empty] | cc5af697-e47c-4b52-9d1a-c4482e522b00,ed237eda-61c8-4413-a6ac-dfe47c99ff10 | , | https://web.fulcrumapp.com/photos/view?photos=cc5af697-e47c-4b52-9d1a-c4482e522b00%2Ced237eda-61c8-4413-a6ac-dfe47c99ff10 | Concrete | Circular Connection,Circular Joint | Drummy
ee99dcc7-350b-41e2-93d8-782ee876094b | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 5 |  |  |  | 2025-07-29 17:18:01 AEST | 2025-07-29 17:19:17 AEST | 30011704-user5@smec.com | james.stone@smec.com | 307 | 3 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Delaminated/ drummy grout along the circumferential joint behind cable tray | [5 empty] | 3f1003a5-1636-455a-9ce5-c149a2be0e2b |  | https://web.fulcrumapp.com/photos/view?photos=3f1003a5-1636-455a-9ce5-c149a2be0e2b | Concrete | Circular Connection,Circular Joint,Misc (Pipes/Cable Tray/etc) | Drummy
15a87495-982a-4303-8ee5-562b781bf9b0 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 5 |  |  |  | 2025-07-29 17:19:20 AEST | 2025-07-29 17:20:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 307 | 1 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Delaminated/ drummy grout along circumferential joint as well as active leak. | [5 empty] | b093145f-97b0-4981-a212-0bbcb175e74c |  | https://web.fulcrumapp.com/photos/view?photos=b093145f-97b0-4981-a212-0bbcb175e74c | Concrete | Circular Connection,Circular Joint | Drummy,Leaks
29c49f04-cecf-4fd1-9fdb-e05cd7a354a6 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 5 |  |  |  | 2025-07-29 17:24:27 AEST | 2025-07-29 17:26:53 AEST | 30011704-user5@smec.com | james.stone@smec.com | 306 | 3 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The steel channel and bolt are heavily corroded | [5 empty] | 1274a3b6-f55c-4753-8f16-a26b17e1114a |  | https://web.fulcrumapp.com/photos/view?photos=1274a3b6-f55c-4753-8f16-a26b17e1114a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
ab8bdddd-a580-4faa-a063-486cb17edbb6 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 6 |  |  |  | 2025-07-29 17:41:08 AEST | 2025-07-29 17:44:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 329 | 3 O’clock |  | Grout Injection Behind Ring | [32 empty] | Grout injection hole filled. Inactive leaks behind channel. Low risk | [24 empty] | AA BP |  | Grout injection hole filled. Inactive leaks behind channel. Low risk | [5 empty] | e5c3d30f-5a08-4bae-9e18-b299caa48163,33077bde-592b-454c-a6c4-96b3881ebbc6 | , | https://web.fulcrumapp.com/photos/view?photos=e5c3d30f-5a08-4bae-9e18-b299caa48163%2C33077bde-592b-454c-a6c4-96b3881ebbc6 | Concrete | Grout Hole | Leaks
4626175d-a404-4582-a1ac-ce6191c88de4 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 7 |  |  |  | 2025-07-29 16:38:41 AEST | 2025-07-29 16:43:11 AEST | 30011704-user5@smec.com | james.stone@smec.com | 306 | 10 |  |  | Steel support structure | [56 empty] | RT |  | Roller assembly support plate has moderate corrosion. | [5 empty] | 03fe68e1-4b51-411c-8125-978f92592583,d885400a-7ac2-4715-beb2-7f60bf131a21 | , | https://web.fulcrumapp.com/photos/view?photos=03fe68e1-4b51-411c-8125-978f92592583%2Cd885400a-7ac2-4715-beb2-7f60bf131a21 | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
975dee94-2191-427d-91a9-a08dc018311d | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3 |  |  |  | 2025-07-29 22:24:39 AEST | 2025-07-29 22:26:07 AEST | 30011704-user5@smec.com | james.stone@smec.com | 329 | 2 O'Clock |  | Grout Injection Hole | [57 empty] | Dr |  | Previous leak location. Leak inactive at time of inspection. Salt deposit present on top of the surface. Grout injection hole in good condition, low priority. |  | yes |  | no |  | 1d218b10-adc6-4ae0-a861-f8a72e44bd3e,3f811988-4136-41a2-849e-5b3b465d1145 | , | https://web.fulcrumapp.com/photos/view?photos=1d218b10-adc6-4ae0-a861-f8a72e44bd3e%2C3f811988-4136-41a2-849e-5b3b465d1145 | Concrete | Grout Hole | Leaks
8b5de240-e197-4d77-87c4-4337a9e675d9 | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3e5d5385-3a2f-4155-b5a3-772fc267e40f | 3 |  |  |  | 2025-07-29 22:42:52 AEST | 2025-07-29 22:44:34 AEST | 30011704-user5@smec.com | james.stone@smec.com | 323 | 2 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | Dr |  | 5mm crack on patchwork. |  | no | Medium |  |  | 6af4532c-8b98-4616-8c74-8ad76380ad86,66209d65-73a7-4b4f-8f2d-abb7c1a29155 | , | https://web.fulcrumapp.com/photos/view?photos=6af4532c-8b98-4616-8c74-8ad76380ad86%2C66209d65-73a7-4b4f-8f2d-abb7c1a29155 | Concrete | Middle of Panel | Crack |  | MIddle of Panel
e99d1c0a-bb70-41fc-94bd-368e69a0d820 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3216 | 118.5853 | POINT (118.5853269 -20.3216476) | 2025-05-27 20:13:18 AEST | 2025-07-29 05:51:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 331 | 11 | Grout Injection Hole | Grout Injection Hole |  | 88650 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5581 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 331, 11 O'Clock, Grout Injection Hole |  |  |  | Grout injection hole has grout delamination. |  | Grout injection hole has grout delamination. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | DR |  | Grout injection hole still has delamination. No change to the defect. | no | yes |  | yes |  | d517855e-4ee8-4d28-856e-84b5acad69e2,e168f490-a595-4ccd-9175-4f2d3a89652d | , | https://web.fulcrumapp.com/photos/view?photos=d517855e-4ee8-4d28-856e-84b5acad69e2%2Ce168f490-a595-4ccd-9175-4f2d3a89652d | Concrete | Grout Hole | Drummy
3441f25e-4e8b-4479-8f9b-bb638194a98f | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:36:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 331 | 8 | Grout Injection Hole | Grout Injection Hole |  | 88648 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 331, 8 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. The seal bolt is in good condition. Low priority. | no | no |  | no |  | 2b54f3b9-8669-4061-9add-78a16a1ffe5f,4f7498c0-39be-4c2f-af37-9525d1552062 | , | https://web.fulcrumapp.com/photos/view?photos=2b54f3b9-8669-4061-9add-78a16a1ffe5f%2C4f7498c0-39be-4c2f-af37-9525d1552062 | Concrete | Grout Hole | Leaks
90b57098-26bf-4ecc-805a-656acd50c39d | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3216 | 118.5853 | POINT (118.5853245 -20.3216495) | 2025-05-27 20:13:18 AEST | 2025-07-29 22:20:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 332 | 2 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88651 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5592 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 332, 2 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Crack on patch repair of circle joint up to 0.25mm in width and extend up to 100mm. |  | Crack on patch repair of circle joint up to 0.25mm in width and extend up to 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change to condition of defect. | no | no | Low |  |  | be361176-9504-4cda-9d37-ed51c7636934 |  | https://web.fulcrumapp.com/photos/view?photos=be361176-9504-4cda-9d37-ed51c7636934 | Concrete | Circular Joint | Crack
c2fa41a9-afc4-4719-ad14-1370294185af | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:33:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 332 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27482 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 332, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. |  | Level 2 to Level 3 corrosion at anchor bolts of conveyor and walkway supports. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel as per previous inspection. Bolt corrosion has advanced. Medium priority | yes | yes |  | no |  | 27a7b740-fe9b-4f35-a810-cb2d26fee39a,7bf749b6-8b59-42bc-8e74-e56f919ce273 | , | https://web.fulcrumapp.com/photos/view?photos=27a7b740-fe9b-4f35-a810-cb2d26fee39a%2C7bf749b6-8b59-42bc-8e74-e56f919ce273 | Steel | Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface
64db4203-7ee3-47ce-91d9-58a2e1a14069 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:31:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 332 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27483 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 332,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The base plate is as per previous inspection. The corrosion of the bolt and nut has advanced. Medium priority | yes | no |  | no |  | 9bb580ad-4b1c-493c-a5a6-cf80fa062fd8,2bbf15a2-6347-420a-b40f-f75423e0c642,b3eeab34-b17f-412a-89c2-1062155ef594,c2a1f714-b0d8-4c39-b1c1-ab765e1100b2 | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=9bb580ad-4b1c-493c-a5a6-cf80fa062fd8%2C2bbf15a2-6347-420a-b40f-f75423e0c642%2Cb3eeab34-b17f-412a-89c2-1062155ef594%2Cc2a1f714-b0d8-4c39-b1c1-ab765e1100b2 | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support
5d4db678-4499-4cd3-97ec-ced45c078fa4 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 03:36:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 334 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 27200 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 334, 12 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion |  | Steel channel support bracket has Level 1 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No corrosion visible at 12. | yes | no |  | yes | Remove defect | 614ac3ec-7ec5-44ab-a27c-c9c542aae2a3 |  | https://web.fulcrumapp.com/photos/view?photos=614ac3ec-7ec5-44ab-a27c-c9c542aae2a3 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
4c963865-be1b-4902-9567-e27e4865c77b | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:57:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 334 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 76402 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44732.2321 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 334, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion. One channel anchor bolt is loose. |  | Steel channel support bracket has Level 1 corrosion. One channel anchor bolt is loose. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | DR |  | Level 1 corrosion is present. Bolt is not loose. Low priority | no | no |  |  |  | 05966727-3456-4340-9de5-5a8ada8a431b,7ece815e-9942-4e4d-b6b6-af2e63bcc834,a64bd342-f431-4212-8569-2d82665d008f | ,, | https://web.fulcrumapp.com/photos/view?photos=05966727-3456-4340-9de5-5a8ada8a431b%2C7ece815e-9942-4e4d-b6b6-af2e63bcc834%2Ca64bd342-f431-4212-8569-2d82665d008f | Steel | Channel Bracket,Channel Bracket-Bolt | Loose
03310e6c-4557-4c82-b608-67fd8932ed2e | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3216 | 118.5853 | POINT (118.5853239 -20.3216463) | 2025-05-27 20:13:18 AEST | 2025-07-27 22:25:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 334 | 8 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 36634 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3654 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 334, 8 O'clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle Joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Circle Joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect is as per previous inspection. The defect is considered superficial with no structural implication. | no | yes |  | no |  | 24207c5c-b69a-4582-8051-da45760ab054 |  | https://web.fulcrumapp.com/photos/view?photos=24207c5c-b69a-4582-8051-da45760ab054 | Concrete | Circular Joint,Radial Joint | Drummy
38474bf8-ef68-4bd3-aaa7-79b1caed7b81 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 03:34:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 335 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27199 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 335, 11 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | DR |  | Leak still inactive at time of inspection. No change to condition. Grout hole sealed. Low priority | no | yes |  |  |  | 9f006284-5f9f-4d3d-8c73-5b15f15743d3,631281fa-d752-4fa2-abdc-22c8877a4f4f | , | https://web.fulcrumapp.com/photos/view?photos=9f006284-5f9f-4d3d-8c73-5b15f15743d3%2C631281fa-d752-4fa2-abdc-22c8877a4f4f | Concrete | Grout Hole | Leaks |  | Not reinforcement
ef00abe4-1b0d-4ead-9d99-01400cabdf75 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 03:33:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 335 | 12 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 88652 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5601 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 335, 12 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | No change. | no | yes |  |  |  | 732be3de-3035-41de-a28d-e2129ec99d77,47d3293f-5912-4102-87cf-0ed6b9bef800 | , | https://web.fulcrumapp.com/photos/view?photos=732be3de-3035-41de-a28d-e2129ec99d77%2C47d3293f-5912-4102-87cf-0ed6b9bef800 | Concrete | Radial Joint | Drummy
9f6af1d9-8cda-496a-80ca-66c4b94a026c | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:40:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 336 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27484 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 336, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel corrosion has advanced. Nut fully corroded. Medium priority. | yes | no |  | no |  | da154ebe-451e-4362-8f3f-76984262e136,33429b9a-8b46-49db-b215-47af5c905152 | 5 o'clock structural steel general condition ,Bolt condition | https://web.fulcrumapp.com/photos/view?photos=da154ebe-451e-4362-8f3f-76984262e136%2C33429b9a-8b46-49db-b215-47af5c905152 | Steel | Channel Bracket-Bolt,Walkway Support | Corrosion-Heavy,Corrosion-Surface
ec77847e-6039-4138-ab2f-af8d74bfd5f8 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:43:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 336 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27485 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 336,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock Base plate condition as per previous inspection. Bolt and nut corrosion has advanced. Nut fully corrected. Medium priority. | yes | no |  | no |  | ef7a6fb2-0766-488f-b506-4abf50a602a4,c85e7457-08cd-4286-abac-a7d8b436db6f,c6491a25-e39c-4063-a3aa-71793f698eb8 | 7 o'clock base plate general condition ,Lower bolt condition ,Middle bolt condition | https://web.fulcrumapp.com/photos/view?photos=ef7a6fb2-0766-488f-b506-4abf50a602a4%2Cc85e7457-08cd-4286-abac-a7d8b436db6f%2Cc6491a25-e39c-4063-a3aa-71793f698eb8 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
1437dcff-f600-4b61-807f-d4d8cf5a8888 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3217 | 118.5853 | POINT (118.5852888 -20.3216721) | 2025-05-27 20:13:18 AEST | 2025-07-29 02:18:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 337 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 76403 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44732.2337 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 337, 4 O'clock, Ring (Segmental Concrete) Damage Affecting Single Ring. |  |  |  | Concrete shell segment has erosion damage. |  | Concrete shell segment has erosion damage. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | DR |  | Erosion damage is still present with no change to condition. Defect is listed at 4 O Clock location, however it's at 5 O Clock. Defect location has been listed incorrectly | no | yes |  | no |  | bd99d698-f91e-4835-bd99-2dd6563d922f,aa89ea2a-c950-4f93-880a-edfd7a63386e | , | https://web.fulcrumapp.com/photos/view?photos=bd99d698-f91e-4835-bd99-2dd6563d922f%2Caa89ea2a-c950-4f93-880a-edfd7a63386e | Concrete |  | Corrosion-Heavy,Corrosion-Surface
01133676-c9b2-42c9-8e74-ef4c6854486e | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3217 | 118.5853 | POINT (118.585295 -20.3216797) | 2025-05-27 20:13:18 AEST | 2025-07-29 03:30:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 338 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 88654 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5834 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 338, 11 O'Clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is missing. |  | One channel anchor bolt is missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Bolt still missing. No change to condition. Low priority | no | yes |  | no |  | 30f4d209-9e6f-44a5-83e8-86967d2c3b9b |  | https://web.fulcrumapp.com/photos/view?photos=30f4d209-9e6f-44a5-83e8-86967d2c3b9b | Steel | Channel Bracket-Bolt | Missing
1839a4cf-b509-4d3d-a214-28ed8c7dd458 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 17:03:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 340 | 12 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88653 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5612 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 340, 12 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Circular joint haa drummy / delaminating grout over an area of 150mm x 150mm. Medium priorty | no |  |  |  |  | b062e88e-2bb2-4603-942d-9f6e10bce057,db1f7229-58a8-4262-b6fb-941c196ddcac | , | https://web.fulcrumapp.com/photos/view?photos=b062e88e-2bb2-4603-942d-9f6e10bce057%2Cdb1f7229-58a8-4262-b6fb-941c196ddcac | Concrete | Circular Connection,Circular Joint | Drummy
6eb3ca9e-dfe1-489f-924a-d549793dae40 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:31:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 340 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27486 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 340, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel general condition as per previous inspection. Surface corrosion noted with loss of section up to 1mm on sides. Bolt and nut corrosion has advanced. Nut fully corroded. Medium priority. | yes | no |  | no |  | 4e55d0cf-025b-42e9-9481-2abbb74c5b07,399bc16e-e9cd-4d40-bc15-75668cc91645 | 5 o'clock structural steel general condition ,Bolt condition | https://web.fulcrumapp.com/photos/view?photos=4e55d0cf-025b-42e9-9481-2abbb74c5b07%2C399bc16e-e9cd-4d40-bc15-75668cc91645 | Steel | Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Corrosion-Surface
0836986b-b48b-4430-9807-6626deedf97f | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3218 | 118.5853 | POINT (118.5853399 -20.3218446) | 2025-05-27 20:13:18 AEST | 2025-07-27 06:34:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 340 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27487 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 340,7 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock base plate as per previous inspection. Bolts corrosion has advanced. Nuts fully corroded. Medium priority. | yes | no |  | no |  | bb441882-b0bf-475b-9d94-23e47bf98be5,32fa4105-90c9-406e-9673-c35bffc290da,a5fe5485-b9f0-4e1b-b4f4-3809b8444c7a | 7 o'clock base plate general condition ,Lower bolt condition ,Middle bolt condition | https://web.fulcrumapp.com/photos/view?photos=bb441882-b0bf-475b-9d94-23e47bf98be5%2C32fa4105-90c9-406e-9673-c35bffc290da%2Ca5fe5485-b9f0-4e1b-b4f4-3809b8444c7a | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support
d7038459-05d2-41f4-bb16-ed4e54c04c5e | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 16:57:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 340 | 12 | Hydrophilic Joint Seal (Circle Joint) | Hydrophilic Joint Seal (Circle Joint) |  | 36635 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3666 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 341, 12 O'clock Hydrophilic Joint Seal (Circle Joint). |  |  |  | 200mm crack, less than 0.3mm wide. |  | 200mm crack, less than 0.3mm wide. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | No presence of crack or leakage at time of inspection. Needs to be checked again at a later stage to confirm the leak. | [5 empty] | 7bd1af9d-c1b6-4c6e-8f64-15894f6d294c,5cc2c97d-5939-4a16-98c3-a34101377002 | , | https://web.fulcrumapp.com/photos/view?photos=7bd1af9d-c1b6-4c6e-8f64-15894f6d294c%2C5cc2c97d-5939-4a16-98c3-a34101377002 | Concrete | Circular Joint | Crack,Leaks
198fa80b-18fe-4b0d-b87a-70d78eb91ef3 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 16:46:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 342 | 12 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 88655 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5892 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 342, 12 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Crack on patch repair of radial joint up to 0.7mm in width and extend up to 150mm. |  | Crack on patch repair of radial joint up to 0.7mm in width and extend up to 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Condition changed. Crack propagated to 20 mm in size. Crack propagation rate is high. Multiple cracks starting to form across the repair patch. Medium priority. | yes | yes |  |  |  | 1bff72a9-19ab-4ece-869c-f9ce4d233138,cc9636eb-8feb-436a-a6fe-1ee786e1d369 | , | https://web.fulcrumapp.com/photos/view?photos=1bff72a9-19ab-4ece-869c-f9ce4d233138%2Ccc9636eb-8feb-436a-a6fe-1ee786e1d369 | Concrete | Radial Joint | Crack
9270d560-2968-4eff-bdfd-1463af1753a0 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:40:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 342 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 27163 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 342, 2 O'Clock, Cable Tray |  |  |  | Cable tray has level 2 corrosion. |  | Cable tray has level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change to corrosion on cable tray. Low priority | no | no |  | no |  | 96f2fcc4-488b-485e-a22d-f5b6bced47b1 |  | https://web.fulcrumapp.com/photos/view?photos=96f2fcc4-488b-485e-a22d-f5b6bced47b1 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
8326eb17-334a-4488-8114-0b3b20347fb8 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3216 | 118.5852 | POINT (118.585154 -20.3216331) | 2025-05-27 20:13:18 AEST | 2025-07-29 13:36:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 343 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26945 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 343, 12 O'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. Salt deposits noted. Plug bolt has surface corrosion. Firewater pipe leak clamp installed below. Medium risk | yes | no |  |  |  | bf2c38e8-1917-4d8e-9894-45b5544082df,ce549d51-8f49-4ccd-b7de-f055ba4b067c,78c656e8-cd87-42a0-bc2b-47513f710a02,de672d25-1ee4-4538-8cb9-dd73ad3a4ff3 | ,,, | https://web.fulcrumapp.com/photos/view?photos=bf2c38e8-1917-4d8e-9894-45b5544082df%2Cce549d51-8f49-4ccd-b7de-f055ba4b067c%2C78c656e8-cd87-42a0-bc2b-47513f710a02%2Cde672d25-1ee4-4538-8cb9-dd73ad3a4ff3 | Concrete | Grout Hole,Misc (Pipes/Cable Tray/etc) | Corrosion-Surface,Leaks |  | Not reinforcement
a4e00808-4c41-42a8-8fa8-635628b4dbd5 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:25:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 344 | 12 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88656 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5903 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 344, 12 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the defect as per previous inspection. The defect is considered superficial with no structural implication. Low priority. | no | yes |  | no |  | d09955b8-c0d1-4042-ab1e-84c919e1a978 |  | https://web.fulcrumapp.com/photos/view?photos=d09955b8-c0d1-4042-ab1e-84c919e1a978 | Concrete | Circular Joint | Drummy
0be0503b-d9ca-4bd8-9d8e-8648b698eeea | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 23:46:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 344 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36636 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 344, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. The plug bolt is in good condition. Low priority. | no | yes |  | no |  | 75e5a949-b8a1-4697-b243-d9b15c3739d9,36fb3e74-cd1c-4924-8981-8df6c725374c | , | https://web.fulcrumapp.com/photos/view?photos=75e5a949-b8a1-4697-b243-d9b15c3739d9%2C36fb3e74-cd1c-4924-8981-8df6c725374c | Concrete | Grout Hole | Leaks |  | Not reinforcement
0de2b9a2-8869-485c-9bf3-de19a6ef3063 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:24:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 344 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26946 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 344, 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Steel channel support bracket has Level 4 corrosion. Bolt is missing. |  | Steel channel support bracket has Level 4 corrosion. Bolt is missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Financial | Priority: P3 |  |  |  | Replace steel channel support bracket with original design. Remove and replace corroded anchor bolt one at a time if possible. If bolt cannot be removed, carry out repair following Steel Corrosion Repair 000-S-12598 corroded anchor bolt details. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair 000-S-12598 corroded anchor bolt details. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | Dr |  | Level 5 corrosion with major surface loss and missing bolt. High priority defect and must be replaced. | yes | no |  |  |  | baa32c90-9d8f-4348-b4f3-1e5300405fe5,2895f799-8287-4f54-8bdf-c1c0ff970f40,58c4cb74-d9d2-40a9-b8e4-25d2167a3efd | ,, | https://web.fulcrumapp.com/photos/view?photos=baa32c90-9d8f-4348-b4f3-1e5300405fe5%2C2895f799-8287-4f54-8bdf-c1c0ff970f40%2C58c4cb74-d9d2-40a9-b8e4-25d2167a3efd | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
07d356c5-0cd5-4910-97ee-fe560ffbd7d2 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:23:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 344 | 5 to 6 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27491 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 344, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel is in general good condition. Bolt corrosion has advanced with the nut fully corroded. Medium priority. | yes | no |  | no |  | eaee1f88-2cc7-4ec6-bae1-aab528ebccc7,bef43256-c1e7-417f-a474-af92673b2549 | 5 o'clock structural steel general condition ,Bolt condition | https://web.fulcrumapp.com/photos/view?photos=eaee1f88-2cc7-4ec6-bae1-aab528ebccc7%2Cbef43256-c1e7-417f-a474-af92673b2549 | Steel | Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface
f296c001-74c3-4924-97b1-887974973929 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 | -20.3217 | 118.5853 | POINT (118.585268 -20.321697) | 2025-05-27 20:13:18 AEST | 2025-07-29 13:23:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 344 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27492 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 344,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock Base plate condition as per previous inspection. Bolt and nut corrosion has advanced. Medium priority. | yes | no |  | no |  | 19948beb-4219-47ae-99f6-78ea32470a81,9291ee17-fd8a-4031-97f6-1c4e2dc64f36,b586378a-3bdc-4e3a-8207-a0a841f25e60 | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition | https://web.fulcrumapp.com/photos/view?photos=19948beb-4219-47ae-99f6-78ea32470a81%2C9291ee17-fd8a-4031-97f6-1c4e2dc64f36%2Cb586378a-3bdc-4e3a-8207-a0a841f25e60 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
8cef577d-f96a-4cf2-b91f-8f42ee0fb700 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 23:00:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 346 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 27164 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 346, 2 O'Clock, Cable Tray |  |  |  | Cable tray has level 1 corrosion |  | Cable tray has level 1 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Cable tray is still corroded. Not a structural defect. Low priority. | no | no |  |  |  | da43e734-fa66-4fb6-9819-5e44992ad556 |  | https://web.fulcrumapp.com/photos/view?photos=da43e734-fa66-4fb6-9819-5e44992ad556 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
3557cfaa-5e32-402e-9afe-074fefc31102 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:22:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 347 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36637 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 347, 2 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive at the front of inspection. Grout plug is in good condition. Low priority defect. | no | no |  |  |  | 52fb7e4d-d3d4-477d-9487-6f9a2d8db067,8fcdd873-e0dc-4f2c-a63d-914275f29463 | , | https://web.fulcrumapp.com/photos/view?photos=52fb7e4d-d3d4-477d-9487-6f9a2d8db067%2C8fcdd873-e0dc-4f2c-a63d-914275f29463 | Concrete | Grout Hole | Leaks |  | Not reinforcement
53bd15ed-3b9a-40d4-90e6-c04fe16321cc | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3218 | 118.5853 | POINT (118.5853399 -20.3218403) | 2025-05-27 20:13:18 AEST | 2025-07-29 13:18:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 347 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 101847 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 19/09/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Missing Components |  | Missing Components | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 347, 4 o'clock, Cathodic protection cable | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Cathodic protection cable is severed. |  | Cathodic protection cable is severed. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | Renew Cathodic Protection Continuity Cable. | Cathodic Protection Technician | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | Bogdan Stanca |  | The defect is still present. Cathodic protection cable detached from the segment. High priority. | no | no |  | no |  | 15dcaba4-0f11-4257-860c-41eaec9c22b1,3be53676-efd9-4171-9b0b-126287c1063c | , | https://web.fulcrumapp.com/photos/view?photos=15dcaba4-0f11-4257-860c-41eaec9c22b1%2C3be53676-efd9-4171-9b0b-126287c1063c | Concrete | Misc (Pipes/Cable Tray/etc) | Missing |  | Misc
57fdf2b6-b533-4679-9ec8-55201d28b789 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:47:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 348 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27493 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 348, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 5 o'clock structural steel condition has advanced from the last inspection. There is no evidence of water leak at joints however,the steel plate and bolt is typically covered by a moist iron spill that provides a corrosion environment. Medium priority. | yes | no |  | no |  | 9a803929-bc53-4179-be66-e1713d04e451,56c46d8a-68d0-4f92-a7dd-9714f0d1732c,adbd87e0-94ea-4f3c-9b11-c197b8f0de1b | 5 o'clock structural steel general condition ,Bolt condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=9a803929-bc53-4179-be66-e1713d04e451%2C56c46d8a-68d0-4f92-a7dd-9714f0d1732c%2Cadbd87e0-94ea-4f3c-9b11-c197b8f0de1b | Steel | Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Leaks
0a5396f1-f25c-43b8-9f3a-fae63b76e747 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:42:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 348 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27494 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 348,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock base plate bolts corrosion has advanced with bolt nuts fully corroded. Medium priority. | yes | no |  | no |  | 25179e17-9572-4b45-a452-a2c8078bb7f0,35950c8e-850d-462e-a007-fd052d96510c,f865dc56-bdd2-495f-a826-e7b0a4c974bf | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition | https://web.fulcrumapp.com/photos/view?photos=25179e17-9572-4b45-a452-a2c8078bb7f0%2C35950c8e-850d-462e-a007-fd052d96510c%2Cf865dc56-bdd2-495f-a826-e7b0a4c974bf | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support
298a4ef3-66f6-4aed-b2b0-2195b9ece792 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:05:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 350 | 2 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88657 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5914 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 350, 2 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. Concrete spalled over an area of 100mm x 50mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. Concrete spalled over an area of 100mm x 50mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | No change to condition of the defect. Defect is at 1 O Clock and not at 2 O Clock. Low risk | no | yes |  |  |  | 8a2d346d-6bdc-436c-9f78-8de5f4dbd191 |  | https://web.fulcrumapp.com/photos/view?photos=8a2d346d-6bdc-436c-9f78-8de5f4dbd191 | Concrete | Circular Joint | Drummy,Surface Damage
53c3656e-0be9-4616-b20a-55b867c32bbf | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:05:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 350 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 26947 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 350, 2 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolt has Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolt has Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | Steel channel bracket not corroded. Bolt is corroded and loose. Low priority. Defect is at 3 O Clock. Low risk | yes | yes |  | yes | At 3 not 2. | c8d27a00-a593-43a7-ae30-17716ac182ad |  | https://web.fulcrumapp.com/photos/view?photos=c8d27a00-a593-43a7-ae30-17716ac182ad | Steel | Channel Bracket,Channel Bracket-Bolt | Loose
7c103095-7c8a-41c2-96e7-b3fb5d5dd221 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:02:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 352 | 12 | Grout Injection Hole | Grout Injection Hole |  | 88658 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 352, 12 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Active at time of inspection. |  | Grout injection hole has leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Scheduled Maintenance Competent Supervisor | DR |  | Leak is active at the time of inspection. Salt deposit has collected into the grout plug. Leak has made the reinforcement to start corroding. Steel bracket supporting the pipe below has leve2 corrosion due to the leak. Condition of grout plug is unknown due to salt deposit. High priority remediation. High risk | yes | yes |  | yes |  | 608b8bb4-ea92-46a6-81f4-0d89392ecd02,91697a85-eddb-43c0-93a6-2a4abb615b55,97e0f05b-6373-4e09-966b-9f7581f83cb9,dcd310c2-55da-4144-b05a-bc35c72c851e,fc9b5395-b5ff-4e1a-9c39-4a45eec5e1de | ,,,, | https://web.fulcrumapp.com/photos/view?photos=608b8bb4-ea92-46a6-81f4-0d89392ecd02%2C91697a85-eddb-43c0-93a6-2a4abb615b55%2C97e0f05b-6373-4e09-966b-9f7581f83cb9%2Cdcd310c2-55da-4144-b05a-bc35c72c851e%2Cfc9b5395-b5ff-4e1a-9c39-4a45eec5e1de | Steel | Grout Hole,Misc (Pipes/Cable Tray/etc) | Leaks |  | Not reinforcement
ec081e57-bca9-4d72-b36d-84695a8ec766 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:37:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 352 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 76405 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44732.2372 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 352, 2 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Corrosion on bolt and steel bracket have both advanced. With about 10 mm surface loss on the plate. Must be replaced. Medium priority | yes | no |  |  |  | 0a3d978a-8df1-443a-97f8-0cd57f635d98 |  | https://web.fulcrumapp.com/photos/view?photos=0a3d978a-8df1-443a-97f8-0cd57f635d98 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
af61acca-5fd5-422f-b167-d89d98c7212b | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:20:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 352 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36639 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3707 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 352, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock corrosion has advanced. Surface corrosion to base plate observed. 5 o'clock structural steel defect corrosion has advanced. | yes | no |  | no |  | 747d0e65-2fb4-4dd2-9c69-0197bf9239a9,1a6feda5-2a80-4895-a8e6-6beffb0109b7,125613b3-7672-485f-8026-bfe4b5b96aca,e3105595-fe71-40c1-8d19-6c1f4c6da83d,0d6d4a0d-db60-4346-8356-d5ea786a087d,bb2d5d5d-533e-4a39-8012-2caec22b9a38 | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition ,5 o'clock structural steel general condition ,Bolt condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=747d0e65-2fb4-4dd2-9c69-0197bf9239a9%2C1a6feda5-2a80-4895-a8e6-6beffb0109b7%2C125613b3-7672-485f-8026-bfe4b5b96aca%2Ce3105595-fe71-40c1-8d19-6c1f4c6da83d%2C0d6d4a0d-db60-4346-8356-d5ea786a087d%2Cbb2d5d5d-533e-4a39-8012-2caec22b9a38 | Steel | Channel Bracket-Bolt,Walkway Support | Corrosion-Surface
2f9d09a2-a9de-46cd-a4ad-a561afd29d80 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 13:00:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 353 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27196 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring: 353, 12 O'clock: Grout Injection Hole. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The condition of the defect has not changed from the previous inspection. The leak is not active. Salt deposits noted. Plug bolt is in good condition. Low priority | no | yes |  | no |  | f07b25e9-448d-4cb7-b9a7-638d44148a0a,b071c9f1-7a52-4e69-b15c-3dcce5ed4732,9cb6671a-9c29-4d1f-84ff-8c84be2a8ac8 | ,, | https://web.fulcrumapp.com/photos/view?photos=f07b25e9-448d-4cb7-b9a7-638d44148a0a%2Cb071c9f1-7a52-4e69-b15c-3dcce5ed4732%2C9cb6671a-9c29-4d1f-84ff-8c84be2a8ac8 | Concrete | Grout Hole | Leaks |  | Not reinforcement
b2d40eb8-4424-4c9e-8cb9-28999df9ce88 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:51:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 356 | 4 to 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36640 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3718 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 356, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | 7 o'clock defect does not appear to advance. The base plate presents surface corrosion. 5 o'clock defect appears to advance with bolt nut fully corroded and lower Base plate section loss up to 1mm. Medium priority. | yes | no |  | no |  | 15148074-d1e0-4ba4-8777-af58a143790d,1bdd8794-9666-4272-bae3-b1fde9eeaf17,7b6e77f4-b408-41ec-8df5-b22268be09da,166615f9-e218-4198-8db3-c527e3110e12,1e9a3a4a-3020-44a3-9a5e-8c1f7489ce48,63d434f9-b74d-4e01-91c7-680c824a74ea | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition ,5 o'clock structural steel general condition ,Bolt condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=15148074-d1e0-4ba4-8777-af58a143790d%2C1bdd8794-9666-4272-bae3-b1fde9eeaf17%2C7b6e77f4-b408-41ec-8df5-b22268be09da%2C166615f9-e218-4198-8db3-c527e3110e12%2C1e9a3a4a-3020-44a3-9a5e-8c1f7489ce48%2C63d434f9-b74d-4e01-91c7-680c824a74ea | Steel | Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface
14e3eb53-94e5-44fe-8453-ecca45d8c115 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:15:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 357 | 1 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 36641 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 357, 1 O'clock Hydrophilic Joint Seal (Circle Joint). | Failure to seal joint | Failure to seal joint |  | Circle joint seal has Leak Inactive at time of inspection. |  | Circle joint seal has Leak Inactive at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | HSE | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Dr |  | No change to the condition of the defect. Inactive at time of inspection. Low priority. | no | no |  |  |  | 6fbaedeb-f34c-4055-bb75-b55eaff4e4cd |  | https://web.fulcrumapp.com/photos/view?photos=6fbaedeb-f34c-4055-bb75-b55eaff4e4cd | Concrete | Circular Joint | Leaks |  | Not reinforcement
5bda9ac0-8f77-41a2-a572-34de92c8cd98 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 22:14:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 357 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27165 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 357, 2 O'Clock and 3 O'Clock, Cable Tray |  |  |  | Cable tray has level 2 corrosion. |  | Cable tray has level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change to corrosion levels. Not a structural defect. Low priority | no | no |  |  |  | 5d882b34-c38a-4238-8321-4661057ffc0f |  | https://web.fulcrumapp.com/photos/view?photos=5d882b34-c38a-4238-8321-4661057ffc0f | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
89243f71-adaf-4f4e-a384-6fa9e3d4a13d | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3218 | 118.5854 | POINT (118.585375 -20.3217633) | 2025-05-27 20:13:18 AEST | 2025-07-29 12:43:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 358 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26950 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 358, 11 O'clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Bogdan Stanca |  | The leak is at the 11 o'clock injection hole. The leak is active at the time of inspection. The steel plug not visible for inspection. The leak has affected the condition of the steel channel as well as the support of the top conveyor that presents advanced corrosion with significant loss of section. High priority. | yes | no |  | no |  | af260108-5bab-4b21-92ba-444d71740860,f2aa7529-946b-4d63-bd0b-17acd893e323,15e182d5-d2dd-46a9-9dc3-9b6f24529031,73ff16d3-8ac9-45d8-8f5c-e2b71c64e7ad,c6fba2c9-9a68-478c-b3df-90dbd8d5a3da,be8bb84b-93ad-40df-ab9b-8b29d9094c8a,8d265a42-0c93-4d26-b1d7-588772922d5f | ,,Top conveyor support condition ,Top conveyor support condition ,Top conveyor support condition ,Top conveyor support condition ,Adjacent top conveyor support for reference | https://web.fulcrumapp.com/photos/view?photos=af260108-5bab-4b21-92ba-444d71740860%2Cf2aa7529-946b-4d63-bd0b-17acd893e323%2C15e182d5-d2dd-46a9-9dc3-9b6f24529031%2C73ff16d3-8ac9-45d8-8f5c-e2b71c64e7ad%2Cc6fba2c9-9a68-478c-b3df-90dbd8d5a3da%2Cbe8bb84b-93ad-40df-ab9b-8b29d9094c8a%2C8d265a42-0c93-4d26-b1d7-588772922d5f | Concrete,Steel | Grout Hole | Corrosion-Heavy,Leaks |  | Not reinforcement
8beb156f-63a7-48fc-b415-82f1abedef99 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 | -20.3216 | 118.5852 | POINT (118.5851853 -20.3215706) | 2025-05-27 20:13:18 AEST | 2025-07-27 00:45:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 358 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27495 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Corrosion Under Buildup |  | Corrosion Under Buildup | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 358, 11 O'clock, Steel Channel Bracket and Anchor Bolt | Rupture | Rupture |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Financial | Priority: P3 |  |  |  | Replace damaged bolts one at a time as per original design specification. Remove corrosion by abrasive blasting or mechanical means and reinstate protective coatings in accordance with BHP specifications. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair Guideline 0136559. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor | Bogdan Stanca |  | The corrosion of the steel channel has advanced. The corrosion on the back of the channel web is putting pressure on the anchor nuts. High priority. | yes | no |  | no |  | c0b98ee2-a40f-4a12-befd-6ae9116e7a93,d5405771-7463-4516-9474-c88eaa8fcff0,d84d2584-a6ae-43fa-affe-cb927a02910f | ,, | https://web.fulcrumapp.com/photos/view?photos=c0b98ee2-a40f-4a12-befd-6ae9116e7a93%2Cd5405771-7463-4516-9474-c88eaa8fcff0%2Cd84d2584-a6ae-43fa-affe-cb927a02910f | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
43167e70-80c6-4e68-a33d-97af83c889fa | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:32:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 358 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26949 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 358, 3 O'clock, Steel Channel Bracket and Anchor Bolt | Rupture | Rupture |  | Steel channel support bracket has Level 5 corrosion and Channel anchor bolts have Level 4 corrosion. |  | Steel channel support bracket has Level 5 corrosion and Channel anchor bolts have Level 4 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Financial | Priority: P3 |  |  |  | Replace steel channel support bracket with original design. Remove and replace corroded anchor bolt one at a time if possible. If bolt cannot be removed, carry out repair following Steel Corrosion Repair 000-S-12598 corroded anchor bolt details. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair 000-S-12598 corroded anchor bolt details. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | DR |  | Corrosion of the steel channel bracket and bolt have expanded. High priority defect and must be replaced. High risk. | yes | no |  |  |  | 69284470-f43a-441e-b6f4-2ecb85caa178,6f0cf841-05a6-4294-abf5-ac5ff8d3e4a7 | , | https://web.fulcrumapp.com/photos/view?photos=69284470-f43a-441e-b6f4-2ecb85caa178%2C6f0cf841-05a6-4294-abf5-ac5ff8d3e4a7 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
e24b8b18-4fda-46aa-8ce6-bd76b35f6e30 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:29:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 358 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 76406 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 358, 4 O'Clock, Segmented Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | hse | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | DR |  | Area of delaminated and drummy concrete remains the same. Moderate priority defect. Defect is present at 5 O clock and not 4. | no | yes |  | yes | Update to 5 O clock. | 34e11315-e635-4e63-ab13-38cf2c7bb85f,39869fbb-30a7-4c51-ae64-f0c98fd8bac3,74120ceb-350a-42de-ae82-ec7c45e26375,6d5dcb33-fbb6-49da-8b09-6cc838d6236a | ,,, | https://web.fulcrumapp.com/photos/view?photos=34e11315-e635-4e63-ab13-38cf2c7bb85f%2C39869fbb-30a7-4c51-ae64-f0c98fd8bac3%2C74120ceb-350a-42de-ae82-ec7c45e26375%2C6d5dcb33-fbb6-49da-8b09-6cc838d6236a | Concrete | Radial Joint | Drummy
2bceccf9-db3d-48b9-9ca6-2e0ec0b8020c | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 23:17:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 358 | 0 | Grout Injection Hole | Grout Injection Hole |  | 36642 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 358, 8 & 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | Grout injection hole located at 9 o'clock. Leak not active at the time of inspection. Plug bolt has surface corrosion. Low priority. | no | yes |  | no |  | 2d48f0ef-e774-4844-aff0-cbbe3e979924,ee1e3f2f-cb50-4657-b71a-9f8afad700f4 | , | https://web.fulcrumapp.com/photos/view?photos=2d48f0ef-e774-4844-aff0-cbbe3e979924%2Cee1e3f2f-cb50-4657-b71a-9f8afad700f4 | Concrete | Grout Hole | Corrosion-Surface,Leaks |  | Not reinforcement
952c1fdc-6dcf-46e2-9508-6f20d1bfb374 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 22 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:21:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 360 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 101848 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 19/09/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Unknown | Unknown |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 360, 1 o'clock, Ring (Segmental Concrete) - Damage Affecting Single Ring | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 150mm x 150mm adjacent the previous patch repair. |  | Concrete shell segment has drummy concrete over an area of 150mm x 150mm adjacent the previous patch repair. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | No change to condition of the defect. Low risk | no | yes |  | no |  | 3ae248a2-b8e0-4dee-85fb-e3b493060797,ec60515a-7f7e-4647-983e-135b3d2479dc | , | https://web.fulcrumapp.com/photos/view?photos=3ae248a2-b8e0-4dee-85fb-e3b493060797%2Cec60515a-7f7e-4647-983e-135b3d2479dc | Concrete |  | Drummy |  | Not reinforcement
37e4424d-b515-4ed0-a8a9-e2eaa11a5050 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 21 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 03:31:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 360 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27496 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 360, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of steel at 7 o'clock has further deteriorated. 5 o'clock structural steel corrosion has advanced. | [5 empty] | f682e154-a3e1-4356-a013-676053a8f43a,59afe36e-f52b-4ecc-9dfb-3bde1f753345,b73c32b4-c868-4364-ac8e-1ea3ef5f93d6,272a2c0f-fec3-4374-8285-4569c7397ab7,ae449e46-26a8-4906-91c3-9ed32619e33e,e9129866-f909-46e8-9f61-1415a9b46270,450bacb0-07b4-49e1-8c75-f2f217944f9e | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition and steel plate loss of section up to 1mm ,Top bolt condition ,5 o'clock structural steel general condition ,Bolt condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=f682e154-a3e1-4356-a013-676053a8f43a%2C59afe36e-f52b-4ecc-9dfb-3bde1f753345%2Cb73c32b4-c868-4364-ac8e-1ea3ef5f93d6%2C272a2c0f-fec3-4374-8285-4569c7397ab7%2Cae449e46-26a8-4906-91c3-9ed32619e33e%2Ce9129866-f909-46e8-9f61-1415a9b46270%2C450bacb0-07b4-49e1-8c75-f2f217944f9e | Steel | Channel Bracket,Channel Bracket-Bolt,Walkway Support | Corrosion-Heavy,Corrosion-Surface
d3d1fe21-f874-4bfd-87a5-2edfece599e4 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 16 |  |  |  | 2025-07-27 22:20:18 AEST | 2025-07-29 12:54:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 354 | 3 O Clock |  | Steel Channel Bracket | [15 empty] | Corrosion of Reinforcement | [41 empty] | DR |  | Missing bolt and level 2 corrosion on the steel bracket. Must be replaced. Medium risk |  | yes |  |  |  | 25246e13-144a-4a49-8b6d-8bcf0864bd3f |  | https://web.fulcrumapp.com/photos/view?photos=25246e13-144a-4a49-8b6d-8bcf0864bd3f | Steel | Channel Bracket,Channel Bracket-Bolt | Missing |  | Not reinforcement
8ef647f6-9849-4d3e-942d-bb15cf7ff288 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 16 |  |  |  | 2025-07-27 22:22:05 AEST | 2025-07-29 12:55:43 AEST | 30011704-user5@smec.com | james.stone@smec.com | 354 | 11 O' Clock |  | Steel Channel Bracket | [57 empty] | Dr |  | Steel bracket for the light has level 2 corrosion. Low priority |  | yes |  | no |  | 7df57168-ca37-4e78-b87c-819175776624,90c1e892-46e1-41db-aa19-b4601bbf6cef | , | https://web.fulcrumapp.com/photos/view?photos=7df57168-ca37-4e78-b87c-819175776624%2C90c1e892-46e1-41db-aa19-b4601bbf6cef | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
29622ff8-986d-47b9-a5c4-38bbf50fdc32 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 16 |  |  |  | 2025-07-27 22:45:27 AEST | 2025-07-27 22:46:55 AEST | 30011704-user5@smec.com | james.stone@smec.com | 352 | 1 O Clock. |  | Steel Channel Bracket | [57 empty] | Dr |  | Steel channel bracket have level 2 corrosion. Anchor bolts missing. Medium priority Defect |  | yes |  | no |  | 5f3c4b08-ee5b-49a9-826d-7e38d4164fcc |  | https://web.fulcrumapp.com/photos/view?photos=5f3c4b08-ee5b-49a9-826d-7e38d4164fcc | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
dc2e9bdb-6609-4dec-abda-c183703d2e38 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 16 |  |  |  | 2025-07-27 23:12:49 AEST | 2025-07-27 23:13:55 AEST | 30011704-user5@smec.com | james.stone@smec.com | 343 | 1 O Clock | [59 empty] | Dr |  | Concrete delamination at patchwork of 200x 200mm. Medium priority. | [5 empty] | 1bbf2ffc-5bda-4309-8f30-e0f9df7ae129,0acd2f39-e280-4db4-8db0-a2c59de505da | , | https://web.fulcrumapp.com/photos/view?photos=1bbf2ffc-5bda-4309-8f30-e0f9df7ae129%2C0acd2f39-e280-4db4-8db0-a2c59de505da | Concrete | Grout Hole | Drummy |  | Grout Hole
5507248c-7112-4640-ab7e-03b2af82a0a2 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 4 |  |  |  | 2025-07-29 17:29:20 AEST | 2025-07-29 17:33:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 333 | 2 |  | Grout Injection Hole | [32 empty] | O’clock, filled grout hole | [24 empty] | BP AA |  | Filled injection grout hole. No keak. Low risk |  | yes |  | no |  | f7eb2531-2423-4ab6-b98f-e7123633c202 |  | https://web.fulcrumapp.com/photos/view?photos=f7eb2531-2423-4ab6-b98f-e7123633c202 | Concrete | Grout Hole
07ed6d49-5260-4062-9ed8-09088febaad2 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 11879e43-89b0-4462-b3ed-a822c8a2f994 | 4 |  |  |  | 2025-07-29 17:36:43 AEST | 2025-07-29 17:46:02 AEST | 30011704-user5@smec.com | james.stone@smec.com | 331 | 3 O’clock |  | Grout Injection Hole | [32 empty] | Inactive grout hole | [24 empty] | AS BP |  | Inactive grout hole. Low risk | [5 empty] | 905e1739-567b-48f2-acd6-6a6392db2e1d,44c99131-51ff-4076-a295-549c8e043e09 | , | https://web.fulcrumapp.com/photos/view?photos=905e1739-567b-48f2-acd6-6a6392db2e1d%2C44c99131-51ff-4076-a295-549c8e043e09 | Concrete | Grout Hole
e0bfad9d-7f10-48fc-94f6-c6e3808a249c | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:13:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 361 | 3 ?- Consider removing entry | Steel Channel Bracket | Steel Channel Bracket |  | 27497 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 361,3 O'Clock,Ducting,Identified in 2018 |  |  |  | Cable tray, Class 3 - Medium corrosion |  | Cable tray, Class 3 - Medium corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Dr |  | No corrosion on cable tray. Remove defect. | no | no |  |  |  | 161514f8-3a65-49d5-9ea2-0897c3b68550,da4394ba-1fde-4d2b-ae54-0fdfeb464a99,55f73106-c1f9-42e2-b0ef-4a52af77951b | ,, | https://web.fulcrumapp.com/photos/view?photos=161514f8-3a65-49d5-9ea2-0897c3b68550%2Cda4394ba-1fde-4d2b-ae54-0fdfeb464a99%2C55f73106-c1f9-42e2-b0ef-4a52af77951b | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) |  |  | no corrosion
f9d8e6ba-17e4-419f-a7f9-c2b1515af087 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 03:10:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 362 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26953 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 362, 1 & 12 O'clock, Hydrophilic Joint Seal (Circle Joint). | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Hydrophilic Joint Seal (Circle Joint) seal has Leak Inactive at time of inspection. |  | Hydrophilic Joint Seal (Circle Joint) seal has Leak Inactive at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive at time of inspection. Reinforcement is heavily corroded. High priority defect. | no | no |  |  |  | e1ca5674-ef85-4468-b317-fd060dae69e2,f22cb23a-7b0d-446d-b17f-d1f7cc6a98b6 | , | https://web.fulcrumapp.com/photos/view?photos=e1ca5674-ef85-4468-b317-fd060dae69e2%2Cf22cb23a-7b0d-446d-b17f-d1f7cc6a98b6 | Concrete | Circular Joint | Leaks |  | Not a reinforcement
fdcc773d-752e-41c4-ab49-6ef1e034eac4 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:45:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 362 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36643 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3742 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 362, 11 O'clock, Channel Anchor Bolts |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | Loose nut still present. Low priority | no | yes |  | no |  | c851c0bf-3dca-449d-973c-47b2b7e053c6,41fc94b4-0689-4dc7-b260-63c96650d9e8 | , | https://web.fulcrumapp.com/photos/view?photos=c851c0bf-3dca-449d-973c-47b2b7e053c6%2C41fc94b4-0689-4dc7-b260-63c96650d9e8 | Steel | Channel Bracket-Bolt | Loose
67eb5cc6-0622-4e3c-abdd-0357565540dd | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 20:16:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 362 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 76407 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 362, 4 O'Clock, Segmented Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | HSE | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | Area of drummy and delaminated concrete has not changed. Condition has changed with cracks and spalling of the concrete. High priority | yes | no |  | yes | Location must be changed to 5 O Clock and not 4. | 699fed82-5dbc-4a7e-a4da-cf43b28d369d,e844badd-b4fa-4eba-aa87-a9fdee7703ad,c6a34022-9f63-4bfe-b6ea-a2660849e410,e75aa0a4-6dc3-4189-b1a2-e5fa579d4ff4 | ,,, | https://web.fulcrumapp.com/photos/view?photos=699fed82-5dbc-4a7e-a4da-cf43b28d369d%2Ce844badd-b4fa-4eba-aa87-a9fdee7703ad%2Cc6a34022-9f63-4bfe-b6ea-a2660849e410%2Ce75aa0a4-6dc3-4189-b1a2-e5fa579d4ff4 | Concrete | Radial Joint | Crack,Drummy,Surface Damage
670a19b6-2a8b-416e-9400-13da5467dfed | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 03:09:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 362 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27498 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 362,3 O'Clock,Ducting,Identified in 2018 |  |  |  | Cable tray, Class 4 - Medium high corrosion |  | Cable tray, Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Dr |  | No corrosion of cable tray. Not a defect. | yes | no | No defect. | yes | Remove defect. | 6480f25e-3443-4d16-81c9-a8bf8a53e479,54f6d985-2dfb-42f8-9d0e-9563c3f2ace3 | , | https://web.fulcrumapp.com/photos/view?photos=6480f25e-3443-4d16-81c9-a8bf8a53e479%2C54f6d985-2dfb-42f8-9d0e-9563c3f2ace3 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
d2e332bc-cdf8-47a4-8703-6aec084e3b77 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 03:08:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 362 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26952 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 362,3 O'Clock,Ducting,Still existing in 2017. |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | DR |  | No corrosion present on the steel bracket at the time of inspection. | yes | no | Low priority | no |  | f48ac8f8-3505-4753-8936-d579ddb5ece6,f9f2fa8d-59a3-408f-9e2a-2cc3dd9f3fc0 | , | https://web.fulcrumapp.com/photos/view?photos=f48ac8f8-3505-4753-8936-d579ddb5ece6%2Cf9f2fa8d-59a3-408f-9e2a-2cc3dd9f3fc0 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
19f81db8-f182-431e-ae05-f7bfb4e00ae8 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:10:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 363 | 12 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 76408 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44732.2431 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 363, 12 O'Clock, Segmented Bolted Joint (Circle Joint). |  |  |  | Circle joint has delamination and minor spalling damage up to 100mm x 100mm. |  | Circle joint has delamination and minor spalling damage up to 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the defect is as per previous inspection. The defect is considered superficial with no structural implication. Low priority | no | yes |  | no |  | 30cbb151-68c0-4a6f-9255-56e2b4002465,ebfd785b-5829-4386-80ba-cf37e66b84f8 | , | https://web.fulcrumapp.com/photos/view?photos=30cbb151-68c0-4a6f-9255-56e2b4002465%2Cebfd785b-5829-4386-80ba-cf37e66b84f8 | Concrete | Circular Joint | Drummy,Surface Damage
78a8d3f5-5729-44df-993f-cd89a143b88b | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:10:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 363 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26954 |  | 6655 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 4/04/2022 |  | 4/04/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Structure,Ring 363,3 O'Clock,Concrete Element,Leak found Dry in 2017 | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint seal has Leak Inactive at time of inspection. |  | Circle joint seal has Leak Inactive at time of inspection. | Rare (Failure within 50 years) |  | Rare (Failure within 50 years) | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Monitor leak condition at the next inspection if it is still dry then monitor. If active the update to P2 and fixed | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | Dr |  | Leak at the circumferential joint still remains inactive at time of inspection. No change to the condition of the defect from previous inspection. Moderate priority defect. | no | no |  |  |  | 6cd1c17f-8e84-4b26-a0cf-d9c8f2efa824,9896113e-8e4b-41f8-b985-1eb4ebb2f8d6 | , | https://web.fulcrumapp.com/photos/view?photos=6cd1c17f-8e84-4b26-a0cf-d9c8f2efa824%2C9896113e-8e4b-41f8-b985-1eb4ebb2f8d6 | Concrete | Circular Connection,Circular Joint | Leaks |  | Not a reinforcement
730237cc-a72b-49cd-8b64-d7a5f09b5852 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 02:56:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 363 | 8 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27166 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 363,8 O'Clock,Bolt, Nut, Washer,New Defect 2017 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | There is no bolt at 8 o'clock. Possible reference to the top bolt of the support plate at 7 o'clock on Ring 364. | [8 empty] | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
998649c0-135e-401e-9470-646e367cb29f | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 12:07:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 364 | 5, 6 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27499 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 364, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect at 7 o'clock doesn't appear to advance. Surface corrosion to base plate. 5 o'clock defect condition has deteriorated further with structural steel loss of section up to 1mm and bolt and nut further corroded. Medium priority. | yes | no |  | no |  | 72118691-1d53-40b8-8e9d-bdf5e8d07fa4,044035e4-363a-4323-b04c-f78648c41bee,ad67254c-2dee-47be-8221-084caa7fcb43,ed3c54ef-73ae-40e7-83f5-d35761e05e83,dd9d1081-1978-477f-b091-57a2160b4d52,3ecb283e-620b-4890-8ca1-48f0234977cf,c6f91c1b-ed02-41ec-a7e0-ace3de12df74 | 7 o'clock Base plate general condition ,Lower bolt condition ,Middle bolt condition ,Top bolt condition ,5 o'clock structural steel condition ,Bolt and nut condition ,Structural Steel condition | https://web.fulcrumapp.com/photos/view?photos=72118691-1d53-40b8-8e9d-bdf5e8d07fa4%2C044035e4-363a-4323-b04c-f78648c41bee%2Cad67254c-2dee-47be-8221-084caa7fcb43%2Ced3c54ef-73ae-40e7-83f5-d35761e05e83%2Cdd9d1081-1978-477f-b091-57a2160b4d52%2C3ecb283e-620b-4890-8ca1-48f0234977cf%2Cc6f91c1b-ed02-41ec-a7e0-ace3de12df74 | Steel | Conveyor Support | Corrosion-Surface |  | Conveyor Support not Channel Bracket
6192474f-0253-4f6e-bef4-8c823090497f | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:39:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 365 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27167 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 365, 8 O'clock Grout Injection Hole |  |  |  | Grout Delamination / debonding at the grout patch repair inside grout injection hole. |  | Grout Delamination / debonding at the grout patch repair inside grout injection hole. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect condition as per previous inspection. The leak is not active at the time of inspection. | no | yes |  | no |  | 129051bb-0395-43ed-b18b-a8662386cb55 |  | https://web.fulcrumapp.com/photos/view?photos=129051bb-0395-43ed-b18b-a8662386cb55 | Concrete | Grout Hole | Drummy,Leaks
8144735c-9c11-4dac-904b-bff2104cbb97 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 06:24:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 366 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36644 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 366, 3 O'clock, Steel Channel Bracket and Anchor Bolt | Rupture | Rupture |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Not Specified | Priority: P3 |  |  |  | Replace damaged bolts one at a time as per original design specification. Remove corrosion by abrasive blasting or mechanical means and reinstate protective coatings in accordance with BHP specifications. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair Guideline 0136559. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor | Dr |  | Corrosion has advanced. High priority defect | yes | yes |  |  |  | 5ca8bb34-d645-499b-b62e-7fd9e9661844 |  | https://web.fulcrumapp.com/photos/view?photos=5ca8bb34-d645-499b-b62e-7fd9e9661844 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
5079c36d-90b0-4055-b7a6-895b11823253 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:37:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 366 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26955 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 366, 3 to 4 O'Clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | Dr |  | Leak is still active at time of inspection. Collection of salt present on the concrete surface. Leak has caused severe corrosion to the steel bracket and the channel anchor bolts. High priority defect. | yes | yes |  | no |  | 626e99ab-1b01-4fb0-a3bb-7d37953c0117,705f676c-9f28-46b8-bcf9-739b9949c927,c51bc9dd-c770-46e5-8211-0432f4c76379,fa5d8033-e1da-436a-8760-0d622f497e46,fa7fe671-af76-488a-a6a9-60ded0ed5fad | ,,,, | https://web.fulcrumapp.com/photos/view?photos=626e99ab-1b01-4fb0-a3bb-7d37953c0117%2C705f676c-9f28-46b8-bcf9-739b9949c927%2Cc51bc9dd-c770-46e5-8211-0432f4c76379%2Cfa5d8033-e1da-436a-8760-0d622f497e46%2Cfa7fe671-af76-488a-a6a9-60ded0ed5fad | Concrete,Steel | Channel Bracket-Bolt | Corrosion-Heavy,Leaks |  | Not a reinforcement
1746dbda-b66c-44e9-9e2b-9229fff8416c | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:35:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 367 | 8 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27169 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 367,8 O'Clock,Bolt, Nut, Washer,New Defect 2017 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | Not clear where the bolt is located. Refer to 7 o'clock Base plate condition and associate bolts for current condition. | [8 empty] | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
b652c6da-778c-4e47-990f-f114a1b7d9e1 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:32:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 368 | 5 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36647 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3763 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 368, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. |  | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the 7 o'clock bolts has further deteriorated. The condition of the structural steel and bolt at 5 o'clock has further deteriorated. Medium priority. | yes | no |  | no |  | f12c8c7c-7f9a-4c44-89a7-863c325891b8,b45d5043-83bd-414c-9b8d-ae7a7b6df9d4,d8babc24-23ed-442c-8cda-2d1fea909519,ff509880-bb64-4db4-9616-78675ab0e0fb,b37c23cc-6d7c-4580-9657-b4b75049e248,551fc313-a64e-4526-9e8f-375399d969b9,3e2e4985-b8ca-44b4-a3eb-0272ae4cd031 | 7 o'clock Base plate general view ,Lower bolt condition ,Middle bolt condition ,Top bolt condition ,5 o'clock steel plate condition ,5 o'clock bolt condition ,Steel condition | https://web.fulcrumapp.com/photos/view?photos=f12c8c7c-7f9a-4c44-89a7-863c325891b8%2Cb45d5043-83bd-414c-9b8d-ae7a7b6df9d4%2Cd8babc24-23ed-442c-8cda-2d1fea909519%2Cff509880-bb64-4db4-9616-78675ab0e0fb%2Cb37c23cc-6d7c-4580-9657-b4b75049e248%2C551fc313-a64e-4526-9e8f-375399d969b9%2C3e2e4985-b8ca-44b4-a3eb-0272ae4cd031 | Steel | Channel Bracket-Bolt,Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Corrosion-Surface
4fccf8ba-6a83-4140-9adc-d5c216ea18a2 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:32:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 368 | 5 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36648 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.3772 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 368, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 5). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect note appears to be a duplication. Refer to the other defect note for the current condition. | [8 empty] | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
fc59170c-fb50-4f7d-8f80-e1bca231d1d4 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:27:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 369 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36649 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 369, 2 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is inactive at time of inspection. Grout plug in good condition. Low priority defect. |  | no |  |  |  | 03016513-04e2-424c-b38e-8d23ee825674,b91cf661-06a0-4d25-b345-bb4942272c60 | , | https://web.fulcrumapp.com/photos/view?photos=03016513-04e2-424c-b38e-8d23ee825674%2Cb91cf661-06a0-4d25-b345-bb4942272c60 | Concrete | Grout Hole | Leaks |  | Not a reinforcement
381f6f37-fce8-4cc0-b044-f4c9769846eb | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:26:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 370 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36650 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.379 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 370, 11 O'clock: Channel Anchor Bolts. |  |  |  | Level 1 corrosion at anchor bolts of steel bracket. Protective coating breakdown on steel bracket. |  | Level 1 corrosion at anchor bolts of steel bracket. Protective coating breakdown on steel bracket. | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect condition as per previous inspection. | no | yes |  | no |  | e9f27f3c-cdf3-4588-a36a-eba8924ba384 |  | https://web.fulcrumapp.com/photos/view?photos=e9f27f3c-cdf3-4588-a36a-eba8924ba384 | Steel | Channel Bracket-Bolt | Coating Failure
a3ef5777-ab60-487a-b5b3-3337a78f79ad | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:25:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 371 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 88659 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.594 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 372, 3 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 10% coverage with breakdown of galvanised coating Corrosion behind cable tray localised around connection to cable tray |  | Steel channel support bracket has Level 2 Corrosion up to 10% coverage with breakdown of galvanised coating Corrosion behind cable tray localised around connection to cable tray | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Defect not present at ring 372, only at 371. Corrosion has advanced on the cable tray, not a structural defect. Low priority. | yes | no |  | yes |  | 6f4e4d0d-bf47-485e-bf12-9413c9ca60b7 |  | https://web.fulcrumapp.com/photos/view?photos=6f4e4d0d-bf47-485e-bf12-9413c9ca60b7 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
ac8339a3-8213-4041-9782-4c5478063946 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:18:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 372 | 5 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27500 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 372, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | Corrosion condition of structural steel and bolt has advanced. Medium priority. | yes | no |  | no |  | 3bcda215-0de6-4479-8264-44c4e77d55ba,09d06eda-614c-43a8-b6b9-a1ef292a67bb | 5 o'clock structural steel and bolt ,Structural steel surface corrosion up to 1mm and bolt condition | https://web.fulcrumapp.com/photos/view?photos=3bcda215-0de6-4479-8264-44c4e77d55ba%2C09d06eda-614c-43a8-b6b9-a1ef292a67bb | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support not Channel Bracket
4baf4570-5cb1-452d-8157-f955e252d4da | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:11:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 372 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27501 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 372,7 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion of bolts and nuts has advanced. Surface corrosion to the base plate is noted up to 1mm. Medium priority. | yes | no |  | no |  | 1a95fed4-aa57-4c30-a1a2-cfe69e0c776a,612706fc-dbeb-4b68-b9d1-47d479c3cc93,d387316b-204e-4559-88d3-010b237e428d,6888ffe0-9623-4451-a20f-78f1c4960c3d | 7 o'clock Base plate and hold down bolts ,Lower bolt condition ,Middle bolt condition and Base plate corrosion level ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=1a95fed4-aa57-4c30-a1a2-cfe69e0c776a%2C612706fc-dbeb-4b68-b9d1-47d479c3cc93%2Cd387316b-204e-4559-88d3-010b237e428d%2C6888ffe0-9623-4451-a20f-78f1c4960c3d | Steel | Conveyor Support | Corrosion-Surface |  | Conveyor Support not Channel Bracket
a3d6d7f4-a71d-4cf2-bc65-118512d6e18e | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:05:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 373 | 8 | Grout Injection Hole | Grout Injection Hole |  | 88660 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5951 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 373, 8 O'Clock, Grout Injection Hole |  |  |  | Grout Delamination / debonding at the grout patch repair inside grout injection hole. |  | Grout Delamination / debonding at the grout patch repair inside grout injection hole. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the defect is as per previous inspection. The leak is not active at the time of inspection. The condition of the plug bolt is not assessable. Low priority | no | yes |  | no |  | f4de2fc2-a3f3-4ff2-81b0-b7e732fb7941,edbbe22c-d8e4-4022-8e93-425711a2fd23 | , | https://web.fulcrumapp.com/photos/view?photos=f4de2fc2-a3f3-4ff2-81b0-b7e732fb7941%2Cedbbe22c-d8e4-4022-8e93-425711a2fd23 | Concrete | Grout Hole | Drummy,Leaks
a442fed5-7f1a-4f4f-93f5-ce595cf2d0e0 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 11:01:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 374 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26957 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 374, 11 & 12 O'Clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection behind the channel. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Scheduled Maintenance Competent Supervisor | Bogdan Stanca |  | This is not a defect. It is a consequence of the 11 o'clock injection hole leak and is not affecting the radial joint. | no | no |  | no |  | ba3ba4db-30b2-41c4-933b-c7cc2541d956 |  | https://web.fulcrumapp.com/photos/view?photos=ba3ba4db-30b2-41c4-933b-c7cc2541d956 | Concrete | Grout Hole,Radial Joint | Leaks |  | Not a reinforcement
9094eb65-c3b9-4580-b6ad-f4b5bed82364 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:31:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 374 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36656 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 374, 12 to 1 O'clock, Channel Anchor Bolts | Rupture | Rupture |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Not Specified | Priority: P3 |  |  |  | Replace damaged bolts one at a time as per original design specification. Remove corrosion by abrasive blasting or mechanical means and reinstate protective coatings in accordance with BHP specifications. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair Guideline 0136559. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor | Bogdan Stanca |  | The leak is active from injection holes at 1 o'clock at the time of inspection. The injection hole at 1 o'clock is located behind the steel channel and cannot be inspected. The steel channel corrosion has advanced. High priority. | yes | no |  | no |  | 25c8e04a-9620-457a-bb9f-a5df757cff22,d9ebd8bf-8865-475d-9e4b-484658918591,268ae35a-c607-434a-843d-28d48e3201da | ,, | https://web.fulcrumapp.com/photos/view?photos=25c8e04a-9620-457a-bb9f-a5df757cff22%2Cd9ebd8bf-8865-475d-9e4b-484658918591%2C268ae35a-c607-434a-843d-28d48e3201da | Steel | Channel Bracket,Channel Bracket-Bolt,Grout Hole | Leaks
099d5a50-96b8-4d9d-aef0-29c6493122c6 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:59:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 374 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76411 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44732.2488 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 374, 3 O'Clock, Channel Anchor Bolts |  |  |  | Steel channel support bracket has Level 1 corrosion and Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion and Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Corrosion advanced on both the anchor bolt and the steel plate. Section loss visible on the base plate. Moderate priority | yes | no |  |  |  | 1ed8012d-a72b-454e-b8eb-d44e4917e06a |  | https://web.fulcrumapp.com/photos/view?photos=1ed8012d-a72b-454e-b8eb-d44e4917e06a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
8aa54075-863c-4cf1-85d2-9f9e18a2e429 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:23:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 374 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27172 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 374, 9 O'Clock and 10 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak Active at time of inspection. |  | Grout injection hole has leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | Working at Heights | Scheduled Maintenance Competent Supervisor | Bogdan Stanca |  | The grout injection holes are located at the 9 and 11 o'clock position. Both appear to have an active leak. The steel plug at 9 o'clock injection hole has surface corrosion. The 11 o'clock injection hole is located behind the steel channel, the steel plug cannot be inspected. Due to the active leak the steel channel is corroded and the active corrosion behind the channel web puts pressure on the anchor bolts and can fail sooner than under normal conditions. High priority | yes | no |  | no |  | 9594ae0f-57c8-4ab0-acfd-e5ce2919a54e,ea7acec1-e69c-4b50-b8aa-03e507390517,59fdeee9-f8f7-4b35-adab-00ed0c0a81f8,db6c191c-0d44-4799-842b-c37f80a0a97a,800bd15e-9825-4f6c-9ec7-b55f7dee6e92 | 9 o'clock injection holes ,9 o'clock steel plug ,11 o'clock injection hole with salt deposits.,11 o'clock injection hole with salt deposits,Effect of leak at 11 o'clock and missing bolt nut | https://web.fulcrumapp.com/photos/view?photos=9594ae0f-57c8-4ab0-acfd-e5ce2919a54e%2Cea7acec1-e69c-4b50-b8aa-03e507390517%2C59fdeee9-f8f7-4b35-adab-00ed0c0a81f8%2Cdb6c191c-0d44-4799-842b-c37f80a0a97a%2C800bd15e-9825-4f6c-9ec7-b55f7dee6e92 | Concrete,Steel | Grout Hole | Corrosion-Surface,Leaks |  | Not a reinforcement
1c1976f4-19a9-48bb-bf36-d4461d2c2f8e | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:57:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 374 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 26956 |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 374,11 O'Clock and 1 O'Clock, Steel Channel Bracket and Anchor Bolt | Rupture | Rupture |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Financial | Priority: P3 |  |  |  | Replace damaged bolts one at a time as per original design specification. Remove corrosion by abrasive blasting or mechanical means and reinstate protective coatings in accordance with BHP specifications. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair Guideline 0136559. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor | Bogdan Stanca |  | The corrosion of the steel channel has advanced. Remediation works are required. Medium priority. | yes | no |  | no |  | 71391711-5af5-4f51-84ee-03036cb338a1,456aa73e-1ccc-47f9-a67e-edf0a46b1bef,11aa68ed-e5f6-4157-bf17-826af0bb3d37,7a5ee5c0-5f0e-4f02-924f-554fcb362220,3ca23d38-b05e-4e15-bb7d-3e85b60a46ba,e7d86181-ed46-4a55-aaca-26fad8ff8b72 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=71391711-5af5-4f51-84ee-03036cb338a1%2C456aa73e-1ccc-47f9-a67e-edf0a46b1bef%2C11aa68ed-e5f6-4157-bf17-826af0bb3d37%2C7a5ee5c0-5f0e-4f02-924f-554fcb362220%2C3ca23d38-b05e-4e15-bb7d-3e85b60a46ba%2Ce7d86181-ed46-4a55-aaca-26fad8ff8b72 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
06e8a2ea-1dd5-49e2-943b-184b41787e16 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 22:08:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 374 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27173 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Structure,Ring 374,9 O'Clock and 10 O'Clock,Brace,New Defect 2017 |  |  |  | Corrosion of diagonal bracing, Class 2 - Medium low corrosion |  | Corrosion of diagonal bracing, Class 2 - Medium low corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the steel is as per previous inspection. A local buckle of one flange is noted. Possible defect at time of installation as no significant loss of section is noted at that location. | no | yes |  | no |  | 866d4905-b586-4fa4-bdb9-5583c7bdb5ea,8ee01681-c42d-47b2-8648-9a6ec9cb6bdc | , | https://web.fulcrumapp.com/photos/view?photos=866d4905-b586-4fa4-bdb9-5583c7bdb5ea%2C8ee01681-c42d-47b2-8648-9a6ec9cb6bdc | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
8dab1d24-5326-4271-bc9f-99bb5b25b2a6 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 10:48:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 375 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36657 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Carbonation Induced |  | Carbonation Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 375, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. Plug bolt is in good condition. | no | yes |  | no |  | 7f05fdbd-7307-4a3e-b367-4e5c1993125a,c5926b36-a6b0-4837-b69c-401c6bca2c44,e3bcf824-9f45-4f85-9b00-675f50cd8145 | ,, | https://web.fulcrumapp.com/photos/view?photos=7f05fdbd-7307-4a3e-b367-4e5c1993125a%2Cc5926b36-a6b0-4837-b69c-401c6bca2c44%2Ce3bcf824-9f45-4f85-9b00-675f50cd8145 | Concrete | Grout Hole | Leaks |  | Not a reinforcement
dd5f1607-3fd2-4a13-a357-f49a695a2233 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:54:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 376 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76413 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44732.2524 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 376, 1 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | Dr |  | Channel anchor bolts remain corroded at same level. No section loss. Low priority | no | no |  | no |  | 1702eb5c-1be3-437b-bbd2-c7b1f52b4ad2 |  | https://web.fulcrumapp.com/photos/view?photos=1702eb5c-1be3-437b-bbd2-c7b1f52b4ad2 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
67106c66-b996-42c1-adac-3f10bdaaf71d | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 21:51:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 376 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36659 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 376, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. Plug bolt is in good condition. | no | yes |  | no |  | 61c087bf-7dc9-4716-9ca3-d77b5ee0c01e,e8323eea-71c1-435f-a95a-abd3cadeca3c | , | https://web.fulcrumapp.com/photos/view?photos=61c087bf-7dc9-4716-9ca3-d77b5ee0c01e%2Ce8323eea-71c1-435f-a95a-abd3cadeca3c | Concrete | Grout Hole | Leaks |  | Not a reinforcement
dda54129-cfff-4041-9059-a23e19c7e939 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 14:24:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 376 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88661 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5959 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 376, 4 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Delamination and the drumminess is still present and in the same size. Crack appearing in the concrete. High priority | yes | no |  | yes | Change location to 5 | cb8aa0a1-d8ef-4b5a-a215-e7a907cbd78f,f5548ed0-c8ae-4b2f-8e5b-b9b1e1c745cf,916993a3-3356-4837-a301-beb928ffb3e5 | ,, | https://web.fulcrumapp.com/photos/view?photos=cb8aa0a1-d8ef-4b5a-a215-e7a907cbd78f%2Cf5548ed0-c8ae-4b2f-8e5b-b9b1e1c745cf%2C916993a3-3356-4837-a301-beb928ffb3e5 | Concrete | Circular Joint | Crack,Drummy
55d11a2c-f0e3-4df7-9810-6043e0f212dd | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 21:48:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 376 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36658 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 376, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Active at time of inspection. |  | Grout injection hole has leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Bogdan Stanca |  | The leak is active at the time of inspection. Steel plug not visible. | no | yes |  | yes | Check with Tunnel engineer on typ treatment of the grout plugs. | db1d0b57-7b78-403d-a25c-8061a844c18b,68e21238-a2c8-4658-9caa-8ae3e6149228,7eaf97d7-a4b6-4502-bedf-7c98c6840899 | ,, | https://web.fulcrumapp.com/photos/view?photos=db1d0b57-7b78-403d-a25c-8061a844c18b%2C68e21238-a2c8-4658-9caa-8ae3e6149228%2C7eaf97d7-a4b6-4502-bedf-7c98c6840899 | Steel | Grout Hole | Leaks |  | Not a reinforcement
d7e20f9a-04e2-482b-a50a-9114c36ee30e | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:59:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 376 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27174 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 376, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1) and lower bolt (Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1) and lower bolt (Level 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect has advanced. Nut bolts fully corroded. Base plate presents surface corrosion with loss of section up to 1mm. Medium priority. | yes | no |  | no |  | a5eead34-d911-445c-b0fa-157990b07ba0,3e7bf9b2-78d8-4b56-9fe2-2aee53b7f580,e9476d3a-b832-4176-b8bf-0e0ddde7f635,efcb19ae-305c-42fa-869e-3f60fd9ebdeb,75159ffb-5873-41c2-b88a-0f6cce2ed2b7,1de962b6-c06e-4871-8368-96181884793e | 7 o'clock base plate general view ,Lower bolt and base plate condition ,middle bolt condition ,Surface corrosion base plate ,Top bolt condition ,Surface corrosion to top of steel plate | https://web.fulcrumapp.com/photos/view?photos=a5eead34-d911-445c-b0fa-157990b07ba0%2C3e7bf9b2-78d8-4b56-9fe2-2aee53b7f580%2Ce9476d3a-b832-4176-b8bf-0e0ddde7f635%2Cefcb19ae-305c-42fa-869e-3f60fd9ebdeb%2C75159ffb-5873-41c2-b88a-0f6cce2ed2b7%2C1de962b6-c06e-4871-8368-96181884793e | Steel | Channel Bracket-Bolt | Corrosion-Surface
118d80d9-55f0-47d5-93d9-364ac21ccc4a | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:54:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 376 | 5 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27502 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 376,5 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | Bolt corrosion has advanced. Medium priority. | yes | no |  | no |  | 4064a709-f95a-46e6-81b5-581fad64f46f |  | https://web.fulcrumapp.com/photos/view?photos=4064a709-f95a-46e6-81b5-581fad64f46f | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | WAlkway Support
02064eb3-c2d5-4628-ab5f-f60ff282c646 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 01:43:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 377 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27176 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 377, 8 O'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The defect is as per previous inspection. The leak is not active. Steel plug in good condition. Low priority | no | yes |  | no |  | c04bbd0f-cca0-4681-860a-c437c1e793b3,8a60f7d4-e814-4edb-91b6-f1041e254cbb | , | https://web.fulcrumapp.com/photos/view?photos=c04bbd0f-cca0-4681-860a-c437c1e793b3%2C8a60f7d4-e814-4edb-91b6-f1041e254cbb | Concrete,Steel | Grout Hole | Leaks |  | Not a reinforcement
564eabc2-9ba1-4f79-ba8a-6b4425bf4340 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:44:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 378 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36660 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.4671 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 378, 3 to 12 O'clock, Channel Anchor Bolts |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | Bolts are still corroded at the same level. Minor corrosion observed on the steel brscket. Low priority defect. | no | no |  |  |  | fc1c4b0e-5203-48b5-8aec-cfc803728ac0,0edeef65-5ce8-4ea2-85a0-de99a8d88d38,9ed32f83-ec0d-4c56-b46a-2964bf590f43 | ,, | https://web.fulcrumapp.com/photos/view?photos=fc1c4b0e-5203-48b5-8aec-cfc803728ac0%2C0edeef65-5ce8-4ea2-85a0-de99a8d88d38%2C9ed32f83-ec0d-4c56-b46a-2964bf590f43 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
cdf67636-4bc4-4382-a908-7345cf6590b8 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:39:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 379 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26958 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 379, 2 O'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive at specified location. No change to condition of the defect. Minor collection of salt deposit present at the grout injection hole. Moderate priority defect. | no |  |  |  |  | 4c088b56-7812-4e73-ac69-56ee5c298d4d,531bdaa0-9f42-47d4-bfc9-d7a7f6c00a8b | , | https://web.fulcrumapp.com/photos/view?photos=4c088b56-7812-4e73-ac69-56ee5c298d4d%2C531bdaa0-9f42-47d4-bfc9-d7a7f6c00a8b | Concrete | Grout Hole | Leaks |  | Not a reinforcement
02f7b7d0-20b3-4cc8-9e85-439d7f1582f4 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:38:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 379 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27177 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 379, 3 O'Clock, Cable Tray |  |  |  | Cable tray has level 1 corrosion. |  | Cable tray has level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Corrosion on cable tray has increased to Level. Not a structural defect, hence low priority. | yes | no |  | no |  | 7ea0df88-a125-4c1e-b999-6b16b90da6c7,d23d8e1e-b2aa-40a8-bbd0-ebbc6e60aa4f | , | https://web.fulcrumapp.com/photos/view?photos=7ea0df88-a125-4c1e-b999-6b16b90da6c7%2Cd23d8e1e-b2aa-40a8-bbd0-ebbc6e60aa4f | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
f9cb6e6a-7ef9-4729-9361-c0bc6b30058c | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 05:36:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 379 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27178 |  | 6655 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 4/04/2022 |  | 4/04/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Structure,Ring 379,3 O'Clock,Concrete Element,New Defect 2017 | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Very Rare Likelihood of failure, resulting in a Priority 4. | Not Specified | Priority: P3 |  |  |  | Monitor leak condition at the next inspection if it is still dry then monitor. If active the update to P2 and fixed | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive at specified location. No change to condition of the defect. Minor collection of salt deposit present at the grout injection hole. Moderate priority defect. | no | yes |  | no |  | 2d55488d-d4fe-4c77-a431-09ea5ffc087a,4867213e-6fe1-431c-8837-4337f73a934a | , | https://web.fulcrumapp.com/photos/view?photos=2d55488d-d4fe-4c77-a431-09ea5ffc087a%2C4867213e-6fe1-431c-8837-4337f73a934a | Concrete | Grout Hole | Leaks
7b65eae9-7fd0-4309-b75e-d3725e7f46b5 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:59:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 380-381 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 88664 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 380 to 381, 7 O'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 400mm x 400mm. |  | Concrete shell segment has drummy concrete over an area of 400mm x 400mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | Excavation | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The condition of the defect has not changed. Defect is considered superficial with no structural implication. Low priority. | no | no |  |  |  | 8097f220-942c-4aa2-b5e3-aa8abe2bb8b8 |  | https://web.fulcrumapp.com/photos/view?photos=8097f220-942c-4aa2-b5e3-aa8abe2bb8b8 | Concrete | Circular Connection | Drummy |  | Circular Connection
8cd2362c-a437-44cb-b741-5ce8f009e4f8 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 | -20.318 | 118.5774 | POINT (118.5774061 -20.3180088) | 2025-05-27 20:13:18 AEST | 2025-07-28 14:26:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 380 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88662 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5968 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 380, 4 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | Delamination and drummy concrete still present at the same size. Spalling of concrete is also visible. Medium priority | yes | no |  | yes | Change defect to 5 O Clock | 64f11d58-116f-4c2e-a2ba-8a296850b39b,c8e62b8d-3fa3-41c0-a5d5-514f94c87715,50203e4e-b3c4-45e9-94e0-b841e0cdfc1b | ,, | https://web.fulcrumapp.com/photos/view?photos=64f11d58-116f-4c2e-a2ba-8a296850b39b%2Cc8e62b8d-3fa3-41c0-a5d5-514f94c87715%2C50203e4e-b3c4-45e9-94e0-b841e0cdfc1b | Concrete | Circular Joint | Drummy,Surface Damage
7234abf2-df4e-4bcf-a83d-6ee6ccc9b9bd | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:56:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 380 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27179 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 380, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion has advanced. Corrosion protection is required. Low priority. | yes | yes |  | no |  | 99433591-c998-4d1d-bebf-86be9b0a42d6,4a329489-0651-4158-b37d-7c3f3a37d75e,e3fb5562-4573-4741-aec8-434a41534331 | ,, | https://web.fulcrumapp.com/photos/view?photos=99433591-c998-4d1d-bebf-86be9b0a42d6%2C4a329489-0651-4158-b37d-7c3f3a37d75e%2Ce3fb5562-4573-4741-aec8-434a41534331 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support
af982fbd-865f-4085-b661-cc18c5398ddd | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 14:26:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 380 | 5 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27503 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 380,5 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion has advanced. Surface corrosion to the base plate. Corrosion protection is required. Medium priority. | yes | no |  | no |  | 8ff917c1-70a6-4ae9-9ebc-59bd7831c45b,96b2b8ea-eb72-48d5-9700-d01d4cd89870,e1599bc3-a53c-4291-89dc-d3f74bdef152 | ,, | https://web.fulcrumapp.com/photos/view?photos=8ff917c1-70a6-4ae9-9ebc-59bd7831c45b%2C96b2b8ea-eb72-48d5-9700-d01d4cd89870%2Ce1599bc3-a53c-4291-89dc-d3f74bdef152 | Steel | Walkway Support | Corrosion-Surface |  | Walkway Support
08a608ae-46a6-47ce-973a-8212e64b7834 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:50:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 381 | 9 | Grout Injection Hole | Grout Injection Hole |  | 88663 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5975 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 381, 9 O'Clock, Grout Injection Hole |  |  |  | Grout Delamination / debonding at the grout patch repair inside grout injection hole. |  | Grout Delamination / debonding at the grout patch repair inside grout injection hole. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect is in the same condition as per previous inspection. The grout hole fill in do not appear to be properly placed resulting in internal delamination. No leak visible at the time of inspection. Plug bolt not visible for inspection. Low priority. | no | yes |  |  |  | ed9f09f9-1fcf-441f-8c1f-308ed513255a,574e918a-bdff-4b51-831c-69f1917abc3a | , | https://web.fulcrumapp.com/photos/view?photos=ed9f09f9-1fcf-441f-8c1f-308ed513255a%2C574e918a-bdff-4b51-831c-69f1917abc3a | Concrete | Grout Hole | Drummy,Leaks
30634ed9-0147-46dc-8714-024dfead7fb9 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:48:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 381 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36661 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 43901.4679 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring: 381, 12 O'clock: Grout Injection Hole. |  |  |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The leak is not active at the time of inspection. The grout hole has been grouted. The condition of the plug bolt is not accessible. No work required, only monitoring to assess the condition of the grout. Low priority. | no | yes |  | no |  | b25cca2f-391b-475e-995b-a23f764fa325,6b9f0b4b-f7d8-4369-a727-e2b5efc80cc7 | , | https://web.fulcrumapp.com/photos/view?photos=b25cca2f-391b-475e-995b-a23f764fa325%2C6b9f0b4b-f7d8-4369-a727-e2b5efc80cc7 | Concrete | Grout Hole | Leaks
2d920562-ec71-42b0-a5cd-5aa40d1452dc | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:43:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 382 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36663 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.4686 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 382, 12 to 1 O'clock, Channel Anchor Bolts |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect has not changed. Low priority | no | yes |  | no |  | 7f9137aa-415c-48f8-82c4-e0ba641bc03a,aba5a43f-6b0d-4adc-ad05-7c97effe8289,af29b490-ee80-42c2-8ae8-7fee67f837e7,fc0ef008-53fe-4d4b-ab67-e82e08ad8c88 | ,,, | https://web.fulcrumapp.com/photos/view?photos=7f9137aa-415c-48f8-82c4-e0ba641bc03a%2Caba5a43f-6b0d-4adc-ad05-7c97effe8289%2Caf29b490-ee80-42c2-8ae8-7fee67f837e7%2Cfc0ef008-53fe-4d4b-ab67-e82e08ad8c88 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
d8e5c77a-d286-4ddc-bb86-1a4e5663191c | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:50:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 383 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27181 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 383, 9 O'Clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Grout Injection Hole". Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | Working at Heights | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. No salt deposits noted. The seal bolt is in good condition. Low priority. | no | yes |  | no |  | 9438ee10-5c2a-437a-9ed2-d42347cabef6,8dec179f-93d1-4d46-ab2d-cc322d616b74 | , | https://web.fulcrumapp.com/photos/view?photos=9438ee10-5c2a-437a-9ed2-d42347cabef6%2C8dec179f-93d1-4d46-ab2d-cc322d616b74 | Concrete | Grout Hole | Leaks |  | Not a reinforcement
a49b2649-2107-44e7-90cf-c9cad5a90212 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:54:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 384 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36665 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 384, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Same as defect noted at 1 O' Clock. Incorrectly noted twice at 12 O' Clock. | yes | yes |  |  |  | 844f3bb8-d61d-4982-94b4-cc0ee95e8f70,f9463ec2-6e90-4de1-b029-18401b935896 | , | https://web.fulcrumapp.com/photos/view?photos=844f3bb8-d61d-4982-94b4-cc0ee95e8f70%2Cf9463ec2-6e90-4de1-b029-18401b935896 | Concrete | Grout Hole,Reinforcement,Misc (Pipes/Cable Tray/etc) | Leaks |  | MIsc as well
87e9373e-fd10-44dc-932a-31eb41ddc3ff | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:49:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 384 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 88665 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44977.5994 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 384, 3 O'Clock, Channel Anchor Bolts |  |  |  | Loose nut at one channel anchor bolt |  | Loose nut at one channel anchor bolt | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | Dr |  | Nut remains loose and corroded at level 2. Not a priority repair | yes | no |  | no |  | 9ea4435c-02ae-4aa8-9386-4122e18ecb9a |  | https://web.fulcrumapp.com/photos/view?photos=9ea4435c-02ae-4aa8-9386-4122e18ecb9a | Steel | Channel Bracket-Bolt | Loose
9f5d65bf-5315-4cfb-a81f-4ba336fad4da | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:30:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 384 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27182 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 384, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 4) and lower bolt (Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 4) and lower bolt (Level 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion has advanced. Surface corrosion to the base plate. Corrosion protection is required. Medium priority. | yes | no |  | no |  | 7327eb69-5124-4d24-ac37-4fda8db334ed,a0c5918b-e487-4d05-b71a-f3aabf49971a,417639d7-53cb-464f-a536-ea3e53c6d3ef,ba960bf6-61d3-4265-8cec-1b067210e28e | ,,, | https://web.fulcrumapp.com/photos/view?photos=7327eb69-5124-4d24-ac37-4fda8db334ed%2Ca0c5918b-e487-4d05-b71a-f3aabf49971a%2C417639d7-53cb-464f-a536-ea3e53c6d3ef%2Cba960bf6-61d3-4265-8cec-1b067210e28e | Steel | Walkway Support | Corrosion-Surface |  | WAlkway support not channel bracket
49495bdf-c7ce-4168-a0fc-30daa2795083 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 22:14:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 384 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26960 |  | 6655 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Repair Verified | 4/04/2022 |  | 4/04/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Structure,Ring 384,1 O'Clock,Concrete Element, | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | Working at Heights | Engineering Repair Methodology Required Competent Supervisor | DR |  | Major leak still active at the time of inspection. Large deposits of salt collecting at grout injection hole and on the pipe below. Pipe and walkway below have gotten severely corroded. Leak seepage onto steel structure holding the conveyor belt has also begun corroding. Condition worsened. High priority repair. Steel mesh on walkway has been replaced during shut 2 at time of inspections after flagging as urgent with BHP. | yes | yes |  |  |  | 717515da-bd94-43aa-8ca9-1baf1b4b3ea8,a7fb349a-5111-466d-9aad-0c3ebae9bf9e,7cc7f688-fc63-4e6e-8e3a-6db4c327dd3a,b90b56e0-0129-4599-ba0e-e4f39372e753,0de1b1e4-1ca8-4838-a51b-ee2165962932,8404c720-fa27-4d0e-888a-c386f4add96b,7f50d4b7-2015-4323-af8f-6095dfcd753f,4241253d-2504-4a1e-a70e-77ebcadd819b,34780b04-3327-47fc-8b40-49fc17dd43be | ,,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=717515da-bd94-43aa-8ca9-1baf1b4b3ea8%2Ca7fb349a-5111-466d-9aad-0c3ebae9bf9e%2C7cc7f688-fc63-4e6e-8e3a-6db4c327dd3a%2Cb90b56e0-0129-4599-ba0e-e4f39372e753%2C0de1b1e4-1ca8-4838-a51b-ee2165962932%2C8404c720-fa27-4d0e-888a-c386f4add96b%2C7f50d4b7-2015-4323-af8f-6095dfcd753f%2C4241253d-2504-4a1e-a70e-77ebcadd819b%2C34780b04-3327-47fc-8b40-49fc17dd43be | Concrete,Steel | Grout Hole,Misc (Pipes/Cable Tray/etc),Reinforcement | Leaks
c2b6dce6-b715-46ff-984b-35a2fe81c8f9 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:31:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 384 | 5 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27505 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 384,5 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion has advanced. Surface corrosion to the base plate. Corrosion protection is required. Medium priority. | yes | no |  | no |  | 5361962a-ad28-41c7-a435-fef992985bd2,8cd15166-3d66-4046-acd9-e263ef1dac53 | , | https://web.fulcrumapp.com/photos/view?photos=5361962a-ad28-41c7-a435-fef992985bd2%2C8cd15166-3d66-4046-acd9-e263ef1dac53 | Steel | Walkway Support | Corrosion-Surface |  | WAlkwya support
9ebc4415-ae28-4d86-9113-4470ab35e677 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:39:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 386 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76414 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44732.2567 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 386, 3 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. One anchor bolt is missing at 3 O'Clock, |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. One anchor bolt is missing at 3 O'Clock, | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change to corrosion levels. Low priority repair. | no | no |  |  |  | 4ab8b151-fff6-4c2c-9284-b323e9daf7de,ecb85c1c-d5b3-4a92-bcbd-80102cb097e5 | , | https://web.fulcrumapp.com/photos/view?photos=4ab8b151-fff6-4c2c-9284-b323e9daf7de%2Cecb85c1c-d5b3-4a92-bcbd-80102cb097e5 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
ef41b310-626a-445c-9dee-665a6ce66fa1 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:28:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 386 | 8 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27184 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 386,8 O'Clock,Bolt, Nut, Washer,New Defect 2017 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | No bolts noted on Ring 386 at 8 o'clock position. Possible mistaken for Ring 384 | [5 empty] | d838fd3e-d38d-4ab4-af2e-8c3ec1fe082b,e8de7375-cade-41c7-8ff1-1e61b88f9069 | , | https://web.fulcrumapp.com/photos/view?photos=d838fd3e-d38d-4ab4-af2e-8c3ec1fe082b%2Ce8de7375-cade-41c7-8ff1-1e61b88f9069 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
9692bbf5-153c-48ba-8725-3599e99946bf | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 14:27:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 387 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88667 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.601 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 387, 4 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Delaminated and drummy concrete is still present on the same size with concrete spalling. Medium priority. | yes | no |  | yes | Location at 5 O Clock not at 4. | 059a1ee2-0d1f-4ff7-b378-80d6bba6c553,743cb8bb-b97c-4350-a402-459e6ff9141f,e740c33c-dc31-4f2b-9816-acaa0171c74d,a05c7714-5418-4928-9ea2-18e7a76ac334 | ,,, | https://web.fulcrumapp.com/photos/view?photos=059a1ee2-0d1f-4ff7-b378-80d6bba6c553%2C743cb8bb-b97c-4350-a402-459e6ff9141f%2Ce740c33c-dc31-4f2b-9816-acaa0171c74d%2Ca05c7714-5418-4928-9ea2-18e7a76ac334 | Concrete | Circular Joint | Drummy,Surface Damage
1ab725f5-04e8-4c73-9573-aba347e62407 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:33:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 388 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 101849 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 45554.5342 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 388, 3 O'Clock, Channel Anchor Bolts. |  |  |  | Loose nut at channel anchor bolts |  | Loose nut at channel anchor bolts | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | Nut still remains loose. Condition of defect lowered to 1. Low priority repair | yes | no |  | no |  | 92380419-91e2-4ed8-b15a-17c8bf030716 |  | https://web.fulcrumapp.com/photos/view?photos=92380419-91e2-4ed8-b15a-17c8bf030716 | Steel | Channel Bracket-Bolt | Loose
398458cf-8804-42c0-9768-d9b80c6e945e | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:10:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 388 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27506 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 388, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1 to 2) and lower bolt (Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1 to 2) and lower bolt (Level 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion has advanced. Corrosion protection is required. Medium priority. | yes | no |  | no |  | bb380eb4-3588-4936-a48f-992a465d0d83,3d7097ea-f55a-4c04-8fe7-58b0e010c23b | , | https://web.fulcrumapp.com/photos/view?photos=bb380eb4-3588-4936-a48f-992a465d0d83%2C3d7097ea-f55a-4c04-8fe7-58b0e010c23b | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support
73e28e10-3d1c-415a-8649-638c3c70f590 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:08:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 388 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27507 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 388,7 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion has advanced. Nuts fully corroded. Base plate surface corrosion. Medium priority. | yes | no |  | no |  | 366b8a98-a9ac-4f1c-b6b9-18e4a03af850,141a35f3-605f-4e53-b071-59d98bb6e5c0,f22c54d9-8bc8-406d-ad2f-07ddc485caba,c8f43ddd-5c57-4252-81e8-626ae0415a57,51515575-dac3-4911-b547-75ea6c4b57c0 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=366b8a98-a9ac-4f1c-b6b9-18e4a03af850%2C141a35f3-605f-4e53-b071-59d98bb6e5c0%2Cf22c54d9-8bc8-406d-ad2f-07ddc485caba%2Cc8f43ddd-5c57-4252-81e8-626ae0415a57%2C51515575-dac3-4911-b547-75ea6c4b57c0 | Steel | Channel Bracket-Bolt | Corrosion-Surface
e23f14a2-7ab3-4198-9182-17ac3da8653e | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:35:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 389 | 12 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 88668 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.6017 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 389, 12 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect is in the same condition as per previous inspection. The defect is superficial and not considered structural. Low priority | no | yes |  | no |  | b7d9b68f-aedc-4e6e-ad4e-b0d22f42cd6f |  | https://web.fulcrumapp.com/photos/view?photos=b7d9b68f-aedc-4e6e-ad4e-b0d22f42cd6f | Concrete | Radial Joint | Drummy
33bbc345-8101-4dcb-9696-efa55ac85aab | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 389 | 9 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88666 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.6001 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 389, 9 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [15 empty] | Concrete | Circular Joint | Drummy
39f68bd5-c46d-45c4-ae0b-24c5d08e1133 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:27:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 390 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26961 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 390, 3 O'Clock, Channel Anchor Bolts |  |  |  | Channel anchor bolts have level 1 corrosion. |  | Channel anchor bolts have level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Condition remains the same. Low priority repair. Not a structural defect | yes | no |  |  |  | b33bcd08-dffe-436f-a6a2-f27efee86bd0 |  | https://web.fulcrumapp.com/photos/view?photos=b33bcd08-dffe-436f-a6a2-f27efee86bd0 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
e313d649-b3d3-410b-8fb6-c523b596298c | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:05:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 390 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 76416 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 390, 4 O'Clock, Segmented Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mmx400mm |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mmx400mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. | Safety | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | No change in the condition. Delaminated concrete section is still the same size with concrete spalling. Defect location is at 5 O Clock and not at 4 O Clock. Medium priority repair. | yes | no |  | no |  | 0646d825-0ff9-4a73-8f1b-65e15d2c5617,784c4c31-cdf3-426d-802d-91969c7d7cbd,986536c9-cd6f-47e3-af5c-d34103d18f9e | ,, | https://web.fulcrumapp.com/photos/view?photos=0646d825-0ff9-4a73-8f1b-65e15d2c5617%2C784c4c31-cdf3-426d-802d-91969c7d7cbd%2C986536c9-cd6f-47e3-af5c-d34103d18f9e | Concrete | Radial Joint | Drummy,Surface Damage
c8fcc039-1311-463d-8d77-d72c40850364 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 18 |  |  |  | 2025-07-26 04:24:16 AEST | 2025-07-29 13:37:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | 384 | 6 o'clock |  |  | Steel column and Walkway support member | [56 empty] | Bogdan Stanca |  | Advanced corrosion to the walkway steel member due to the constant water dripping. High priority member protection required together with the sealing of water infiltration. |  |  |  | no |  | 8756a1fc-2715-4bb9-abc8-24acc9491c22,d2425b74-eba3-4887-9616-610a78101b37,e865c697-ff78-4967-859c-66bb78f41dae,6c5ca9ff-8f90-42f9-92a9-4051287592b3 | ,,, | https://web.fulcrumapp.com/photos/view?photos=8756a1fc-2715-4bb9-abc8-24acc9491c22%2Cd2425b74-eba3-4887-9616-610a78101b37%2Ce865c697-ff78-4967-859c-66bb78f41dae%2C6c5ca9ff-8f90-42f9-92a9-4051287592b3 | Steel | Walkway Support | Corrosion-Heavy
a9cbec8f-3318-4ff3-88f9-0e90419a882b | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 19 |  |  |  | 2025-07-26 05:49:30 AEST | 2025-07-26 05:51:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 384 | 2 O' Clock |  | Steel Channel Bracket | [15 empty] | Corrosion - Structure Member/Platework |  | 2 | [39 empty] | Dr |  | Leak at 11 O' Clock seeping down to the steel bracket and bolt causing them to corrode. Level 1 corrosion. Not a priority repair |  | yes |  |  |  | cb4df31f-4fed-401b-981c-8502ef6888c2 |  | https://web.fulcrumapp.com/photos/view?photos=cb4df31f-4fed-401b-981c-8502ef6888c2 | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks
2399f34f-f12e-4518-959e-7eb044cec708 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 13 |  |  |  | 2025-07-26 21:38:00 AEST | 2025-07-26 21:42:42 AEST | 30011704-user5@smec.com | james.stone@smec.com | 378 | 11 o'clock |  | Grout Injection Hole | [51 empty] | Yes |  | No |  |  |  | Bogdan Stanca |  | The grout injection hole has been sealed using mortar. There is no active leak at the time of inspection. Fill grout is drummy. The condition of the plug bolt is not known. Possible failure of grout in the near future. Visual monitoring is required to catch when leaking appears. |  |  |  | yes | New defect to be included with BHP attributes. | 69a020de-3143-4054-938d-35c80a1106fd |  | https://web.fulcrumapp.com/photos/view?photos=69a020de-3143-4054-938d-35c80a1106fd | Concrete | Grout Hole,Mortar | Drummy,Leaks
d9116405-5b89-48f7-b14f-15658e6bc6ad | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 13 |  |  |  | 2025-07-26 21:48:32 AEST | 2025-07-26 21:49:08 AEST | 30011704-user5@smec.com | james.stone@smec.com | 377 | 11 o'clock |  | Grout Injection Hole | [51 empty] | Yes |  | No |  |  |  | Bogdan Stanca |  | The grout injection hole has been sealed using mortar. There is no active leak at the time of inspection. Fill grout is drummy. The condition of the plug bolt is not known. Possible failure of grout in the near future. Visual monitoring is required to catch when leaking appears. |  |  |  | yes | New defect to be included with BHP attributes. | a19102a0-d615-437c-831a-cb09d4c014c6 |  | https://web.fulcrumapp.com/photos/view?photos=a19102a0-d615-437c-831a-cb09d4c014c6 | Concrete | Grout Hole,Mortar | Drummy,Leaks
c68d5fe0-6d2f-41e5-85c5-fb0aa710e26b | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 12 |  |  |  | 2025-07-27 06:05:59 AEST | 2025-07-27 06:06:43 AEST | 30011704-user5@smec.com | james.stone@smec.com | 372 | 1 O Clock |  | Channel Anchor Bolts | [57 empty] | Dr |  | Level 1 corrosion on channel anchor bolts. Low priority defect |  | yes |  | no |  | 017784cb-c2e9-4a23-88eb-3357c71c69c8 |  | https://web.fulcrumapp.com/photos/view?photos=017784cb-c2e9-4a23-88eb-3357c71c69c8 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
88680ec1-8a79-4872-9629-e68905a6767a | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 12 |  |  |  | 2025-07-27 06:08:25 AEST | 2025-07-27 06:09:57 AEST | 30011704-user5@smec.com | james.stone@smec.com | 371 | 3 O Clock |  | Grout Injection Hole | [57 empty] | Dr |  | Previous leak location. Inactive at time of inspection. Grout plug in good condition, low priority defect. |  | yes |  |  |  | e3bb389d-a806-4d64-9559-44a4870190cf,49249ff2-c22d-4c3c-b80d-7ec30cf26226 | , | https://web.fulcrumapp.com/photos/view?photos=e3bb389d-a806-4d64-9559-44a4870190cf%2C49249ff2-c22d-4c3c-b80d-7ec30cf26226 | Concrete | Grout Hole | Leaks
4835c39d-927b-426a-b4e6-2f66d7700c67 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 12 |  |  |  | 2025-07-27 06:15:30 AEST | 2025-07-27 06:17:02 AEST | 30011704-user5@smec.com | james.stone@smec.com | 368 | 12 O Clock. |  | Grout Injection Hole | [57 empty] | Dr |  | Previous leak location. Leak inactive at time of inspection. Grout injection hole has been sealed. Low priority defect. |  | yes |  | no |  | 90000960-e844-4206-a240-942f9178c6d0 |  | https://web.fulcrumapp.com/photos/view?photos=90000960-e844-4206-a240-942f9178c6d0 | Concrete | Grout Hole | Leaks
7c2bdf62-1f16-4927-8a65-d5177326adab | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 10 |  |  |  | 2025-07-27 21:54:38 AEST | 2025-07-27 21:59:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 363 | 11 O' Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Inactive leak at the circumferential joint. | 3 | [39 empty] | DR |  | Circumferential joint has a previous inactive leak with a collection of salt deposit.same leak as the one at 3 O Clock. Moderate priority defect. |  | yes |  |  |  | ec1d7f22-47fd-44fa-8108-41562ff6a2c2,838c032a-fbc4-4634-b570-6cf40008ec62 | , | https://web.fulcrumapp.com/photos/view?photos=ec1d7f22-47fd-44fa-8108-41562ff6a2c2%2C838c032a-fbc4-4634-b570-6cf40008ec62 | Concrete | Circular Connection,Circular Joint | Leaks
14c5ac5e-ec69-475a-a422-91a26b6f5cf2 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 10 |  |  |  | 2025-07-27 22:03:32 AEST | 2025-07-29 12:15:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 362 | 3 O'Clock |  | Hydrophilic Joint Seal (Circle Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 3 | [39 empty] | Dr |  | Drummy and Delaminated concrete at the circumferential joint of about 100m X 200mm. Moderate priority defect. |  | yes |  | no |  | 7744c58e-a018-49a9-aa00-95952b1042a2 |  | https://web.fulcrumapp.com/photos/view?photos=7744c58e-a018-49a9-aa00-95952b1042a2 | Concrete | Circular Connection,Circular Joint | Drummy
6ae48250-56cf-4f72-86d6-291459991616 | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 9c02e216-6c30-4006-b03f-dcfa367bcdac | 5 |  |  |  | 2025-07-29 11:06:00 AEST | 2025-07-29 11:10:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 373 | 2 |  | Segment Bolted Joint (Circle Joint) | [32 empty] | O’clock position drilled hole Chloride sampling | [16 empty] | Repair grout filler | [7 empty] | AA BP |  | Concrete drill test hole 22/7/25. To repair with grout filler. |  | no |  | yes |  | c2f7ce9e-ce8f-4107-be44-183081c21f6e |  | https://web.fulcrumapp.com/photos/view?photos=c2f7ce9e-ce8f-4107-be44-183081c21f6e | Concrete | Circular Joint | Test Hole
7d1452d0-366d-4fb6-b4d0-75cc6eb925e6 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:16:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 392 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36670 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 392, 11 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | No change. Leak inactive at time of inspection. Low priority defect. | no | no |  | no |  | ede9cf72-4256-4954-9587-31a060ea4a87 |  | https://web.fulcrumapp.com/photos/view?photos=ede9cf72-4256-4954-9587-31a060ea4a87 | Concrete | Grout Hole | Leaks |  | Not a reinforcement
ee1c28a1-6aae-4008-b85b-235e10c2dcf7 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3216 | 118.5853 | POINT (118.5852704 -20.3216348) | 2025-05-27 20:13:18 AEST | 2025-07-26 05:22:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 392 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36671 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 392, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive. Lower priority defect. | no | no |  | no |  | 365066c1-cd97-4e85-882b-7462a6e935d9,c8579f98-6db6-44db-8210-4879692ce657 | , | https://web.fulcrumapp.com/photos/view?photos=365066c1-cd97-4e85-882b-7462a6e935d9%2Cc8579f98-6db6-44db-8210-4879692ce657 | Concrete | Grout Hole | Leaks |  | Not a reinforcement
c211f9a3-fc04-493a-9275-ee430d95d650 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:22:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 392 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76418 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44732.3326 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 392, 2 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change in condition. Bolt remains corroded at same level. Low priority repair. | no | no |  |  |  | c657b8e5-9da7-4646-9859-0838944589e9,d9b2b8cb-3226-41d9-b6eb-9fe71bdfab87 | , | https://web.fulcrumapp.com/photos/view?photos=c657b8e5-9da7-4646-9859-0838944589e9%2Cd9b2b8cb-3226-41d9-b6eb-9fe71bdfab87 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
34f5e8ff-ad61-4dbc-9130-2a59cc4cb423 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3216 | 118.5853 | POINT (118.5852695 -20.3216341) | 2025-05-27 20:13:18 AEST | 2025-07-26 01:21:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 392 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27188 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 392, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion of the bolt and nut has advanced. Corrosion protection is required. Medium priority. | yes | no |  | no |  | 2a4cc0c4-fe53-4bc7-9aeb-4ff5fd5916ef,1ef9bd38-3b48-48c0-b412-656c3bfa74b4 | , | https://web.fulcrumapp.com/photos/view?photos=2a4cc0c4-fe53-4bc7-9aeb-4ff5fd5916ef%2C1ef9bd38-3b48-48c0-b412-656c3bfa74b4 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway support not Channel Bracket Bolt
74bb48c6-4434-4a67-8542-2d23505b3b8c | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:20:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 392 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27508 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 392,7 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion of the bolt and nut has advanced. Corrosion protection is required. Medium priority. | yes | no |  | no |  | 0e954a19-a498-4f12-a71a-4cb81c1646cc,3774f680-4535-4346-9634-367dcfb95cf6,21714449-495d-4ae1-abfd-3c5f93b14ef0 | ,, | https://web.fulcrumapp.com/photos/view?photos=0e954a19-a498-4f12-a71a-4cb81c1646cc%2C3774f680-4535-4346-9634-367dcfb95cf6%2C21714449-495d-4ae1-abfd-3c5f93b14ef0 | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support
02bfb29a-a41f-48a5-b4dc-92d929b7a7de | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:18:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 393 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36672 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 393, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Dr |  | Leak inactive. No change in condition. Low priority defect. | no | no |  | no |  | e819ce35-283b-4483-a62e-93e86fac2312,aeb576fd-d72c-4796-88d6-07e303975d67,2e3fd1bc-f021-419f-89a6-45f179fb14ae | ,, | https://web.fulcrumapp.com/photos/view?photos=e819ce35-283b-4483-a62e-93e86fac2312%2Caeb576fd-d72c-4796-88d6-07e303975d67%2C2e3fd1bc-f021-419f-89a6-45f179fb14ae | Concrete | Grout Hole | Leaks |  | Not a reinforcement
8519002c-33f3-458d-a32a-46f387f0476e | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:10:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 394 | 9 | Grout Injection Hole | Grout Injection Hole |  | 76419 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 394, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is still inactive. No change in condition. Low priority | no | no |  | no |  | 5c9983e0-bd06-49d2-bb45-52dd36415b16 |  | https://web.fulcrumapp.com/photos/view?photos=5c9983e0-bd06-49d2-bb45-52dd36415b16 | Concrete | Grout Hole | Leaks
d0d2e72c-f37c-4c51-aee5-b9dff1281b22 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 05:12:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 396 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76421 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44732.3365 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 396, 2 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | No bolt identified at 4 O'Clock. Error in reporting and needs to be updated. Corroded and loose bolt only present at 2 O'Clock and has been noted as a separate defect. | yes | no |  | no |  |  |  |  | Steel | Channel Bracket,Channel Bracket-Bolt | Loose
7feb9b4b-53ba-4c71-b5dc-aceca0e6e54f | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:07:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 396 | 9 | Grout Injection Hole | Grout Injection Hole |  | 76420 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 396, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | DR |  | Leak remains inactive at time on inspection. Low priority defect. | no | no |  | no |  | 04d1fe5e-84f0-44e2-88f5-6267b392ed16 |  | https://web.fulcrumapp.com/photos/view?photos=04d1fe5e-84f0-44e2-88f5-6267b392ed16 | Concrete | Grout Hole | Leaks
9df4cc9b-137b-4d39-9571-89486588b87a | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:14:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 396 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27190 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 396, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 4 to 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 2) and lower bolt (Level 4 to 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion of nut and bolt has advanced and corrosion protection is required. Medium priority. | yes | no |  | no |  | 74f06a1a-7250-43d0-84d6-89c659b955c9,ff667873-6ac3-44d0-8382-133eb1f99f38,c8fcce37-8d5c-47d8-95c8-673c6dc21dc6 | ,, | https://web.fulcrumapp.com/photos/view?photos=74f06a1a-7250-43d0-84d6-89c659b955c9%2Cff667873-6ac3-44d0-8382-133eb1f99f38%2Cc8fcce37-8d5c-47d8-95c8-673c6dc21dc6 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
ed09b847-4ec7-485c-9116-6d36b6a078c2 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 23:31:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 396 | 5 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27509 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 396,5 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Dr |  | Very minor corrosion. Low priority defect. | yes |  |  |  |  | 55605167-5390-41b2-bac6-9662e99e62ef,72fe3241-02c5-476b-a59d-37775673b1d0 | , | https://web.fulcrumapp.com/photos/view?photos=55605167-5390-41b2-bac6-9662e99e62ef%2C72fe3241-02c5-476b-a59d-37775673b1d0 | Steel | Channel Bracket-Bolt | Corrosion-Surface
35b185e7-f06b-4d28-8d9e-a8881872931f | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:11:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 396 | 7 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27510 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 396,7 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | Bogdan Stanca |  | The corrosion to the bolt and nut has advanced and surface corrosion to the base plate is noted. Corrosion protection treatment is required. Medium priority. | yes | no |  | no |  | 1be06889-951b-40e6-b6ce-6ada2e25c0e1,6548def3-6e46-467d-a779-942427298ea6,a620d9a0-22df-45fd-b968-7718be49720e,bb121acd-d009-408c-b6c0-3573099fd447 | ,,, | https://web.fulcrumapp.com/photos/view?photos=1be06889-951b-40e6-b6ce-6ada2e25c0e1%2C6548def3-6e46-467d-a779-942427298ea6%2Ca620d9a0-22df-45fd-b968-7718be49720e%2Cbb121acd-d009-408c-b6c0-3573099fd447 | Steel | Conveyor Support | Corrosion-Surface |  | Conveyor Support
b87778a9-82e5-44b3-86a1-def67b851c1a | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:08:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 397 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36673 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 4. >= US$250 million, < US$2 billion |  | Severity Level 4. >= US$250 million, < US$2 billion | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 397, 7 O'clock, Segmented Bolted Joint (Circle Joint). | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint has spalling over an area of 100mm x 400mm. Exposed embedded metal connection with Level 1 corrosion. |  | Circle joint has spalling over an area of 100mm x 400mm. Exposed embedded metal connection with Level 1 corrosion. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Component should be "Segmented Bolted Joint (Circle Joint)". Adopted default consequence Financial - Level 3 | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. BHP WAIO standard drawing 000-S-12618. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The defect has not changed from the last inspection. The defect is at the circular joint. The defect is considered superficial with no structural implication. Low priority. | no | no |  | no |  | 234d876c-0e1b-447a-8682-0eadc1779072,3375af6f-c830-4cbd-87a5-e6acc70e87ee | , | https://web.fulcrumapp.com/photos/view?photos=234d876c-0e1b-447a-8682-0eadc1779072%2C3375af6f-c830-4cbd-87a5-e6acc70e87ee | Concrete | Circular Connection,Circular Joint | Surface Damage |  | Not a reinforcement
acb5b556-ea5b-47c6-9bde-19456e79c3da | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:04:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 398 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36674 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43901.4768 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 398, 11 O'clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | No change. Very minor corrosion. Low priority defect. | yes | no |  | yes |  | 5b4000bd-77d7-4155-a99f-99e23bb6b04e |  | https://web.fulcrumapp.com/photos/view?photos=5b4000bd-77d7-4155-a99f-99e23bb6b04e | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
b81e5f38-9e04-4037-b4bb-d064e9aecb58 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 01:04:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 398 | 9 | Grout Injection Hole | Grout Injection Hole |  | 76422 |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 398, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak Inactive at time of inspection. |  | Grout injection hole has leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineer (CC), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | On-Line | No | - | - | Condition Monitoring Competent Supervisor |  |  |  | no | yes |  | no |  | e6c66229-1500-4b1d-b94a-b5a30ae2dec6,c2bad1cb-c778-4cd5-aadb-5403825e2000 | , | https://web.fulcrumapp.com/photos/view?photos=e6c66229-1500-4b1d-b94a-b5a30ae2dec6%2Cc2bad1cb-c778-4cd5-aadb-5403825e2000 | Concrete | Grout Hole | Leaks
9724e946-e62c-4b08-8360-d935a1774c6d | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 23 | -20.318 | 118.5775 | POINT (118.5774562 -20.317978) | 2025-05-27 20:13:18 AEST | 2025-07-30 02:25:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 398 | 8 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27194 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 398,8 O'Clock,Bolt, Nut, Washer,New Defect 2017 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Skipped due to mud and poor access | [8 empty] | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
833c4f4b-82b2-4f7e-baf6-c97a77b0a32f | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 23 | -20.3218 | 118.5854 | POINT (118.5853511 -20.3217731) | 2025-05-27 20:13:18 AEST | 2025-07-30 02:26:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 398 | 8 | Steel Channel Bracket | Steel Channel Bracket |  | 27195 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 398,8 O'Clock,Support Bracket,New Defect 2017 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Skipped due to poor access caused by mud. | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
c1d1a6ba-a187-4740-8b98-ea42cc118ba8 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:55:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 399 | 12 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 88669 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 44977.6024 |  |  | No | Missing |  | Concrete Damage due to Cast- In |  | 2 | [8 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 399, 12 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | DR |  | Condition remains unchanged. Same area still has drummy concrete with delamination. | no | yes |  | no |  | 3e7b80ec-5066-4c08-9865-48d06a291e53 |  | https://web.fulcrumapp.com/photos/view?photos=3e7b80ec-5066-4c08-9865-48d06a291e53 | Concrete | Circular Joint | Drummy
4f0c3be3-8b93-40d5-9868-8e620d2a51a1 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3218 | 118.5853 | POINT (118.585347 -20.3217734) | 2025-05-27 20:13:18 AEST | 2025-07-27 08:33:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 400 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 76423 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 44732.3391 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 400, 1 O'Clock, Steel Channel Bracket and Anchor Bolt |  |  |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No change. Low priority defect - not structural. Condition 1. Reduced severity | yes | no |  | no |  | 53e4a215-f407-476d-817f-5382b5381cee |  | https://web.fulcrumapp.com/photos/view?photos=53e4a215-f407-476d-817f-5382b5381cee | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
c697d855-0a79-48b5-bdb6-a6e8d7a9ddbf | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:50:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 401 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69302 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 401, 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Inactive leak at time of inspection. Minor deposits of salt along the grout injection hole. Condition 2. Low priority repair. | yes | no |  | no |  | 41e1743b-0c05-449a-9cb8-733354795b7f,f96bddb2-e0c3-4edf-b399-2309fdba2860,933872b1-a4e1-417c-9015-21528b98dc9e | ,, | https://web.fulcrumapp.com/photos/view?photos=41e1743b-0c05-449a-9cb8-733354795b7f%2Cf96bddb2-e0c3-4edf-b399-2309fdba2860%2C933872b1-a4e1-417c-9015-21528b98dc9e | Concrete | Grout Hole | Leaks |  | Not a reinforcement
07b02139-8c44-47ee-a965-9975e3aaf94b | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:50:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 402 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36676 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 402, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | DR |  | Condition remains unchanged. Defect is low priority. | no | yes |  |  |  | 5826687b-c4e0-4881-a2a4-a6a230183de7 |  | https://web.fulcrumapp.com/photos/view?photos=5826687b-c4e0-4881-a2a4-a6a230183de7 | Concrete | Grout Hole | Leaks |  | Not a reinforcement
e9759e5f-2eda-403b-bd63-0b87254b3ee4 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:48:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 403 | 12 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 83983 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 44859.2142 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 403, 12 o'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | Dr |  | Delamination and drummy concrete still present at same location. No change to condition. | no | no |  | no |  | 55f19b68-5c9c-4f74-a6d9-e8b92c04a607 |  | https://web.fulcrumapp.com/photos/view?photos=55f19b68-5c9c-4f74-a6d9-e8b92c04a607 | Concrete | Radial Joint | Drummy
6738d7b8-9280-460f-b339-9891be2849fd | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:45:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 403 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69303 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 403, 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is dry at time of inspection and is a low priority repair. Condition 2. | yes | no |  | no |  | 00cb3542-e831-447a-845f-ae58f3aee9b8,cb53aa1c-e28e-4dd2-ad76-c29bb06c3485,359ee5e6-e43b-4dc0-ad48-40a225d78e69 | ,, | https://web.fulcrumapp.com/photos/view?photos=00cb3542-e831-447a-845f-ae58f3aee9b8%2Ccb53aa1c-e28e-4dd2-ad76-c29bb06c3485%2C359ee5e6-e43b-4dc0-ad48-40a225d78e69 | Concrete | Grout Hole | Leaks |  | Not reinforcement
34c0e2db-9856-4b90-845c-c2891821531f | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:41:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 404 | 1 | Grout Injection Hole | Grout Injection Hole |  | 36677 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 404, 1 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak remains inactive, however there remains a fairly large deposit of salt residue around the surface till 2 O'Clock. Condition 2. | no | no |  | no |  | 7dad61e0-eba7-44d1-ad3b-82db97d37d98 |  | https://web.fulcrumapp.com/photos/view?photos=7dad61e0-eba7-44d1-ad3b-82db97d37d98 | Concrete | Grout Hole | Leaks |  | Not reinforcement
3c284588-9627-469b-aba8-242eccd247cb | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:36:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 404 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 83984 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.217 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 404, 2 o'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Corrosion up 25% coverage. |  | Steel channel support bracket has Level 2 Corrosion up 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No level 2 corrosion observed. Minor corrosion present, not a structural defect. Low priority repair. Condition 2 | yes | no |  | no |  | f7f5ccbf-4983-4aff-ae49-f3a1759be6f2,3f4c127e-aed9-47fc-9479-17fe8a413c58,8b96c381-27cb-4b9c-a35b-70957a7bb05c | ,, | https://web.fulcrumapp.com/photos/view?photos=f7f5ccbf-4983-4aff-ae49-f3a1759be6f2%2C3f4c127e-aed9-47fc-9479-17fe8a413c58%2C8b96c381-27cb-4b9c-a35b-70957a7bb05c | Steel | Channel Bracket | Corrosion-Surface
dbef65af-dc75-4059-aee5-a685e11a9f7d | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3216 | 118.5853 | POINT (118.5852694 -20.3216344) | 2025-05-27 20:13:18 AEST | 2025-07-28 23:24:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 404 | 4 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 83985 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 404, 4 o'clock, Segmented Bolted Joint (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Component should be "Segmented Bolted Joint (Circle Joint)". Adopted default consequence Financial - Level 3. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | On-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Dr |  | No change to condition. Defect at 5 | yes | no |  | yes | Defect location at 5 | a602d40f-3369-4beb-b623-10efc311537e,4cc94c27-bda1-43f4-b74d-a7007c41c44f | , | https://web.fulcrumapp.com/photos/view?photos=a602d40f-3369-4beb-b623-10efc311537e%2C4cc94c27-bda1-43f4-b74d-a7007c41c44f | Concrete | Circular Joint | Drummy
f3726d45-274e-44b3-ba84-d0579f24013a | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:43:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 404 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27215 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 404, 9 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Condition remains unchanged. Leak is still inactive. Condition 2. Low priority defect. | yes | no |  |  |  | 89d30c7f-8345-408f-a5be-ee4d4ac3e816 |  | https://web.fulcrumapp.com/photos/view?photos=89d30c7f-8345-408f-a5be-ee4d4ac3e816 | Concrete | Grout Hole | Leaks |  | Not reinforcement
5f1efeab-ba43-47f1-a15c-8c74db2d557c | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:49:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 406 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27217 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 406,8 o'clock, Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | Dr |  | Incorrect location. Defect at 9 O clock with no change. Leak still remains inactive. | no | no |  | yes | Location needs to be updated. |  |  |  | Concrete | Grout Hole,Reinforcement | Leaks
75ccc4b4-9e56-48f2-9dab-383d1775fc10 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:39:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 407 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36679 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 407, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | DR |  | Condition remains unchanged. Leak still inactive with a deposit of salt around the gout injection hole. | no | yes |  | no |  | 951b7f92-7635-42dc-b95b-333236a99854 |  | https://web.fulcrumapp.com/photos/view?photos=951b7f92-7635-42dc-b95b-333236a99854 | Concrete | Grout Hole | Leaks |  | Not reinforcement
3a901f71-d387-416a-8c89-299668289a88 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:30:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 407 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36680 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 407, 12 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Condition remains unchanged. Leak still inactive at time of inspection | no | no |  |  |  | 66277032-d81a-4527-a3f6-4118df1def04,4c56cfd5-27fc-4f83-b7b2-c0fb45f7b9e3 | , | https://web.fulcrumapp.com/photos/view?photos=66277032-d81a-4527-a3f6-4118df1def04%2C4c56cfd5-27fc-4f83-b7b2-c0fb45f7b9e3 | Concrete | Grout Hole | Leaks |  | Not reinforcement
dc108eb4-6b93-4bfc-ab49-18bd4ddfd804 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 23:41:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 407 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69304 |  | 6856 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 24/10/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 407, 2 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Engineering Repair Methodology Required Competent Engineer | Dr |  | Leak inactive at time of inspection. Grout plug condition unknown. Medium priority defect | no | no |  | no |  | a4d34835-1cf6-4436-a2cd-9a12bf45fc4a,8374a583-1047-4583-85b9-f24bfae81372 | , | https://web.fulcrumapp.com/photos/view?photos=a4d34835-1cf6-4436-a2cd-9a12bf45fc4a%2C8374a583-1047-4583-85b9-f24bfae81372 | Concrete | Grout Hole | Leaks |  | Not reinforcement
d4049556-27fa-48fb-bcf3-501d6f9ebf3f | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3216 | 118.5853 | POINT (118.585269 -20.3216372) | 2025-05-27 20:13:18 AEST | 2025-07-28 23:20:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 407 | 4 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 83986 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 407, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Failure to seal joint | Failure to seal joint |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Component should be "Segmented Bolted Joint (Radial Joint)". Adopted default consequence Health & Safety - Level 2. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Dr |  | Incorrect location. Defect at 5 O Clock Delamination and drumminess of concrete is still present at the radial joint. No change in the condition of the defect | no | yes |  | yes | Defect location must be updated. | e3000b6e-10bd-4cc3-827f-f8df6142df92,fd645fd3-e446-41bb-91b3-3e7cb4f791b8,51ddb50d-62cf-4322-9abd-8cb07c01dd6b | ,, | https://web.fulcrumapp.com/photos/view?photos=e3000b6e-10bd-4cc3-827f-f8df6142df92%2Cfd645fd3-e446-41bb-91b3-3e7cb4f791b8%2C51ddb50d-62cf-4322-9abd-8cb07c01dd6b | Concrete | Circular Joint | Drummy |  | Circular Joint not Radial
e8b14123-1013-47c4-ac71-bb1f62044d84 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 00:43:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 407 | 8 | Grout Injection Hole | Grout Injection Hole |  | 36678 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 407, 8 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. Low priority | no | yes |  | no |  | 8ffbacc5-6579-406d-bfcc-44ebe3e2a476,b977e818-b720-44dd-8f85-cb34895100b5,5ed978d3-aa85-4786-898f-c2d16bff0d58 | ,, | https://web.fulcrumapp.com/photos/view?photos=8ffbacc5-6579-406d-bfcc-44ebe3e2a476%2Cb977e818-b720-44dd-8f85-cb34895100b5%2C5ed978d3-aa85-4786-898f-c2d16bff0d58 | Concrete | Grout Hole | Leaks |  | Not reinforcement
a93597df-8e51-43d3-95a5-f54ad5856786 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 04:26:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 408 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 83987 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.2225 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 408, 2 o'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Corrosion up 25% coverage. |  | Steel channel support bracket has Level 2 Corrosion up 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | No level 2 corrosion observed at specified steel bracket. Minor corrosion present, low priority - not a structural defect. | yes | no |  | yes | Removal of defect. | 6de41093-8af6-466d-81bd-823337bb1369,570bc228-4c7f-4688-bcd1-3794c3c6028a,efa41b40-a435-4142-b6c6-87a7967982b1 | ,, | https://web.fulcrumapp.com/photos/view?photos=6de41093-8af6-466d-81bd-823337bb1369%2C570bc228-4c7f-4688-bcd1-3794c3c6028a%2Cefa41b40-a435-4142-b6c6-87a7967982b1 | Steel | Channel Bracket | Corrosion-Surface
7cbd8598-c14b-45ca-98d0-284ff4d81147 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 10:12:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 408 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36681 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 408, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Slight drumminess in concrete. Size 500x200mm. Risk low | yes | no |  | no |  | c9040830-1680-46ac-9753-302fc068cec4,9269ed15-5b9a-4894-b44d-83becf78e7ab | , | https://web.fulcrumapp.com/photos/view?photos=c9040830-1680-46ac-9753-302fc068cec4%2C9269ed15-5b9a-4894-b44d-83becf78e7ab | Concrete | Grout Hole | Drummy,Leaks |  | Not reinforcement
7144fdf3-94a8-4699-90a3-56cdde923960 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 11:34:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 409 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36682 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 409, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is dry at time of inspection and has been repaired. Low priority defect. | yes | no |  | yes | Reducing severity | 94b1fbc1-6506-494e-8521-f05b8246f961,173f181a-1b1e-4fcd-8b12-e241ad6b90f6 | , | https://web.fulcrumapp.com/photos/view?photos=94b1fbc1-6506-494e-8521-f05b8246f961%2C173f181a-1b1e-4fcd-8b12-e241ad6b90f6 | Concrete | Grout Hole | Leaks |  | Not reinforcement
68c48880-f9f7-485e-b2b7-b078c74cf36f | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 10:47:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 409 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69305 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 409, 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged, dry leak chloride induced. | [5 empty] | d34814cf-4630-41f9-a5d9-2e78e55969db,a40f4130-e6f8-4d19-bb41-8f1fba522faa | , | https://web.fulcrumapp.com/photos/view?photos=d34814cf-4630-41f9-a5d9-2e78e55969db%2Ca40f4130-e6f8-4d19-bb41-8f1fba522faa | Concrete | Grout Hole | Leaks |  | Not reinforcement
fb4c04e8-66e8-4a87-9cb5-c473d45003eb | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 10:40:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 411 | 0 | Grout Injection Hole | Grout Injection Hole |  | 69306 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 411, 1 & 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Grout injection hole has been sealed. | [5 empty] | b0ea61aa-aa55-4ae0-b632-82fb6bee4bc6,82c8e9d2-5144-4e3b-ac2a-a6b7efa0abe4,64221e7d-e81f-4234-b320-2f68060a1074,71cd90df-1c9e-412d-b055-420709876562 | ,,, | https://web.fulcrumapp.com/photos/view?photos=b0ea61aa-aa55-4ae0-b632-82fb6bee4bc6%2C82c8e9d2-5144-4e3b-ac2a-a6b7efa0abe4%2C64221e7d-e81f-4234-b320-2f68060a1074%2C71cd90df-1c9e-412d-b055-420709876562 | Concrete | Grout Hole | Leaks |  | Not reinforcement
85058dd4-d83f-486a-a1d9-41db32fb8987 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 18:53:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 411 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36683 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 411, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 0b3db613-839d-4ccc-af0f-3938638d72cf |  | https://web.fulcrumapp.com/photos/view?photos=0b3db613-839d-4ccc-af0f-3938638d72cf | Concrete | Grout Hole | Leaks |  | Not reinforcement
a8a9b8e3-8131-4a60-b46d-811954a1cf1f | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 10:59:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 412 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69307 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 412, 1 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Dry leakage chloride induced. Condition unchanged | [5 empty] | 12920104-164f-4c13-b57d-7c1d023a8fd4 |  | https://web.fulcrumapp.com/photos/view?photos=12920104-164f-4c13-b57d-7c1d023a8fd4 | Concrete | Grout Hole | Leaks |  | Not reinforcement
e86831fb-da49-4f27-9ddd-143e16a1f137 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:01:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 412 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36684 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 412, 3 &4 o'clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Loss of production and services | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Condition unchanged | [5 empty] | a0c14c79-9c99-4e57-ad99-46eee8748144 |  | https://web.fulcrumapp.com/photos/view?photos=a0c14c79-9c99-4e57-ad99-46eee8748144 | Concrete |  | Leaks |  | Not reinforcement
261e1a01-43fa-4f31-84d8-2cdd483799c8 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 412 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69308 |  | 8714 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Other Damage not Covered |  | Other Damage not Covered | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 412, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 to Level 5 Corrosion. Channel anchor bolts are missing. |  | Steel channel support bracket has Level 4 to Level 5 Corrosion. Channel anchor bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Replace corroded channels brackets and anchor bolts. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | [11 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
932a433d-147c-4a27-b7ce-bedb5736a5a9 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:43:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 412 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93626 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 412, 5 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | On-Line | No | - | - | Standard Repair Detail Competent Supervisor | KP |  | The walkway support is severely corroded as well as drummy grout along the radial joint | yes |  |  |  |  | 44bcf1f1-0265-4393-99b8-3c6965e48adc |  | https://web.fulcrumapp.com/photos/view?photos=44bcf1f1-0265-4393-99b8-3c6965e48adc | Concrete | Radial Joint,Walkway Support | Drummy
19545804-0ac9-4147-9ef2-2ffb24342940 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3217 | 118.5853 | POINT (118.5852827 -20.3216544) | 2025-05-27 20:13:18 AEST | 2025-07-25 18:50:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 413 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93632 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 413, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Condition not changed, still drummy patch repair along radial joint | no |  |  |  |  | c50a0230-cf54-46b4-bdef-36342f70bfae,5b5c076a-dadb-48c9-bedd-836134ff84a9 | , | https://web.fulcrumapp.com/photos/view?photos=c50a0230-cf54-46b4-bdef-36342f70bfae%2C5b5c076a-dadb-48c9-bedd-836134ff84a9 | Concrete | Radial Joint | Drummy
daefa5cd-bc49-45a4-af10-73ffa01039b8 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:14:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 414 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36686 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.4879 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 414, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket is missing a fastener. |  | Steel channel support bracket is missing a fastener. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | On-Line |  |  |  |  | RT |  | Missing fastener | [5 empty] | 42d8689d-39e0-451f-b540-7ccd998a3e62 |  | https://web.fulcrumapp.com/photos/view?photos=42d8689d-39e0-451f-b540-7ccd998a3e62 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
08582d67-041a-42b0-884f-c76c6af9d06a | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3217 | 118.5853 | POINT (118.5852817 -20.3216542) | 2025-05-27 20:13:18 AEST | 2025-07-28 11:48:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 414 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69309 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 414, 5 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints over an area of 200mm x 200mm. |  | Grout Delamination / debonding at radial segment bolted joints over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Remediate concrete as per BHP Standards and specifications | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | Delimited grout/ drummy area along the radial joint 300x200mm. | yes |  |  |  |  | 7a928768-a161-47c9-a6d7-d8cb1f85553f,7fd53a94-3210-44e0-98d7-80baee739b5b | , | https://web.fulcrumapp.com/photos/view?photos=7a928768-a161-47c9-a6d7-d8cb1f85553f%2C7fd53a94-3210-44e0-98d7-80baee739b5b | Concrete | Radial Joint | Drummy
f4ca4f17-0b73-4634-9d43-907deefaeecb | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 18:39:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 415 | 12 | Hydrophilic Joint Seal (Circle Joint) | Hydrophilic Joint Seal (Circle Joint) |  | 36687 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 43901.4887 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 415, 12 o'clock. Hydrophilic Joint Seal (Circle Joint) |  |  |  | Hydrophilic Joint (Circle Joint) has 6mm offset at circumferential joint between ring 415 and 416. Offset possibly from construction. |  | Hydrophilic Joint (Circle Joint) has 6mm offset at circumferential joint between ring 415 and 416. Offset possibly from construction. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Offset has remained to be same as observed last time (6.0 mm) | no |  |  |  |  | 027eb9e1-6fac-48ff-a7cb-9863575983e6 |  | https://web.fulcrumapp.com/photos/view?photos=027eb9e1-6fac-48ff-a7cb-9863575983e6 | Concrete | Circular Connection,Circular Joint | Displacement
ac21bf47-698d-427f-b297-826f40efad13 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 18:37:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 416 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36689 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 416, 12 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Engineering Repair Methodology Required Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | e1980d52-8b1f-4027-8b3a-cf8e88dac5b4 |  | https://web.fulcrumapp.com/photos/view?photos=e1980d52-8b1f-4027-8b3a-cf8e88dac5b4 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
5a5807c5-2a4e-44bc-af56-783b6db2561d | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:35:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 417 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69310 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 417, 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Dry leakage chloride induced. Condition unchanged. | [5 empty] | aea1bccb-fb25-4120-b980-39854aa0ec31,d96203a9-7e0c-45f9-9596-ed1f2df0d538 | , | https://web.fulcrumapp.com/photos/view?photos=aea1bccb-fb25-4120-b980-39854aa0ec31%2Cd96203a9-7e0c-45f9-9596-ed1f2df0d538 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
7e2b524b-8254-42d2-8c85-2eeaa626985d | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3216 | 118.5853 | POINT (118.5852711 -20.3216416) | 2025-05-27 20:13:18 AEST | 2025-07-28 11:54:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 417 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93633 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 417, 5 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Delimited/ Drummy grout still appears to be there, no change in the condition | no |  |  |  |  | 2934a1f2-3b3c-44bd-99ed-5f16d78bea44 |  | https://web.fulcrumapp.com/photos/view?photos=2934a1f2-3b3c-44bd-99ed-5f16d78bea44 | Concrete | Circular Joint | Drummy
94eea390-468b-4351-b099-71a03b6f3f04 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:40:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 418 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36690 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.4908 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 418, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket is missing a nut fastener. |  | Steel channel support bracket is missing a nut fastener. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | RT |  | Bolt missing, condition unchanged. | [5 empty] | 308abadc-1379-4f23-8b1b-d1b377c0e739 |  | https://web.fulcrumapp.com/photos/view?photos=308abadc-1379-4f23-8b1b-d1b377c0e739 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
33cf16c4-23d5-48e6-b5f5-d255bb1f12b4 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 09:30:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 419 | 10 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93634 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 419, 10 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | no |  |  |  |  | 6337c4c7-3f67-4f43-a61d-21825d33b846,4a608612-c1b7-4afd-b97b-4cd7c98fee29 | , | https://web.fulcrumapp.com/photos/view?photos=6337c4c7-3f67-4f43-a61d-21825d33b846%2C4a608612-c1b7-4afd-b97b-4cd7c98fee29 | Concrete | Radial Joint | Drummy
a9eb6928-1ee5-4b49-bde7-214235cf0d6e | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:43:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 419 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69311 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 419, 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Dry leakage chloride induced. No change. | [5 empty] | 86260a13-410b-49e5-8a34-b060ca41d739,9483aa06-2253-45b7-9107-1e4cdeb30dfc | , | https://web.fulcrumapp.com/photos/view?photos=86260a13-410b-49e5-8a34-b060ca41d739%2C9483aa06-2253-45b7-9107-1e4cdeb30dfc | Concrete | Grout Hole | Leaks |  | Not Reinforcement
f232ee2b-f8ec-409a-ac82-d13e43fb45b2 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 18:16:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 420 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36692 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 420, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 40ecce58-aa4b-468f-ade8-bfc2e969251f |  | https://web.fulcrumapp.com/photos/view?photos=40ecce58-aa4b-468f-ade8-bfc2e969251f | Concrete | Grout Hole | Leaks |  | Not Reinforcement
ae8c9cbf-1eef-4896-81c9-3bca99a3eeb3 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:45:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 420 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69312 |  | 6512 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Repair Verified | 22/12/2021 |  | 17/02/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Loose Bolt |  | Loose Bolt | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 420, 2 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts are loose. |  | Channel anchor bolts are loose. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Remediate concrete as per BHP Standards and specifications | Priority: P3 |  |  |  | Replace missing and refasten loose anchor bolts as per original approved design. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | Scaffolding | Working at Heights | Maintenance Repair Competent Supervisor | RT |  | Defect remediated | [5 empty] | 1649d09f-9c0b-4073-bd21-cc863e6b6c93 |  | https://web.fulcrumapp.com/photos/view?photos=1649d09f-9c0b-4073-bd21-cc863e6b6c93 | Steel | Channel Bracket,Channel Bracket-Bolt | Loose
027b0a63-9442-42f4-846f-fc78e20d5071 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 24 | -20.3217 | 118.5853 | POINT (118.5852848 -20.3216698) | 2025-05-27 20:13:18 AEST | 2025-07-28 11:51:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 420 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93636 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 420, 8 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged, high priority. | [5 empty] | 3bbd316b-9e98-4667-a154-2cddab881a83,9cce90cb-dcbd-4129-aa60-bb3412d43f2a | , | https://web.fulcrumapp.com/photos/view?photos=3bbd316b-9e98-4667-a154-2cddab881a83%2C9cce90cb-dcbd-4129-aa60-bb3412d43f2a | Concrete | Circular Connection | Drummy |  | Circular Connection
1a48db1d-27cc-4ea8-a587-bb5b2033e879 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 17 | -20.3217 | 118.5853 | POINT (118.5852806 -20.3216511) | 2025-07-25 19:06:46 AEST | 2025-07-27 08:35:33 AEST | 30011704-user5@smec.com | james.stone@smec.com | 420 | 7 O'Clock |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Offset in between rings of 6mm | [5 empty] | 57bd0190-508c-4f4a-b764-7e24255d8960 |  | https://web.fulcrumapp.com/photos/view?photos=57bd0190-508c-4f4a-b764-7e24255d8960 | Concrete | Circular Connection | Displacement |  | Circular Connection
b365c24f-8b20-4077-ad63-6216dfb5b3e0 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 17 | -20.3218 | 118.5854 | POINT (118.5853531 -20.3217705) | 2025-07-26 09:57:29 AEST | 2025-07-27 08:35:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 411 | 10 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess in concrete size 200x400mm. Risk low | [5 empty] | e7ab0e19-b194-4d70-ae92-de20dd18fcd5 |  | https://web.fulcrumapp.com/photos/view?photos=e7ab0e19-b194-4d70-ae92-de20dd18fcd5 | Concrete | Circular Joint | Drummy |  | Circular Joint
ad7fc94b-e0c9-429a-9c11-478efef03006 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 17 | -20.3218 | 118.5853 | POINT (118.5853264 -20.3217688) | 2025-07-26 10:23:56 AEST | 2025-07-27 08:36:15 AEST | 30011704-user5@smec.com | james.stone@smec.com | 408 | 7 O'Clock |  |  | Structural footings | [56 empty] | RT |  | Active rusting on bolts and structural footings. | [5 empty] | 79e95a8e-eab5-48c3-b355-955f80618082 |  | https://web.fulcrumapp.com/photos/view?photos=79e95a8e-eab5-48c3-b355-955f80618082 | Steel | Conveyor Support | Corrosion-Surface |  | Conveyor Support
9ab37c1a-a49a-4cfb-aee3-3d2935679000 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 16 |  |  |  | 2025-07-26 11:10:24 AEST | 2025-07-26 11:15:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 409 | 5 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate is corroding as well as the bolts are heavily corroded . Structural steel supporting the walkway is heavily corroded. High priority. | [5 empty] | 58a43ba6-d5ef-403a-b628-ce5fcbf2e2ad,06ae60a8-ab7f-4d0d-88db-75022aaf2e79,29f98391-9243-4fb5-9dc0-1a80d243925f | ,, | https://web.fulcrumapp.com/photos/view?photos=58a43ba6-d5ef-403a-b628-ce5fcbf2e2ad%2C06ae60a8-ab7f-4d0d-88db-75022aaf2e79%2C29f98391-9243-4fb5-9dc0-1a80d243925f | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support
fc14b70d-02d2-46f6-8d6d-4c3564a2a335 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 16 |  |  |  | 2025-07-26 11:57:06 AEST | 2025-07-26 19:42:02 AEST | 30011704-user5@smec.com | james.stone@smec.com | 412 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate is corroding as well as the bolts are heavily corroded . Structural steel supporting the walkway is heavily corroded. High priority. |  | yes |  |  |  | 1fab9147-1bc8-40b0-a1a2-dfc28d1290d6,72a9e528-421d-411e-8ef5-a59f00b9d13f,18df65da-5c26-4458-bc21-09a4ef0f84df,b394e39f-eda1-4b6a-825e-3d282654f918 | ,,, | https://web.fulcrumapp.com/photos/view?photos=1fab9147-1bc8-40b0-a1a2-dfc28d1290d6%2C72a9e528-421d-411e-8ef5-a59f00b9d13f%2C18df65da-5c26-4458-bc21-09a4ef0f84df%2Cb394e39f-eda1-4b6a-825e-3d282654f918 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support
0feb4245-5e3b-4b56-b9ef-242d20dfdad5 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 16 |  |  |  | 2025-07-26 12:10:54 AEST | 2025-07-26 19:42:08 AEST | 30011704-user5@smec.com | james.stone@smec.com | 416 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate is actively corroding as well as the bolts are heavily corroded . Structural steel supporting the walkway is corroded at the bottom.High priority. |  | yes |  |  |  | 0f78da60-fa46-45f5-b7d5-b58822571263,47973566-dde1-418c-a614-14302487cc6f,ab16dba1-e23e-4dbf-a840-72660e552394,2426bb37-ce61-42da-99ab-8f0191a5654e | ,,, | https://web.fulcrumapp.com/photos/view?photos=0f78da60-fa46-45f5-b7d5-b58822571263%2C47973566-dde1-418c-a614-14302487cc6f%2Cab16dba1-e23e-4dbf-a840-72660e552394%2C2426bb37-ce61-42da-99ab-8f0191a5654e | Steel | Centre Support,Centre Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | CEntre and walkway Support
7c2f508a-5a13-441b-82c3-506740408f7b | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 16 |  |  |  | 2025-07-26 12:44:45 AEST | 2025-07-26 19:42:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 420 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate is actively corroding as well as the bolts are heavily corroded . Structural steel supporting the walkway is corroded at the bottom.High priority. |  | yes |  |  |  | 2cb6ab90-c410-4cfc-960e-8165914dd96d,7ab57503-2311-4e14-8de0-8291dec6c1cf,c9955b6e-12e8-491c-b6d2-2d624be4fb84 | ,, | https://web.fulcrumapp.com/photos/view?photos=2cb6ab90-c410-4cfc-960e-8165914dd96d%2C7ab57503-2311-4e14-8de0-8291dec6c1cf%2Cc9955b6e-12e8-491c-b6d2-2d624be4fb84 | Steel | Centre Support,Centre Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Centre and walkway suport
6e637fa7-fb55-4b9d-9866-99c6be320da6 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 17 | -20.3218 | 118.5854 | POINT (118.5853553 -20.3217747) | 2025-07-26 10:58:37 AEST | 2025-07-27 08:36:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 412 | 7 O'Clock |  |  | support structure | [56 empty] | RT |  | Rusted weld joints and bolts. Condition moderate | [5 empty] | 65bc5386-1da0-4189-914d-386ae7a4131d |  | https://web.fulcrumapp.com/photos/view?photos=65bc5386-1da0-4189-914d-386ae7a4131d | Steel | Centre Support | Corrosion-Surface
a2e06fb9-46c7-4058-96a9-a05c43e0c8ee | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 17 | -20.3218 | 118.5854 | POINT (118.5853621 -20.3217545) | 2025-07-26 11:17:01 AEST | 2025-07-27 08:37:16 AEST | 30011704-user5@smec.com | james.stone@smec.com | 413 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Slight drumminess in concrete, size 150x150mm. Low priority | [5 empty] | e709b68a-6b69-4777-9d47-f05a4311fff8 |  | https://web.fulcrumapp.com/photos/view?photos=e709b68a-6b69-4777-9d47-f05a4311fff8 | Concrete |  | Drummy
0f6f0cf3-1455-4055-ab47-84f556b15470 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 17 | -20.3218 | 118.5854 | POINT (118.5853715 -20.3217585) | 2025-07-26 11:52:58 AEST | 2025-07-27 08:38:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 416 | 7 O'Clock |  |  | structural footing | [56 empty] | RT |  | Presence of active rust on the footing. 1x bolt has failed, active rust may lead to accelerated loss of structural integrity of other components upholding the structure. This may lead to dislocation of footing. Medium priority | [5 empty] | 83912569-7056-438e-84e6-7f0d734ec626 |  | https://web.fulcrumapp.com/photos/view?photos=83912569-7056-438e-84e6-7f0d734ec626 | Steel | Centre Support | Corrosion-Surface
577ae0da-e6ac-4559-a45b-0f2700766d59 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 17 | -20.3218 | 118.5853 | POINT (118.5853322 -20.3217526) | 2025-07-26 12:00:30 AEST | 2025-07-27 08:38:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 420 | 7 O'Clock |  |  | Structural footings | [56 empty] | RT |  | Loss of surface on footing with presence of active rust. May compromise the structural integrity of the lower section of the footing and reduce the load bearing capacity. Medium priority | [5 empty] | a3ab9164-4315-4f34-aae2-fc88a907e576 |  | https://web.fulcrumapp.com/photos/view?photos=a3ab9164-4315-4f34-aae2-fc88a907e576 | Steel | Centre Support | Corrosion-Surface
43740b9e-a244-45d7-b340-6e63eda7a65e | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 19 |  |  |  | 2025-07-26 01:17:06 AEST | 2025-07-26 01:18:40 AEST | 30011704-user5@smec.com | james.stone@smec.com | 392 | 9 O Clock |  | Hydrophilic Joint Seal (Circle Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 3 |  |  |  | Health & Safety | [35 empty] | Dr |  | Delamination and drumminess on circumferential joint 200mm x 300mm |  | yes |  | no |  | fcb86e52-f0f2-41de-95c5-6602c1a60b1d,42cbfc11-133f-4c4c-804f-62163fe7e19d | , | https://web.fulcrumapp.com/photos/view?photos=fcb86e52-f0f2-41de-95c5-6602c1a60b1d%2C42cbfc11-133f-4c4c-804f-62163fe7e19d | Concrete | Circular Connection,Circular Joint | Drummy
8b2a0a49-1ff2-4930-b894-2a3e342e0fff | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 19 |  |  |  | 2025-07-26 05:14:21 AEST | 2025-07-26 05:16:03 AEST | 30011704-user5@smec.com | james.stone@smec.com | 394 | 2 O'Clock |  | Hydrophilic Joint Seal (Radial Joint) | [57 empty] | Dr |  | Hairline crack of 2mm present on patchwork carried out. |  | yes |  | no |  | 9a100f85-63c2-4d0b-a7f5-13e48761af2c,d7582504-aae6-44d4-97e1-929f9aad7422 | , | https://web.fulcrumapp.com/photos/view?photos=9a100f85-63c2-4d0b-a7f5-13e48761af2c%2Cd7582504-aae6-44d4-97e1-929f9aad7422 | Concrete | Radial Joint | Crack
e5ebe5b0-9d92-4790-9f7a-bd5372ad23d4 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 20 |  |  |  | 2025-07-25 18:24:44 AEST | 2025-07-25 18:26:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 418 | 10 o’clock to 11 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Signs of surface corrosion along the steel channel. | [5 empty] | d14b563c-f8d8-4f01-bc57-53d6045e378a,bf332a30-5574-4a12-89b1-93387ebb4265 | , | https://web.fulcrumapp.com/photos/view?photos=d14b563c-f8d8-4f01-bc57-53d6045e378a%2Cbf332a30-5574-4a12-89b1-93387ebb4265 | Steel | Channel Bracket | Corrosion-Surface
4c1604ee-3cf6-4e05-9f75-e361468fd378 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 20 |  |  |  | 2025-07-25 18:42:24 AEST | 2025-07-25 18:44:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 414 | 10 o’clock to 12 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Signs of active surface corrosion along the steel channel. | [5 empty] | 05c30767-c572-4c6d-867c-90e9eca00e15,caa98eb3-993b-48d0-a82b-44623e829b26,ed0e062e-81f7-4a62-b20b-9136c1c560a6 | ,, | https://web.fulcrumapp.com/photos/view?photos=05c30767-c572-4c6d-867c-90e9eca00e15%2Ccaa98eb3-993b-48d0-a82b-44623e829b26%2Ced0e062e-81f7-4a62-b20b-9136c1c560a6 | Steel | Channel Bracket | Corrosion-Surface
dcdb2339-01c6-4513-a799-02200d8bdbe2 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 11 | -20.3217 | 118.5853 | POINT (118.5852826 -20.3216959) | 2025-07-28 11:03:33 AEST | 2025-07-30 05:04:54 AEST | 30011704-user5@smec.com | james.stone@smec.com | 412 | 3 |  | Channel Anchor Bolts | [57 empty] | RT |  | Dry leakage chloride induced. Medium priority. | [5 empty] | bf4b1fec-cffb-4911-b221-d0d928b97e07,5900b4e0-21f1-47e0-81b1-9afdbfbf3bc8 | , | https://web.fulcrumapp.com/photos/view?photos=bf4b1fec-cffb-4911-b221-d0d928b97e07%2C5900b4e0-21f1-47e0-81b1-9afdbfbf3bc8 | Steel | Channel Bracket-Bolt | Leaks
28aab728-1120-4b5d-a203-6dd718e3ec23 | a4ab9852-aae4-4525-a1e0-d027c91a211a | a4ab9852-aae4-4525-a1e0-d027c91a211a | 11 |  |  |  | 2025-07-28 11:27:27 AEST | 2025-07-28 11:32:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 416-417 | 2 |  | Hydrophilic Joint Seal (Radial Joint) | [57 empty] | RT |  | Offset of 4mm in between rings. | [5 empty] | 195230eb-814e-4521-9550-a0c4ca108023 |  | https://web.fulcrumapp.com/photos/view?photos=195230eb-814e-4521-9550-a0c4ca108023 | Concrete | Radial Joint | Displacement
d1bdc7d4-c31a-420f-9c1e-b4d030f9f3f1 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:43:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 421 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26963 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 421, 11 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | da811ca8-27ee-4906-8017-90df57aa57b1 |  | https://web.fulcrumapp.com/photos/view?photos=da811ca8-27ee-4906-8017-90df57aa57b1 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
66f86778-2e63-4052-a030-86afdb693a4e | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:25:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 421 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27224 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 421, 2 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. |  | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Very Rare Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | The grout injection hole had an inactive leak at the time of inspection | no |  |  |  |  | cfbb1515-8aa5-4c79-bc0b-fbe576855433 |  | https://web.fulcrumapp.com/photos/view?photos=cfbb1515-8aa5-4c79-bc0b-fbe576855433 | Concrete | Grout Hole | Leaks
f31e2e1d-7b6a-4415-b3ff-bdf420f67b61 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:39:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 422 | 11 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 83988 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 422, 11 o'clock, Segmented Bolted Joint (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Component should be "Segmented Bolted Joint (Circle Joint)". Adopted default consequence Financial - Level 3. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | KP |  | Condition not changed, drummy patch repair along circumferential joint | no |  |  |  |  | 0135ab13-042d-4be8-987c-3f14ca845e4f |  | https://web.fulcrumapp.com/photos/view?photos=0135ab13-042d-4be8-987c-3f14ca845e4f | Concrete | Circular Connection,Circular Joint | Drummy
08a454d3-9655-499a-a3a8-5186d15dbf55 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:35:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 423 | 10 | Hydrophilic Joint Seal (Radial Joint) | Hydrophilic Joint Seal (Radial Joint) |  | 93638 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 423, 10 O'Clock, Segmented Bolted Joint (Radial Joint) | Failure to seal joint | Failure to seal joint |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. Component should be "Segmented Bolted Joint (Radial Joint)". Adopted default consequence Health & Safety - Level 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Condition no changed, drummy patch repair along radial joint | no |  |  |  |  | f42eec06-5c0c-4c7e-a6ae-52e7dd2ac4e6 |  | https://web.fulcrumapp.com/photos/view?photos=f42eec06-5c0c-4c7e-a6ae-52e7dd2ac4e6 | Concrete | Radial Joint | Drummy
351cfc2d-d4e3-403d-812a-ade5a62454cc | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:34:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 423 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36693 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 423, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | bee00b07-ba81-4062-896d-9ec9358fc2fd |  | https://web.fulcrumapp.com/photos/view?photos=bee00b07-ba81-4062-896d-9ec9358fc2fd | Concrete | Grout Hole | Leaks |  | Not Reinforcement
5d6f842e-ae81-4b2c-800b-2939d632d841 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:19:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 423 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69313 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 44552.1358 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 423, 2 o'clock, Grout Injection Hole |  |  |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Grout injection hole had inactive leak at the time of inspection, no change in condition | no |  |  |  |  | 5c037c7a-b648-412e-8c3b-3ad834ed4513 |  | https://web.fulcrumapp.com/photos/view?photos=5c037c7a-b648-412e-8c3b-3ad834ed4513 | Concrete | Grout Hole | Leaks
1e102bb8-d7d7-47b3-8993-31175d5b42ab | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:03:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 423 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93639 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 423, 5 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Delimited/drummy grout still in the same area , no change | no |  |  |  |  | f348bf0a-7a79-43b9-bad8-b247e319d7b3 |  | https://web.fulcrumapp.com/photos/view?photos=f348bf0a-7a79-43b9-bad8-b247e319d7b3 | Concrete | Circular Joint | Drummy
f4d0f6b1-6ac1-4f4f-b008-a7198cc92c20 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:16:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 424 | 1 | Grout Injection Hole | Grout Injection Hole |  | 36696 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 424, 1 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection point had inactive leak at the time of inspection, no change in condition | no |  |  |  |  | cbc85857-3148-44dc-b467-1a92d8d815eb |  | https://web.fulcrumapp.com/photos/view?photos=cbc85857-3148-44dc-b467-1a92d8d815eb | Concrete | Grout Hole | Leaks |  | Not Reinforcement
510f7336-5adf-42d9-aae9-5be4e0da237b | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:34:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 424 | 11 | Grout Injection Hole | Grout Injection Hole |  | 83990 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 424, 11 o'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding, Walkway | - | Standard Repair Detail Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | yes |  |  |  |  | b3f8f1c6-a776-4576-8c43-3d2b3102dac6 |  | https://web.fulcrumapp.com/photos/view?photos=b3f8f1c6-a776-4576-8c43-3d2b3102dac6 | Concrete | Grout Hole | Leaks
f3a62cb4-9cd4-40da-a6d3-1c56ddad57af | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 424 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36694 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 424, 7 o'clock, Segment bolted joint (circle joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint,Reinforcement | Drummy
6d29dc2d-fe5c-43f4-ab93-d88178ae742a | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 18:44:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 424 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36695 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 424, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 1b1fafb5-6a7a-4c08-8eb4-33563c558c9b |  | https://web.fulcrumapp.com/photos/view?photos=1b1fafb5-6a7a-4c08-8eb4-33563c558c9b | Concrete | Grout Hole | Leaks |  | Not Reinforcement
9ff91af0-9680-41e9-94e1-99ac29fa5d42 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:13:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 425 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 83991 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 44859.2894 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 425, 1 o'clock, Concrete shell segment |  |  |  | Concrete shell segment has Cracking - hairline crack at two locations extending 0.15m and 0.3mm in width. |  | Concrete shell segment has Cracking - hairline crack at two locations extending 0.15m and 0.3mm in width. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | The hairline crack along the concrete still appears to be of same size as recorded in the past | no |  |  |  |  | d487f111-4067-4d88-9e38-6694bbd8cb3c,fec0f1a9-5375-44b3-9ffb-e54b2b804750,7c9c3c30-ca9b-4c15-94e3-a265ecfc022b | ,, | https://web.fulcrumapp.com/photos/view?photos=d487f111-4067-4d88-9e38-6694bbd8cb3c%2Cfec0f1a9-5375-44b3-9ffb-e54b2b804750%2C7c9c3c30-ca9b-4c15-94e3-a265ecfc022b | Concrete | Radial Joint,Grout Hole | Crack |  | Radial joint and grout hole
98a2a2b1-663f-45ee-8bfb-11424b6ee7c3 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 13:41:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 425 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69314 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 425, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | a43af0f3-2777-4d7f-91af-5a8633d92de5 |  | https://web.fulcrumapp.com/photos/view?photos=a43af0f3-2777-4d7f-91af-5a8633d92de5 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
e67840b0-e093-468d-9ef0-2d619113b4f1 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:07:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 425 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 83992 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 425, 5 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | - | - | Standard Repair Detail Competent Supervisor | KP |  | Delimited/drummy grout along the circumferential joint still present, no change in the condition | no |  |  |  |  | e8b70c58-3384-475c-bd07-9f9a6fc7905c |  | https://web.fulcrumapp.com/photos/view?photos=e8b70c58-3384-475c-bd07-9f9a6fc7905c | Concrete | Circular Connection,Circular Joint | Drummy
64e18dc1-ca53-4d31-9638-dbb5288276ed | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:07:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 426 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 69316 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.1477 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 426, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 5% coverage. |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 5% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Steel channel appears to be in fair condition | yes |  |  |  |  | 1650092d-f6be-4360-afa1-bb3a7ec3ca58,ae3e8e24-4bdd-4611-9e99-8b9c5e088b6b | , | https://web.fulcrumapp.com/photos/view?photos=1650092d-f6be-4360-afa1-bb3a7ec3ca58%2Cae3e8e24-4bdd-4611-9e99-8b9c5e088b6b | Steel | Channel Bracket | Corrosion-Surface
17b2744a-8e99-4312-99c3-3ad0c0166bec | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:28:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 426 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26966 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 426, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket bolts have Level 2 - Medium Low Corrosion and numerous bolts are missing. Steel channel has Level 2 corrosion at 5% coverage. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket bolts have Level 2 - Medium Low Corrosion and numerous bolts are missing. Steel channel has Level 2 corrosion at 5% coverage. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | 426 |  | Condition unchanged, corrosion along the steel channel and 2 bolts are missing one at 11 o clock and 1 at 10 o’clock | no |  |  |  |  | a707791e-8130-423e-b49a-716e850d2992 |  | https://web.fulcrumapp.com/photos/view?photos=a707791e-8130-423e-b49a-716e850d2992 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
a109e3f1-3302-4466-ae11-28b164b36081 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:09:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 426 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 69315 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.1394 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 426, 3 o'clock, Steel Channel Support Bracket. |  |  |  | Steel channel bracket has Level 2 corrosion up 75% coverage. |  | Steel channel bracket has Level 2 corrosion up 75% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Change in the condition, it appears to have severely corroded steel channel as well as bolt | yes |  |  |  |  | 9f3774cb-bd81-4cf4-8f4f-40b8e31ee057 |  | https://web.fulcrumapp.com/photos/view?photos=9f3774cb-bd81-4cf4-8f4f-40b8e31ee057 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
6f6b81e8-f27e-4fff-8161-829097ef98dd | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:11:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 426 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93640 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 426, 5 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Delimited/drummy grout still present along the radial joint | no |  |  |  |  | f7a819c0-7744-43f5-9741-0055e51b6db7 |  | https://web.fulcrumapp.com/photos/view?photos=f7a819c0-7744-43f5-9741-0055e51b6db7 | Concrete | Radial Joint | Drummy
7c6b65a3-6d2c-462b-83ec-a55cb150bd62 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:01:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 428 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69317 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.1543 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 428, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 1 Low Corrosion. |  | Channel anchor bolts have Level 1 Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still appears to have minor surface corrosion on bolt | no |  |  |  |  | 708572c3-b756-4202-bb8b-22d81e363164 |  | https://web.fulcrumapp.com/photos/view?photos=708572c3-b756-4202-bb8b-22d81e363164 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
d7940fb4-a0a9-47fa-b4eb-cacf229136d6 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 11:00:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 428 | 3 o’clock | Steel Channel Bracket | Steel Channel Bracket |  | 69318 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.1556 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 428, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel bracket has Level 2 - Minor Corrosion up to 100% coverage. |  | Steel channel bracket has Level 2 - Minor Corrosion up to 100% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still appears to have minor surface corrosion | no |  |  |  |  | 5b43ae59-19a0-4b38-98c5-ddd59a2c5427 |  | https://web.fulcrumapp.com/photos/view?photos=5b43ae59-19a0-4b38-98c5-ddd59a2c5427 | Steel | Channel Bracket | Corrosion-Surface
b09d2431-1299-49eb-923c-1e83d09fbad6 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 18:28:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 428 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26967 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 428, 9 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Condition unchanged. | [5 empty] | 98d7dabe-a6f1-4937-b69f-81be12a7aaab |  | https://web.fulcrumapp.com/photos/view?photos=98d7dabe-a6f1-4937-b69f-81be12a7aaab | Concrete | Grout Hole | Leaks |  | Not reinforcement
07a93389-60b1-4241-acfc-82361914813e | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 10:51:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 429 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69319 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 429, 1 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition, inactive leak during the inspection | no |  |  |  |  | 0fc50b1c-e51e-4c8a-84e1-f92c65d464c6 |  | https://web.fulcrumapp.com/photos/view?photos=0fc50b1c-e51e-4c8a-84e1-f92c65d464c6 | Concrete | Grout Hole | Leaks |  | Not reinforcement
7f834adf-fdf2-465e-ac11-4732bde6e4a4 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 429 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93641 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 429, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
5f829997-5db5-450d-b519-4bc9e8215be6 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:14:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 429 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93642 |  | 8516 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 16/08/2023 |  | 24/10/2024 | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 429, 5 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. Duplicate of defect 93641. Marked as repair verified to manage duplicate defects LC 10/10/24 |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Delimited/Drummy grout still present along the circumferential joint | no |  |  |  |  | 25214c4f-6488-4d7f-912c-fc1cd8ecba84 |  | https://web.fulcrumapp.com/photos/view?photos=25214c4f-6488-4d7f-912c-fc1cd8ecba84 | Concrete | Circular Connection,Circular Joint | Drummy
bf4c8ad5-6111-4bbf-9990-b9e81d759e37 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 429 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36698 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 429, 7 o'clock. Segment bolted joint (radial joint). | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Cost impact associated with unplanned maintenance and downtime. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Radial Joint | Drummy |  | Not reinforcement
0f37e5a4-50b7-4004-8d83-3e07ab0f55e3 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:19:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 430 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 69320 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.158 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 430, 10 to 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 1 - Surface Corrosion |  | Steel channel support bracket has Level 1 - Surface Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged, minor surface rusting | no |  |  |  |  | 28fc4ac9-1be8-49ee-8779-3553fcf9b32e,85109a2b-90ba-4729-a184-201249508a75 | , | https://web.fulcrumapp.com/photos/view?photos=28fc4ac9-1be8-49ee-8779-3553fcf9b32e%2C85109a2b-90ba-4729-a184-201249508a75 | Steel | Channel Bracket | Corrosion-Surface
b49299b4-1640-4ef0-9520-a848a51ff542 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 10:44:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 430 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 69321 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.1597 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 430, 2 & 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 5% coverage. Steel channel support bracket bolts have Level 1 - Surface Corrosion. |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 5% coverage. Steel channel support bracket bolts have Level 1 - Surface Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still appears to have minor surface corrosion | no |  |  |  |  | 8992c7ce-c1df-4fb7-bf75-928392b286e4,39e6754e-0abb-498a-973c-3051fa529d58 | , | https://web.fulcrumapp.com/photos/view?photos=8992c7ce-c1df-4fb7-bf75-928392b286e4%2C39e6754e-0abb-498a-973c-3051fa529d58 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
686bb978-3d1f-4e5d-8656-076e1acc0d31 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:22:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 430 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36699 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.4985 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 430, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket bolts have Level 2 - Medium Low Corrosion. |  | Steel channel support bracket bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Condition unchanged | [5 empty] | 78b89563-2e13-4b08-ac59-eb2f40043710 |  | https://web.fulcrumapp.com/photos/view?photos=78b89563-2e13-4b08-ac59-eb2f40043710 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
29e3eb1d-7384-4c61-8865-4540140f8031 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 | -20.3218 | 118.5854 | POINT (118.585351 -20.3217883) | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 430 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69322 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 22/12/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 430, 9 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Engineering Repair Methodology Required Competent Supervisor | [11 empty] | Concrete | Grout Hole,Reinforcement | Leaks
86064f74-33e4-430b-9e22-b60b86916b48 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:17:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 431 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36700 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 431, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 9ba8e3d4-0fd8-4479-a24e-15bc65946d77 |  | https://web.fulcrumapp.com/photos/view?photos=9ba8e3d4-0fd8-4479-a24e-15bc65946d77 | Concrete | Grout Hole | Leaks |  | Not reinforcement
2a6d14c8-6668-4908-9094-53a814bcf708 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:23:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 431 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 83994 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 431, 4 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
7003588f-b4d9-4ca9-80f8-2fda0a0e6a6b | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:17:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 432 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69323 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 432, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | dea3f957-19b6-4009-afcf-589f3956e28c |  | https://web.fulcrumapp.com/photos/view?photos=dea3f957-19b6-4009-afcf-589f3956e28c | Concrete | Grout Hole | Leaks |  | Not reinforcement
7c17bfbd-04a0-460c-95d7-b50342462227 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:24:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 432 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 83999 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.3385 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 432, 3 o'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion up 25% coverage. |  | Steel channel support bracket has Level 2 Minor Corrosion up 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | No change in the condition of the steel channel appears to have minor surface corrosion | no |  |  |  |  | ace10c50-4461-4f98-815f-95060ff76644 |  | https://web.fulcrumapp.com/photos/view?photos=ace10c50-4461-4f98-815f-95060ff76644 | Steel | Channel Bracket | Corrosion-Surface
8baa84f1-2e8a-48e8-8c1c-c27a5b4c199c | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:19:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 433 | 0 | Grout Injection Hole | Grout Injection Hole |  | 69324 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 22/12/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 433, 1 & 3 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Engineering Repair Methodology Required Competent Supervisor | KP |  | The grout injection hole had a inactive leak at the time of inspection | no |  |  |  |  | 1d390412-0a8d-434e-abe1-e4765c09ec8c |  | https://web.fulcrumapp.com/photos/view?photos=1d390412-0a8d-434e-abe1-e4765c09ec8c | Concrete | Grout Hole | Leaks |  | Not reinforcement
ca8ddc7b-1ab5-46f5-9341-8eff7eed9557 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:17:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 434 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27230 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 434, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion. Channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 2 corrosion. Channel anchor bolts have Level 2 corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | In the same condition, severely corroded steel channel as well as bolt | yes |  |  |  |  | 352ec64c-7946-441d-8ecd-70b7675991c3 |  | https://web.fulcrumapp.com/photos/view?photos=352ec64c-7946-441d-8ecd-70b7675991c3 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
65dc3620-a78e-4606-83a0-b39c48c8d881 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:08:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 436 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69326 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 436, 1 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | The grouting hole had inactive leak at the time of inspection | no |  |  |  |  | 12b6cdcf-ca85-41bb-bc00-8322cea3884e |  | https://web.fulcrumapp.com/photos/view?photos=12b6cdcf-ca85-41bb-bc00-8322cea3884e | Concrete | Grout Hole | Leaks |  | Not reinforcement
ad5710bc-b7ac-4cc8-9597-2f5f10f45275 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:52:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 436 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69325 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 436, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 2c09c93d-19ed-4b5b-9c24-4ee36971476e |  | https://web.fulcrumapp.com/photos/view?photos=2c09c93d-19ed-4b5b-9c24-4ee36971476e | Concrete | Grout Hole | Leaks |  | Not reinforcement
3b73f31c-bbbc-4d49-95ee-076dcab67c7c | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:05:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 437 | 0 | Grout Injection Hole | Grout Injection Hole |  | 69327 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 437, 1 & 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | The grout injection hole had inactive leak at the time of inspection | no |  |  |  |  | 99b5b6a7-27aa-48f5-8e1e-c480031c6ec6 |  | https://web.fulcrumapp.com/photos/view?photos=99b5b6a7-27aa-48f5-8e1e-c480031c6ec6 | Concrete | Grout Hole | Leaks |  | Not reinforcement
0817c966-866f-4390-bc9e-4c6f4cbc8411 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:04:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 437 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93645 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 437, 5 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Drummy / delimitated grouting along the circumferential joint | no |  |  |  |  | 705b5099-ed18-48e3-95da-f500be2420eb |  | https://web.fulcrumapp.com/photos/view?photos=705b5099-ed18-48e3-95da-f500be2420eb | Concrete | Circular Connection,Circular Joint | Drummy
7775ed09-7dba-4d01-98b7-255fb362af17 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 438 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101786 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 438, 4 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
17e88561-693a-4b09-a136-8de9637e41ab | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 438 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101787 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 438, 7 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Safety |  | Shear failure of bolt Safety | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
d859f765-dbe0-45f5-b5d7-5b2a9066230c | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 438 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69328 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 438, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Grout Hole,Reinforcement | Leaks
0840b277-67b8-44cc-989a-e9624b97cd04 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:47:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 439 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36704 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 439, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 813fe6cb-4286-4679-b527-8db42aabe9f1 |  | https://web.fulcrumapp.com/photos/view?photos=813fe6cb-4286-4679-b527-8db42aabe9f1 | Concrete | Grout Hole | Leaks |  | Not reinforcement
19c32f5f-a22e-4cde-b75a-271b916b9e27 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:45:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 440 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36705 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 440, 11 o'clock, Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 200 mm x 300 mm. |  | Concrete shell segment has drummy concrete over an area of 200 mm x 300 mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), downgraded to P3 and defect to be monitored. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Drummy patch repair, condition unchanged | no |  |  |  |  | e28ae72f-5d43-497b-bc2a-9f9f7b358611 |  | https://web.fulcrumapp.com/photos/view?photos=e28ae72f-5d43-497b-bc2a-9f9f7b358611 | Concrete |  | Drummy |  | Not reinforcement
61bbcff3-52ef-4dd9-a631-7b35cab8823c | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:44:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 440 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36707 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 440, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 164413a0-1c92-4f80-8466-25b465481a41 |  | https://web.fulcrumapp.com/photos/view?photos=164413a0-1c92-4f80-8466-25b465481a41 | Concrete | Grout Hole | Leaks |  | Not reinforcement
9c9a6a2c-12c2-4b17-bb68-c0cb6835584c | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:53:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 440 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36708 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 440, 12 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition, an inactive leak at the time of inspection | no |  |  |  |  | 34afd2f0-ddd3-465f-ac1c-2d7a70bf63a9 |  | https://web.fulcrumapp.com/photos/view?photos=34afd2f0-ddd3-465f-ac1c-2d7a70bf63a9 | Concrete | Grout Hole | Leaks |  | Not reinforcement
09138a22-45f5-42fa-8cc1-863f1339221c | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 440 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 101774 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 45553.5786 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 440, 2 & 3 O'clock, Steel Channel Bracket and Anchor Bolts |  |  |  | Steel channel support bracket has Level 1 corrosion at 3 o'clock and wide spread protective coating breakdown. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion at 3 o'clock and wide spread protective coating breakdown. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [15 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Coating Failure
342f51b3-5643-49af-a1dc-cf68c60888a8 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:52:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 440 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 101773 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 45553.5765 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 440, 2 & 3 O'clock, Steel Channel Bracket and Anchor Bolts |  |  |  | Steel channel support bracket has Level 1 corrosion at 3 o'clock and wide spread protective coating breakdown. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion at 3 o'clock and wide spread protective coating breakdown. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | No change in condition. Still surface corrosion | no |  |  |  |  | 75af7aae-c502-441c-92e1-d67c9c7fedcd |  | https://web.fulcrumapp.com/photos/view?photos=75af7aae-c502-441c-92e1-d67c9c7fedcd | Steel | Channel Bracket,Channel Bracket-Bolt | Coating Failure,Corrosion-Surface
d1e3d468-d840-46d4-8a8d-e82424a8658c | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 440 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69329 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 440, 9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Grout Hole,Reinforcement | Leaks
5a78c1c1-be5a-46c8-86e6-815751bb84e1 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:38:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 441 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69330 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 441, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 72358497-fc9f-43de-823c-03acdbfe2210 |  | https://web.fulcrumapp.com/photos/view?photos=72358497-fc9f-43de-823c-03acdbfe2210 | Concrete | Grout Hole | Leaks |  | Not reinforcement
54d53344-9937-464d-9b1c-5c7f5d896bef | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 16:41:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 442 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36711 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.5263 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 442, 1 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket bolts have Level 2 Corrosion. |  | Steel channel support bracket bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe). |  | Loss of minor services (NOT water pipe). |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Steel channel bolts and channel have level 2 rust. Condition worsening. | [5 empty] | 0e3a6a32-a0be-48c1-9b82-b585bd9e4807,b4d7e17d-7fc6-4087-840f-d0601f373f51,027903ef-920d-4aec-b460-e5980c9086d4 | ,, | https://web.fulcrumapp.com/photos/view?photos=0e3a6a32-a0be-48c1-9b82-b585bd9e4807%2Cb4d7e17d-7fc6-4087-840f-d0601f373f51%2C027903ef-920d-4aec-b460-e5980c9086d4 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
14275da8-cc85-4b02-b483-b5aa817cb2df | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 16:09:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 442 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84006 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 442, 1 o'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | On-Line | No | - | - | Condition Monitoring Competent Supervisor | RT |  | Cannot check | [8 empty] | Concrete |  | Leaks
87017e97-3627-4d1a-9a31-7de25b3ae899 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:07:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 442 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 26968 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 442, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel bracket has Level 2 Corrosion up to 25% coverage. |  | Steel channel bracket has Level 2 Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Condition unchanged | [5 empty] | 20559346-16cd-41b5-8ef5-24fc4e803ab2 |  | https://web.fulcrumapp.com/photos/view?photos=20559346-16cd-41b5-8ef5-24fc4e803ab2 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
eec244b9-7d69-4f50-9bd3-0359040a8dfa | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 18:06:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 442 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36710 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.5221 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 442, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). |  | Channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Condition unchanged | [5 empty] | 3faa703e-5962-40dd-afbd-a98f8f3ea23c |  | https://web.fulcrumapp.com/photos/view?photos=3faa703e-5962-40dd-afbd-a98f8f3ea23c | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
50793fe8-4642-424a-a076-2e217c9db7e9 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 16:12:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 442 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69331 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 442, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 484d3744-1977-43e2-bb71-bfbfef16e306 |  | https://web.fulcrumapp.com/photos/view?photos=484d3744-1977-43e2-bb71-bfbfef16e306 | Concrete | Grout Hole | Leaks |  | Not reinforcement
9d009ce1-0ae3-405b-8481-f79bf9408973 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:33:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 444 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36712 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 444, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 359df2a3-92bb-48d2-866b-c8eae7f04199 |  | https://web.fulcrumapp.com/photos/view?photos=359df2a3-92bb-48d2-866b-c8eae7f04199 | Concrete | Grout Hole | Leaks |  | Not reinforcement
457ab898-0787-42e8-ad14-cda7ebc7c021 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 444 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69332 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 444, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Grout Hole | Leaks |  | Not reinforcement
95d90d02-b802-46df-8a77-2450873e07cb | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:33:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 445 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69334 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Carbonation Induced |  | Carbonation Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 445, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | ca4dee69-2a64-4328-b421-6043bf0efe17 |  | https://web.fulcrumapp.com/photos/view?photos=ca4dee69-2a64-4328-b421-6043bf0efe17 | Concrete | Grout Hole | Leaks |  | Not reinforcement
57961ab1-58f0-402e-b049-daab8b7ef2ac | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:55:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 445 | 3 | Grout Injection Hole | Grout Injection Hole |  | 69333 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 445, 3 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | e5c97f74-f17a-4303-a225-946b643d7d2a |  | https://web.fulcrumapp.com/photos/view?photos=e5c97f74-f17a-4303-a225-946b643d7d2a | Concrete | Grout Hole | Leaks |  | Not reinforcement
5c1df270-7a0c-472d-a320-8328d729b42f | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:31:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 446 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69335 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.1867 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 446, 10 to 12 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 1 Low Corrosion. |  | Channel anchor bolts have Level 1 Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Some surface rusting. Condition unchanged | no |  |  |  |  | 8cb92e46-5044-4299-902b-f4dc6f83ad11 |  | https://web.fulcrumapp.com/photos/view?photos=8cb92e46-5044-4299-902b-f4dc6f83ad11 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
76546889-a9f5-49ba-8438-e9ee84a8cd13 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 | -20.3741 | 118.6339 | POINT (118.6338517 -20.3741124) | 2025-05-27 20:13:18 AEST | 2025-07-28 23:22:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 446 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27529 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 446, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket bolts have Level 2 Corrosion. Steel channel support bracket has Level 2 corrosion. |  | Steel channel support bracket bolts have Level 2 Corrosion. Steel channel support bracket has Level 2 corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Rusted channel support bolt. | no |  |  |  |  | 3eb68b36-814c-42f7-8244-ccc54651dcc0 |  | https://web.fulcrumapp.com/photos/view?photos=3eb68b36-814c-42f7-8244-ccc54651dcc0 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
83b1cd8f-ca41-4290-98d9-ba5901f48693 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 446 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93646 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 446, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
955ecded-e6fb-431a-be76-88c292c4df29 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:58:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 446 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69336 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 446, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged. Condition 3 | [5 empty] | 69da2f8f-afcb-4513-af83-07809e05048e |  | https://web.fulcrumapp.com/photos/view?photos=69da2f8f-afcb-4513-af83-07809e05048e | Concrete | Grout Hole | Leaks |  | Not reinforcement
af393a8a-c006-4781-a35b-e6925894370f | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:29:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 447 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69337 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 447, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 9c37613e-be8e-445b-88ae-acbb0bab188a |  | https://web.fulcrumapp.com/photos/view?photos=9c37613e-be8e-445b-88ae-acbb0bab188a | Concrete | Grout Hole | Leaks |  | Not reinforcement
26c4fcdb-fd7b-493b-bce8-2254ce5cbca3 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:42:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 447 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69338 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 447, 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 45a24335-7159-44e1-ba1b-6934c41be7c1 |  | https://web.fulcrumapp.com/photos/view?photos=45a24335-7159-44e1-ba1b-6934c41be7c1 | Concrete | Grout Hole | Leaks |  | Not reinforcement
0c9014c3-5961-4030-8b3e-aa3eaccec0d5 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:38:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 448 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69339 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.1951 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 448, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 1 Low Corrosion. |  | Channel anchor bolts have Level 1 Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Condition unchanged | [5 empty] | 8784b29c-e599-4fd5-b024-42aedab86745 |  | https://web.fulcrumapp.com/photos/view?photos=8784b29c-e599-4fd5-b024-42aedab86745 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
ea0da559-25da-456a-b7a8-d3b3073351a0 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 448 | 0 | Grout Injection Hole | Grout Injection Hole |  | 36713 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 448, 8 &9 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | [11 empty] | Concrete | Grout Hole,Reinforcement | Leaks
258d6808-5a00-40cc-9930-3a463d88d788 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 448 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69340 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 448, 9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Grout Hole,Reinforcement | Leaks
6d5a4809-a994-4559-8bcb-d2269f116527 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:25:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 449 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36714 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 449, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 8a451519-4025-447e-82c5-7a1aafa8e916 |  | https://web.fulcrumapp.com/photos/view?photos=8a451519-4025-447e-82c5-7a1aafa8e916 | Concrete | Grout Hole | Leaks |  | Not reinforcement
0424ca87-6d17-4168-b099-48678a9f3bd0 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 | -20.3742 | 118.6339 | POINT (118.6338764 -20.3741936) | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 449 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84009 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 449, 4 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
37ee35ed-1ede-4b5d-b20c-e9b91ab614ea | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 | -20.3217 | 118.5853 | POINT (118.585329 -20.3216695) | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 450-470 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101788 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Between Ring 450 & 470, 7 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
adaff8b0-e83f-40ea-9d0d-b7dced790478 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 13:26:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 450 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36715 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 450, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Condition unchanged at | no |  |  |  |  | 4e56c67e-48d0-4db8-87e7-8f399c763688 |  | https://web.fulcrumapp.com/photos/view?photos=4e56c67e-48d0-4db8-87e7-8f399c763688 | Concrete |  | Leaks |  | Not reinforcement
bad18804-790d-4ac6-ad19-1f5dcbf86870 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:27:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 450 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26969 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 450, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 25 % coverage. Channel anchor bolts have Level 2 Corrosion. |  | Steel channel support bracket has Level 2 Corrosion up to 25 % coverage. Channel anchor bolts have Level 2 Corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Steel channel and bolts where found to be corroded. | no |  |  |  |  | 702510d3-83fa-4d03-ba6e-44c025c1e9e5 |  | https://web.fulcrumapp.com/photos/view?photos=702510d3-83fa-4d03-ba6e-44c025c1e9e5 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
edf60464-b7be-46be-9c6f-796da90197c2 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 18 | -20.3741 | 118.6339 | POINT (118.633859 -20.3741321) | 2025-05-27 20:13:18 AEST | 2025-07-28 23:51:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 450 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69353 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 450, 9 o'clock, Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  |  | no | [7 empty] | Concrete | Grout Hole | Leaks |  | Not reinforcement
cb4e89e1-9783-48b8-9e4f-0318fa096580 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 |  |  |  | 2025-07-25 15:45:45 AEST | 2025-07-28 23:47:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 440 | 12 |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Drummy concrete patch repair along the radial joint | [5 empty] | c1dd7129-80ae-4051-bf39-3e4788b2a08e |  | https://web.fulcrumapp.com/photos/view?photos=c1dd7129-80ae-4051-bf39-3e4788b2a08e | Concrete | Radial Joint | Drummy
2614e761-dd66-4182-ae3e-2e7142691af3 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 | -20.3741 | 118.6336 | POINT (118.6335715 -20.3741234) | 2025-07-25 15:57:08 AEST | 2025-07-28 23:47:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 434 | 12 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drumminess in the patch repair along the circumferential joint | [5 empty] | 437aaf00-59a7-4921-ab5e-6237654b5aba |  | https://web.fulcrumapp.com/photos/view?photos=437aaf00-59a7-4921-ab5e-6237654b5aba | Concrete | Circular Connection,Circular Joint | Drummy
11d22181-5f81-45dc-aa15-adef4fb075b4 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 |  |  |  | 2025-07-25 16:02:20 AEST | 2025-07-28 23:47:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 432 | 11 |  |  | Cathodic protection cable disbanded and circle joint | [56 empty] | KP |  | Cathodic protection cable disbanded and drummy patch repair along the radial joint | [5 empty] | 56e71430-af85-4878-8bf0-b5a299ec1230 |  | https://web.fulcrumapp.com/photos/view?photos=56e71430-af85-4878-8bf0-b5a299ec1230 | Concrete | Circular Joint,Radial Joint,Misc (Pipes/Cable Tray/etc) | Drummy |  | Misc
9707856a-10f5-4aa1-ab09-37c06d1891d3 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 |  |  |  | 2025-07-25 16:39:56 AEST | 2025-07-28 23:27:44 AEST | 30011704-user5@smec.com | james.stone@smec.com | 422 | 10 o’clock and 11 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Steel channel has corrosion/ rusting and had one bolt is corroded and one bolt at 10 o’clock is missing | [5 empty] | 08b7b6b5-7fe2-48d2-ace2-0cb86e7ca759 |  | https://web.fulcrumapp.com/photos/view?photos=08b7b6b5-7fe2-48d2-ace2-0cb86e7ca759 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
ca8d8e53-fa41-4fff-84c4-0e95dd61c187 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 | -20.3742 | 118.6338 | POINT (118.6337669 -20.374184) | 2025-07-26 13:23:51 AEST | 2025-07-28 23:28:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 424 | 6 o’clock |  | Steel Channel Bracket | [32 empty] | Ring 424 | [24 empty] | KP |  | The base plate is heavily corroding as well as the bolts are heavily corroded / shear off. Structural steel supporting the walkway is corroded at the bottom.High priority. |  | yes |  |  |  | 7d8a631e-e0b4-4f61-86e6-d34a7e6cd01f,85dcee09-8c76-4df5-9c78-5384e5ff5743,e92af3a2-c6ec-4716-ab3b-2a7f13e3323b | ,, | https://web.fulcrumapp.com/photos/view?photos=7d8a631e-e0b4-4f61-86e6-d34a7e6cd01f%2C85dcee09-8c76-4df5-9c78-5384e5ff5743%2Ce92af3a2-c6ec-4716-ab3b-2a7f13e3323b | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support not Channel Bracket
616a0f49-69cf-46a8-9d7b-006f910a63d9 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 |  |  |  | 2025-07-26 13:50:42 AEST | 2025-07-26 19:40:57 AEST | 30011704-user5@smec.com | james.stone@smec.com | 428 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate is corroding and the bolts are heavily corroded / shear off. Structural steel supporting the walkway is corroded at the bottom.High priority. |  | yes |  |  |  | a76ad4f2-0a17-4c38-8f9b-81692987fe69,c767d336-2bb9-4c43-bfdc-ebbb3833497a,deebdb38-cb32-48cb-87b0-e3756b7b4f47,2af1c6b5-961e-4cb3-99a5-1c14429aba85 | ,,, | https://web.fulcrumapp.com/photos/view?photos=a76ad4f2-0a17-4c38-8f9b-81692987fe69%2Cc767d336-2bb9-4c43-bfdc-ebbb3833497a%2Cdeebdb38-cb32-48cb-87b0-e3756b7b4f47%2C2af1c6b5-961e-4cb3-99a5-1c14429aba85 | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support
4f91f717-f03e-435e-a359-e2b91545b13a | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 |  |  |  | 2025-07-26 15:44:23 AEST | 2025-07-26 19:41:03 AEST | 30011704-user5@smec.com | james.stone@smec.com | 432 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate and the bolts are corroded . Structural steel supporting the walkway is corroded at the bottom. priority. |  | yes |  |  |  | 1825b3dd-e939-4775-9ac4-d9cddc090043,64581fde-65a0-4d5f-98e8-fa10cf05a241 | , | https://web.fulcrumapp.com/photos/view?photos=1825b3dd-e939-4775-9ac4-d9cddc090043%2C64581fde-65a0-4d5f-98e8-fa10cf05a241 | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support
8245700b-c6c7-4e8e-9e3e-b6c7c0407f7d | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 |  |  |  | 2025-07-26 16:16:53 AEST | 2025-07-26 19:41:10 AEST | 30011704-user5@smec.com | james.stone@smec.com | 436 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate is corroding and the bolts are heavily corroded. Structural steel supporting the walkway is corroded at the bottom.High priority. |  | yes |  |  |  | 48ae783f-6969-4887-bf71-b919e59a23e3,a977163b-879e-457f-9d40-b45027aaf727,476523af-42ee-4a2f-a2ca-045444ece15d | ,, | https://web.fulcrumapp.com/photos/view?photos=48ae783f-6969-4887-bf71-b919e59a23e3%2Ca977163b-879e-457f-9d40-b45027aaf727%2C476523af-42ee-4a2f-a2ca-045444ece15d | Steel | Centre Support,Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support and Walkway Support not Channel Bracket
92d5d7d2-e9b5-4e7f-a3cc-d61705bb4014 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 |  |  |  | 2025-07-26 16:54:46 AEST | 2025-07-26 19:41:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 444 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Bottom slab has 0.6mm cracks and base plate is corroding as well as the bolts are heavily corroded. Structural steel supporting the walkway is corroded at the bottom.High priority. | [5 empty] | b416df54-3819-4efb-9457-8f70a275514b,dd4818bd-ae6e-4dcf-9421-d05863538b4b,70675b50-0cf8-49ef-a461-ac9ebd5c8f5b | ,, | https://web.fulcrumapp.com/photos/view?photos=b416df54-3819-4efb-9457-8f70a275514b%2Cdd4818bd-ae6e-4dcf-9421-d05863538b4b%2C70675b50-0cf8-49ef-a461-ac9ebd5c8f5b | Steel | Centre Support,Walkway Support | Crack |  | Centre Support and walkway Support not Channel Bracket
d2c31662-8298-4afd-bdc0-8439c60bd149 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 12 |  |  |  | 2025-07-26 17:02:37 AEST | 2025-07-26 19:41:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 448 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Bottom slab has 0.6mm cracks and base plate is corroding as well as the bolts are heavily corroded with one of the bolt has shear off. Structural steel supporting the walkway is corroded from bottom.High priority. |  | yes |  |  |  | b939b70f-fd3c-4483-921f-f683e5384aba,255dae64-8dc6-490d-82a1-48dc2c5230ec,755fd25a-2360-423d-b6a6-48e0ad56d72f,398acbfc-f785-4dfb-8942-dd817580b75e | ,,, | https://web.fulcrumapp.com/photos/view?photos=b939b70f-fd3c-4483-921f-f683e5384aba%2C255dae64-8dc6-490d-82a1-48dc2c5230ec%2C755fd25a-2360-423d-b6a6-48e0ad56d72f%2C398acbfc-f785-4dfb-8942-dd817580b75e | Steel | Centre Support,Walkway Support | Crack |  | Centre Support and walkway Support not Channel Bracket
7b393d18-c01a-4fee-aa67-0d31a19dde44 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 14 | -20.3218 | 118.5853 | POINT (118.5852785 -20.3217541) | 2025-07-26 12:15:20 AEST | 2025-07-27 08:39:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 422 | 8 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess close to circular joint. 150x200mm. Low priority | [5 empty] | 61f8e10a-b4ce-4540-9a32-c4ec9e424992 |  | https://web.fulcrumapp.com/photos/view?photos=61f8e10a-b4ce-4540-9a32-c4ec9e424992 | Concrete | Circular Connection,Circular Joint | Drummy
6e6b7b64-98ae-481b-b770-538a9ceca646 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 14 | -20.3211 | 118.5842 | POINT (118.5842474 -20.3211204) | 2025-07-26 12:29:44 AEST | 2025-07-28 15:40:40 AEST | 30011704-user5@smec.com | james.stone@smec.com | 424 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Delamination and drumminess close to circular joint. Size 100x200mm. Low priority | [5 empty] | dd1ee598-ca6c-46e7-9e2a-46eb63adebb0 |  | https://web.fulcrumapp.com/photos/view?photos=dd1ee598-ca6c-46e7-9e2a-46eb63adebb0 | Concrete | Circular Connection,Circular Joint | Drummy
699a3c7a-bb54-4a38-9b49-37ae1a348a73 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 14 | -20.3205 | 118.5839 | POINT (118.5839023 -20.3204688) | 2025-07-26 12:33:36 AEST | 2025-07-28 15:40:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 424 | 7 O'Clock |  |  | structure footing | [56 empty] | RT |  | Active rust and 1x bolt has failed. May lead to structural failure and dislocation of the footing. Low priority. | [5 empty] | 7c1981df-e564-4b37-8526-e1e65206fc1f |  | https://web.fulcrumapp.com/photos/view?photos=7c1981df-e564-4b37-8526-e1e65206fc1f | Steel | Conveyor Support | Corrosion-Surface |  | Conveyor Support
59df3ab6-2554-47b8-9e03-89ad0b1cd5be | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 14 | -20.3207 | 118.5831 | POINT (118.5830918 -20.3207041) | 2025-07-26 12:58:15 AEST | 2025-07-27 08:40:21 AEST | 30011704-user5@smec.com | james.stone@smec.com | 428 | 7 O'Clock |  |  | structure footing | [56 empty] | RT |  | Severe rust on footing, will reduce the lateral load bearing capacity of the structural section in-between ring 424-432. Priority medium | [5 empty] | 39d49b3e-b949-4552-8461-a9c353bb59ac |  | https://web.fulcrumapp.com/photos/view?photos=39d49b3e-b949-4552-8461-a9c353bb59ac | Steel | Conveyor Support | Corrosion-Surface |  | Conveyor Support
b05af62b-40e5-4275-8b9e-32be71306cb0 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 14 | -20.3197 | 118.5818 | POINT (118.5818347 -20.3196907) | 2025-07-26 13:27:10 AEST | 2025-07-28 23:29:12 AEST | 30011704-user5@smec.com | james.stone@smec.com | 438 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Grout delamination / drummy concrete over an area of 200x500mm. Low priority. | [5 empty] | 1cf114fa-2685-4b00-b5db-c99f376d1d97 |  | https://web.fulcrumapp.com/photos/view?photos=1cf114fa-2685-4b00-b5db-c99f376d1d97 | Concrete |  | Drummy
29992ab5-2dc7-4818-a00d-a0d5e27651df | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 14 | -20.319 | 118.5809 | POINT (118.5809042 -20.3189921) | 2025-07-26 13:50:33 AEST | 2025-07-28 23:47:33 AEST | 30011704-user5@smec.com | james.stone@smec.com | 440 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Grout Delamination / Drummy Concrete at circular joint over an area 100mm x 300mm. | [5 empty] | 1f4d22c1-7e1b-4541-8efa-3a952cd7b2e4 |  | https://web.fulcrumapp.com/photos/view?photos=1f4d22c1-7e1b-4541-8efa-3a952cd7b2e4 | Concrete | Circular Connection,Circular Joint | Drummy
09763a8f-bbac-4fca-ba6b-9efd1a843f07 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 13 | -20.3182 | 118.58 | POINT (118.5800034 -20.3182446) | 2025-07-26 15:52:00 AEST | 2025-07-27 08:41:11 AEST | 30011704-user5@smec.com | james.stone@smec.com | 446 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess close to circular joint. Size 100x300mm. Priority low |  | yes |  |  |  | 2d11b452-3aab-4049-937a-3540f574abb3 |  | https://web.fulcrumapp.com/photos/view?photos=2d11b452-3aab-4049-937a-3540f574abb3 | Concrete | Circular Connection,Circular Joint | Drummy
03baf5e1-4df8-4d98-b98c-58ae71bfbd4c | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 13 | -20.3173 | 118.5796 | POINT (118.5795658 -20.3173317) | 2025-07-26 16:10:21 AEST | 2025-07-28 09:42:19 AEST | 30011704-user5@smec.com | james.stone@smec.com | 450 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Delamination and drumminess close to circular joint. Size 150x300mm. Priority low | [5 empty] | e6aa7dcf-1f52-4fb2-85ed-51e94fb15868 |  | https://web.fulcrumapp.com/photos/view?photos=e6aa7dcf-1f52-4fb2-85ed-51e94fb15868 | Concrete | Circular Connection,Circular Joint | Drummy
f2887f8b-b4c0-4e49-a924-5a980db07ffe | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 7 | -20.3742 | 118.634 | POINT (118.6339565 -20.3741768) | 2025-07-27 17:45:28 AEST | 2025-07-28 23:28:45 AEST | 30011704-user5@smec.com | james.stone@smec.com | 440 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy patch repair along the circumferential joint | [5 empty] | 0de411dd-4f72-4724-bb92-c6bb9cdff46f |  | https://web.fulcrumapp.com/photos/view?photos=0de411dd-4f72-4724-bb92-c6bb9cdff46f | Concrete | Circular Connection,Circular Joint | Drummy
e8cfb9ef-304b-4ab8-8d0a-d277956450e5 | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 8 | -20.3742 | 118.6339 | POINT (118.6339446 -20.3741822) | 2025-07-27 17:46:45 AEST | 2025-07-28 23:43:36 AEST | 30011704-user5@smec.com | james.stone@smec.com | 446 | 2 |  | Channel Anchor Bolts | [57 empty] | RT |  | Rusted channel anchor bolt | [5 empty] | 8e622677-f933-4d47-9781-420335499848 |  | https://web.fulcrumapp.com/photos/view?photos=8e622677-f933-4d47-9781-420335499848 | Steel | Channel Bracket-Bolt
298e71c7-34f5-41c7-a4dc-bafdb4d5071e | fb048eb7-416c-4027-acd6-08f65efde129 | fb048eb7-416c-4027-acd6-08f65efde129 | 6 | -20.3742 | 118.6339 | POINT (118.6339318 -20.374178) | 2025-07-28 10:56:49 AEST | 2025-07-28 23:28:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 428 | 1 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Delimitated /Drummy grout work 100x200 mm along the circumferential joint | [5 empty] | 327308a6-de1b-4b1e-847e-877fe0dd3323 |  | https://web.fulcrumapp.com/photos/view?photos=327308a6-de1b-4b1e-847e-877fe0dd3323 | Concrete | Circular Connection,Circular Joint | Drummy
860e7718-8365-473c-9623-e29741d15690 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:15:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 451 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69341 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 451, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | RT |  | Dry leakage chloride induced. No changes | [5 empty] | dd770812-69c7-4da0-8b05-04690a3b001f,0724d918-150a-4720-b904-80ab6f1c3d01 | , | https://web.fulcrumapp.com/photos/view?photos=dd770812-69c7-4da0-8b05-04690a3b001f%2C0724d918-150a-4720-b904-80ab6f1c3d01 | Concrete | Grout Hole | Leaks |  | Not reinforcement
5b9d4c1d-0240-475c-9220-c4e4d5b09126 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:15:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 451 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84011 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 451, 4 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Drummy concrete. Condition unchanged | [5 empty] | 259ed654-b18e-4c26-a035-066debfbfd90 |  | https://web.fulcrumapp.com/photos/view?photos=259ed654-b18e-4c26-a035-066debfbfd90 | Concrete | Circular Joint | Drummy
ab051c45-4364-4337-b4e8-9793134b9f02 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:15:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 452 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69342 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 452, 11 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 9b8f53d2-05cd-45a8-b420-d8c26e7fd882 |  | https://web.fulcrumapp.com/photos/view?photos=9b8f53d2-05cd-45a8-b420-d8c26e7fd882 | Concrete | Grout Hole | Leaks |  | Not reinforcement
ae8f93f9-f2d7-4e00-a33b-9e770379f5b1 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 15:37:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 452 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 69344 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.2656 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 452, 2 & 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Channel anchor bolts have Level 1 - Low Corrosion |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Channel anchor bolts have Level 1 - Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Condition unchanged | [5 empty] | 1b5d64b7-8923-432f-ad11-4f3ddd5ad548 |  | https://web.fulcrumapp.com/photos/view?photos=1b5d64b7-8923-432f-ad11-4f3ddd5ad548 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
4852e18a-12d1-437a-85c2-2a62e865d064 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:31:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 452 | 0 | Grout Injection Hole | Grout Injection Hole |  | 36716 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 452, 8 & 9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Leak is still active and affecting the structural footings. Condition 4 | [5 empty] | 248d8c38-c1af-4c84-bf7a-54e82e85b361,43783ba2-71e2-4348-ab38-c881d57b970e | , | https://web.fulcrumapp.com/photos/view?photos=248d8c38-c1af-4c84-bf7a-54e82e85b361%2C43783ba2-71e2-4348-ab38-c881d57b970e | Concrete | Grout Hole | Leaks |  | Not reinforcement
402e9f1f-2fea-4b4a-86bf-b96d7cf5be3c | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 | -20.3217 | 118.5853 | POINT (118.5853316 -20.3216621) | 2025-05-27 20:13:18 AEST | 2025-07-28 12:16:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 453 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36717 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 453, 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | RT |  | Dry leakage chloride induced. No changes | [5 empty] | 7dfa6cb3-00ca-4d44-bbc5-109ea158ce7f,ac16d54a-30eb-435b-8b4b-e283d1306ec8 | , | https://web.fulcrumapp.com/photos/view?photos=7dfa6cb3-00ca-4d44-bbc5-109ea158ce7f%2Cac16d54a-30eb-435b-8b4b-e283d1306ec8 | Concrete | Grout Hole | Leaks |  | Not reinforcement
10433cfa-7e24-4540-962f-5e0530f51a68 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 14:48:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 453 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93647 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 453, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Grout delamination / Drummy concrete at circular joint over area 100mm x 200mm | [5 empty] | dcaabf6f-91f2-4576-a4ba-937651f8290e |  | https://web.fulcrumapp.com/photos/view?photos=dcaabf6f-91f2-4576-a4ba-937651f8290e | Concrete | Circular Connection,Circular Joint | Drummy
c12ed37f-7f90-40d6-babf-55745454bf05 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 14:49:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 453 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26970 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 453, 9 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage locally | Leaks through tunnel liner, leading to accelerated concrete damage locally |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Dry leak chloride induced | no |  |  |  |  | 61887f6d-eaa0-49a6-8214-69133a51bd2e |  | https://web.fulcrumapp.com/photos/view?photos=61887f6d-eaa0-49a6-8214-69133a51bd2e | Concrete | Grout Hole | Leaks |  | Not reinforcement
ab1cbeaf-404b-49ff-a0b6-c25329f0f56c | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:21:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 454 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84012 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 454, 1 o'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | On-Line | No | Scaffolding | - | Condition Monitoring Competent Supervisor | RT |  | Dry leak and chloride induced | [5 empty] | f48b0893-ec7e-4ae2-9dc0-26febfbe2151 |  | https://web.fulcrumapp.com/photos/view?photos=f48b0893-ec7e-4ae2-9dc0-26febfbe2151 | Concrete | Channel Bracket | Leaks |  | Channel Bracket
2bf7f44a-afee-4c0c-9cab-f42c4b7fffdc | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 15:59:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 454 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84014 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 454, 4 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | Walkway | Excavation | Standard Repair Detail Competent Supervisor | RT |  | Repair patch is still drummy. Size 120x200mm. Priority low. | [5 empty] | fed08f97-527e-486f-8f42-c0065de808e1 |  | https://web.fulcrumapp.com/photos/view?photos=fed08f97-527e-486f-8f42-c0065de808e1 | Concrete | Circular Joint | Drummy
2a3ab78b-956e-4f55-bcd2-ffd2aba91956 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 | -20.3217 | 118.5853 | POINT (118.5853379 -20.3216518) | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 454 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93648 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 454, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
a5052931-3033-47b3-9107-e32cacc35834 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:31:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 455 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69345 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 455, 1 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | RT |  | No changes | [5 empty] | 1a6cb328-8095-42b8-997d-df9fd05cfad8 |  | https://web.fulcrumapp.com/photos/view?photos=1a6cb328-8095-42b8-997d-df9fd05cfad8 | Concrete | Grout Hole | Leaks |  | Not reinforcement
179d491d-31ef-48ec-b8dc-b9205ebdbf54 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:06:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 455 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69346 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 455, 11 o'clock. Concrete Shell Segment - Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | yes |  |  |  |  | 47969ef8-8a05-4692-87f6-0fb5cb7b63dc |  | https://web.fulcrumapp.com/photos/view?photos=47969ef8-8a05-4692-87f6-0fb5cb7b63dc | Concrete | Grout Hole | Leaks |  | Not reinforcement
be58997a-5c17-4f40-895c-73b41e508f84 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:08:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 455 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36718 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 455, 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 59335249-849f-4964-95ad-148353fbf953 |  | https://web.fulcrumapp.com/photos/view?photos=59335249-849f-4964-95ad-148353fbf953 | Concrete | Grout Hole | Leaks |  | Not reinforcement
7767dfcd-f003-4392-862f-9cad7959c413 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:26:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 455 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93649 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 455, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 23deb664-aaa3-408a-a268-66999ce3ce69 |  | https://web.fulcrumapp.com/photos/view?photos=23deb664-aaa3-408a-a268-66999ce3ce69 | Concrete | Circular Joint | Drummy
eb5d45f5-898a-45f3-a7db-704b75b2c438 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:07:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 456 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69347 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 456, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | 1cc43000-0d59-442e-bf4d-85b7c6b952f0 |  | https://web.fulcrumapp.com/photos/view?photos=1cc43000-0d59-442e-bf4d-85b7c6b952f0 | Concrete | Grout Hole | Leaks |  | Not reinforcement
0bcba375-89cc-474b-84a7-f6f1459476d0 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:12:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 456 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84015 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.3765 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 456, 3 o'Clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is loose. |  | One channel anchor bolt is loose. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | RT |  | Condition unchanged | [5 empty] | bf6268be-33c1-4c77-9b4f-4797a57e01df |  | https://web.fulcrumapp.com/photos/view?photos=bf6268be-33c1-4c77-9b4f-4797a57e01df | Steel | Channel Bracket-Bolt | Loose
53d9b935-f028-4762-adbf-3873036ef829 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:26:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 456 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84016 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 456, 4 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Condition unchanged | [7 empty] | 0faa9f17-691a-4331-9290-4b6be0ec70a4 |  | https://web.fulcrumapp.com/photos/view?photos=0faa9f17-691a-4331-9290-4b6be0ec70a4 | Concrete | Circular Joint | Drummy
24dde0ab-25a9-4c90-bedb-e17958b3db2b | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:03:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 456 | 0 | Grout Injection Hole | Grout Injection Hole |  | 36719 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 456, 8 &9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Leak is still active with salt dripping onto the support structure below. Condition 5 | [5 empty] | 179eaf2d-e62f-489d-93be-4e78b5e791f5 |  | https://web.fulcrumapp.com/photos/view?photos=179eaf2d-e62f-489d-93be-4e78b5e791f5 | Concrete | Grout Hole | Leaks |  | Not reinforcement
16eeb9ff-b57e-4185-9351-7036c326631e | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:07:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 457 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69348 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 457, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole and inactive water leakage at the time of inspection | no |  |  |  |  | c5fbd4f8-79ee-43fc-99a5-84cbe2a763a1 |  | https://web.fulcrumapp.com/photos/view?photos=c5fbd4f8-79ee-43fc-99a5-84cbe2a763a1 | Concrete | Grout Hole | Leaks |  | Not reinforcement
09f53c0f-7c91-443b-ab29-892b29b7f104 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:34:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 457 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36721 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 457, 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | No changes | [5 empty] | 957e5668-5dad-402e-9738-34118714206f,57af3723-ea5b-4d4f-a397-76a87a057420 | , | https://web.fulcrumapp.com/photos/view?photos=957e5668-5dad-402e-9738-34118714206f%2C57af3723-ea5b-4d4f-a397-76a87a057420 | Concrete | Grout Hole | Leaks |  | Not reinforcement
c9204fd6-bf6d-4a71-aa9d-4c0a7ab968c5 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:30:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 457 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101789 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 457, 4 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | b0daa1ea-e579-46ac-bfb8-bb9834ae64f9 |  | https://web.fulcrumapp.com/photos/view?photos=b0daa1ea-e579-46ac-bfb8-bb9834ae64f9 | Concrete | Circular Joint | Drummy
3f69ff7d-f8ee-4c1f-8c23-5d8b561b0962 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 15:01:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 458 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27537 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 458, 10 to 12 & 1 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 2 corrosion. Channel support bracket has Level 2 corrosion. |  | Channel anchor bolts have Level 2 corrosion. Channel support bracket has Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged | no |  |  |  |  | d93e3b20-c89b-4aca-aeb9-76463c173138 |  | https://web.fulcrumapp.com/photos/view?photos=d93e3b20-c89b-4aca-aeb9-76463c173138 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
8ddd3cf7-ff2e-4c38-a326-f20283aeeea4 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:34:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 458 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84017 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 458, 4 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 664d8862-788e-4e02-8bba-7bf8f6b617db |  | https://web.fulcrumapp.com/photos/view?photos=664d8862-788e-4e02-8bba-7bf8f6b617db | Concrete | Circular Joint | Drummy
a1d12b7d-b088-4aaf-8ef8-e5e42a0045c7 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:11:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 458 | 9 | Grout Injection Hole | Grout Injection Hole |  | 69349 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 458, 9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Leak is still inactive. No changes | [5 empty] | a05dcb6a-1c0a-420e-ba8f-58f5a9ebd1d0,b8f14ff9-927c-43c7-b31e-87081de69ed9 | , | https://web.fulcrumapp.com/photos/view?photos=a05dcb6a-1c0a-420e-ba8f-58f5a9ebd1d0%2Cb8f14ff9-927c-43c7-b31e-87081de69ed9 | Concrete | Grout Hole | Leaks |  | Not reinforcement
da2b19e1-b5c6-4d06-b9c7-4514badddfbc | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:38:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 459 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36723 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Carbonation Induced |  | Carbonation Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 459, 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Dry, no signs of leaks at the time of inspection. Condition seems to have improved. | [5 empty] | f2f4764f-76a4-460d-b2b0-31d2a73cce64,9ff97dc2-44c9-4265-9ce5-c315737f966a | , | https://web.fulcrumapp.com/photos/view?photos=f2f4764f-76a4-460d-b2b0-31d2a73cce64%2C9ff97dc2-44c9-4265-9ce5-c315737f966a | Concrete | Grout Hole | Leaks |  | Not reinforcement
db691232-c13c-4209-a24f-096e910ac8bc | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:36:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 459 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93650 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 459, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 21d72e09-c076-4f76-a348-db2df81f01dc |  | https://web.fulcrumapp.com/photos/view?photos=21d72e09-c076-4f76-a348-db2df81f01dc | Concrete | Circular Joint | Drummy
0c34231e-4c84-4a08-b212-3fa0ebef0097 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:41:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 460 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69351 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.2736 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 460, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 1 Low Corrosion. |  | Channel anchor bolts have Level 1 Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Surface rust only. | [5 empty] | fe53d948-c2a8-4824-8a14-9a0ad5941e8b |  | https://web.fulcrumapp.com/photos/view?photos=fe53d948-c2a8-4824-8a14-9a0ad5941e8b | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
dba5be0b-8c86-47b3-8181-d9200171e736 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 14:56:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 460 | 11 | Grout Injection Hole | Grout Injection Hole |  | 69350 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 460, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole had a patch repair | yes |  |  |  |  | 013aa420-2af4-4123-93ea-9c929e742e48 |  | https://web.fulcrumapp.com/photos/view?photos=013aa420-2af4-4123-93ea-9c929e742e48 | Concrete | Grout Hole | Leaks |  | Not reinforcement
b615b83e-a320-4d44-b0f8-6c8e16ebd9ec | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:25:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 460 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 69352 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.2746 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 460, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 50% coverage. Steel channel support bracket bolts have Level 2 Corrosion. |  | Steel channel support bracket has Level 2 Corrosion up to 50% coverage. Steel channel support bracket bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Condition unchanged. | [5 empty] | 55d3cff4-c36a-456e-a35a-22afd20e9829 |  | https://web.fulcrumapp.com/photos/view?photos=55d3cff4-c36a-456e-a35a-22afd20e9829 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
6d0d1a70-d2e2-4857-a1f7-a9f140169f78 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 16:58:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 461 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27342 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 461, 7 o'clock, Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete Shell Segment has drummy concrete 200mm x 300mm. |  | Concrete Shell Segment has drummy concrete 200mm x 300mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), downgraded to P3 and defect to be monitored. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | ,condition unchanged | [5 empty] | d6143658-c87f-44d6-a493-af31f7374fb6 |  | https://web.fulcrumapp.com/photos/view?photos=d6143658-c87f-44d6-a493-af31f7374fb6 | Concrete | Circular Joint,Radial Joint | Drummy |  | Circular Joint and Radial Joint. Not reinforcement
21e21b7a-a998-4f66-8c39-7d87f068bebd | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 14:42:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 462 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 69356 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.2803 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 462, 10 to 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Steel channel support bracket bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Steel channel support bracket bolts have Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged | no |  |  |  |  | 5e4f6d73-1193-4f47-bbc8-bd53e850933e |  | https://web.fulcrumapp.com/photos/view?photos=5e4f6d73-1193-4f47-bbc8-bd53e850933e | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
756c306c-1703-4c78-b6e4-505faf8fbf58 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 | -20.3217 | 118.5853 | POINT (118.5853084 -20.3216507) | 2025-05-27 20:13:18 AEST | 2025-07-28 16:24:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 462 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36724 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 462, 11 o'clock. Concrete Shell Segment - Segment bolted joint (circle joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150 mm x 150 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150 mm x 150 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged. Circular joint had grout delamination / drummy grout over an area of 150mm x 150mm. | [5 empty] | 31027021-87f0-4abe-a8a5-f5e8d02f8f85,1570e264-2c78-4fe7-b029-6b1005ae5651,9b6d55f3-f93a-4d33-b2ab-b5aa5ba75ac2 | ,, | https://web.fulcrumapp.com/photos/view?photos=31027021-87f0-4abe-a8a5-f5e8d02f8f85%2C1570e264-2c78-4fe7-b029-6b1005ae5651%2C9b6d55f3-f93a-4d33-b2ab-b5aa5ba75ac2 | Concrete | Circular Connection,Circular Joint | Drummy |  | Not reinforcement
568214da-440f-4df5-9c4b-a19bf203d731 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 | -20.3216 | 118.5853 | POINT (118.5853161 -20.3216335) | 2025-05-27 20:13:18 AEST | 2025-07-28 14:58:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 462 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84019 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.3827 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 462, 3 o'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion up 25% coverage. |  | Steel channel support bracket has Level 2 Minor Corrosion up 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | RT |  | Presence of surface rust. Condition unchanged. | [5 empty] | 4b169867-4d01-4164-b98c-193e01dac1dd |  | https://web.fulcrumapp.com/photos/view?photos=4b169867-4d01-4164-b98c-193e01dac1dd | Steel | Channel Bracket | Corrosion-Surface
a4d2ccb6-cd4e-43fd-886f-2bfc9e679fde | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:56:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 462 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84020 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 462, 4 o'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Cathodic Protection continuity cable severed. |  | Cathodic Protection continuity cable severed. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), upgraded to P2. | Not Specified | Priority: P2 |  |  |  | Reinstate Cathodic Protection Continuity Cable. | Cathodic Protection Technician | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | RT |  | CP is functional | [5 empty] | 355774db-4dc5-4d24-a099-9922baac9c1c |  | https://web.fulcrumapp.com/photos/view?photos=355774db-4dc5-4d24-a099-9922baac9c1c | Concrete
d32fc221-1533-4901-a4ec-9d59e8948884 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 462 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69355 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 22/12/2021 |  | 17/02/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 462, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints |  | Grout Delamination / debonding at circle segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Remediate grout as per BHP Standards and specifications | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
e95a2d47-d0cb-4d20-a822-9f2d9bc8c87d | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:36:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 463 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36725 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 463, 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition, it was inactive leak at the time of inspection | no |  |  |  |  | baa5a0c6-9228-44ae-8fae-42aff739daf8 |  | https://web.fulcrumapp.com/photos/view?photos=baa5a0c6-9228-44ae-8fae-42aff739daf8 | Concrete | Grout Hole | Leaks |  | Not reinforcement
85b7cb45-4302-4f34-af32-949f29ef2ffd | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 17:12:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 463 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27343 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 463, 7 o'clock, Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete Shell Segment has drummy concrete over an area of 200mm x 400mm. |  | Concrete Shell Segment has drummy concrete over an area of 200mm x 400mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), downgraded to P3 and defect to be monitored. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | b89b8006-24c1-4964-99ee-8e9115a25e69 |  | https://web.fulcrumapp.com/photos/view?photos=b89b8006-24c1-4964-99ee-8e9115a25e69 | Concrete |  | Drummy |  | Not reinforcement
dfd1f5de-e462-44d9-b7f2-b7636804708f | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:21:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 464 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26971 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 464, 1 to 3 o'clock. Hydrophilic Joint Seal (Circle Joint) | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Inactive at time of inspection. |  | Hydrophilic Joint Seal (Circle Joint) has Leak - Inactive at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint | Leaks |  | Not reinforcement
d4992409-ac3d-4176-bf1a-e2811b05f190 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:32:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 464 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27540 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 464, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts are missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). |  | Channel anchor bolts are missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still missing bolt and the steel channel has corrosion | no |  |  |  |  | cef02811-87fc-4608-a436-d368d3c94d8b |  | https://web.fulcrumapp.com/photos/view?photos=cef02811-87fc-4608-a436-d368d3c94d8b | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
5b5700f5-9522-4671-b44f-476517b42498 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:18:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 464 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36727 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 464, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | The leak is inactive. The seal is working successfully. | [5 empty] | 119eb1d8-8973-4e71-b429-2d5674f2b71b,c3efe76e-c1be-4542-bd58-cb8466a3d923 | , | https://web.fulcrumapp.com/photos/view?photos=119eb1d8-8973-4e71-b429-2d5674f2b71b%2Cc3efe76e-c1be-4542-bd58-cb8466a3d923 | Concrete | Grout Hole | Leaks |  | Not reinforcement
2f088e88-b2e7-4daa-9fad-290fe0d85831 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 465 | 0 | Grout Injection Hole | Grout Injection Hole |  | 69354 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 465, 1 & 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Grout Hole | Leaks |  | Not reinforcement
b25c16c0-68a0-4b54-8c20-dcd48c88dbad | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:52:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 465 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101790 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 465, 4 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 4e4efdde-3593-4b68-8209-1b96c84e2190 |  | https://web.fulcrumapp.com/photos/view?photos=4e4efdde-3593-4b68-8209-1b96c84e2190 | Concrete | Circular Joint | Drummy
1403bcd3-fd59-437b-8ca5-450f1256af10 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 14:28:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 466 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26972 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 466, 10 & 11 & 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support brackets have Level 2 Corrosion up to 25% coverage. Steel anchor bolt has Level 1 corrosion. One anchor bolt is missing at 11 o'clock. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support brackets have Level 2 Corrosion up to 25% coverage. Steel anchor bolt has Level 1 corrosion. One anchor bolt is missing at 11 o'clock. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged | no |  |  |  |  | 762e32fb-db78-4573-8d8f-d1a07ae1723b |  | https://web.fulcrumapp.com/photos/view?photos=762e32fb-db78-4573-8d8f-d1a07ae1723b | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
3b4ca8f1-dcbf-497c-af7a-c0dc55929370 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 14:27:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 466 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36732 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 466, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  |  | no |  |  |  |  | ec7c5741-8078-4f3d-88bb-f52128037956 |  | https://web.fulcrumapp.com/photos/view?photos=ec7c5741-8078-4f3d-88bb-f52128037956 | Concrete | Reinforcement | Leaks
7bad49c0-6406-4978-972e-e3bd51592128 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:25:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 466 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84022 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.3873 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 466, 3 o'clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion up 25% coverage. |  | Steel channel support bracket has Level 2 Minor Corrosion up 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line | [6 empty] | No change, steel channel and bolt has surface corrosion | no |  |  |  |  | 7161adfd-e1bd-4abb-85e2-674f3f9b512c,324f1c61-782d-4f87-b541-d772057f6c36 | , | https://web.fulcrumapp.com/photos/view?photos=7161adfd-e1bd-4abb-85e2-674f3f9b512c%2C324f1c61-782d-4f87-b541-d772057f6c36 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
21154751-1d0a-40f4-bfe0-3bd0bb02374f | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:56:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 466 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36726 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 466, 4 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 300 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 300 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Condition unchanged. | [5 empty] | 22504241-1ba8-482c-83b1-ae2354248539 |  | https://web.fulcrumapp.com/photos/view?photos=22504241-1ba8-482c-83b1-ae2354248539 | Concrete | Circular Joint | Drummy |  | Not reinforcement
fe3e467f-ff06-4d20-9d80-469598b2b33f | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:02:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 466 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84024 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 466, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Component should be "Segmented Bolted Joint (Radial Joint)". Adopted default consequence Health & Safety - Level 2. | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | The concrete patch is drummy and undergoing delamination. Size 200x180mm. Medium priority. | [5 empty] | 9d4ea948-20cc-4bd7-a658-fa8a2bd22a84 |  | https://web.fulcrumapp.com/photos/view?photos=9d4ea948-20cc-4bd7-a658-fa8a2bd22a84 | Concrete | Radial Joint | Drummy |  | Only Radial
d862abc0-e618-4359-af72-a9a4f5bd40d4 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 14:22:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 467 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36735 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 467, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Conditions unchanged, observed to be in same condition as previously reported. | no |  |  |  |  | ff75ad8e-e39c-4778-a804-c6061f8e90b7 |  | https://web.fulcrumapp.com/photos/view?photos=ff75ad8e-e39c-4778-a804-c6061f8e90b7 | Concrete | Grout Hole | Leaks |  | Not reinforcement
4507c201-f3dc-4566-8cff-be9ebf44c7bb | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:03:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 467 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36733 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 467, 4 o'clock, Segment Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 8bdc9a9d-a4a8-4f52-9d86-cf25bee0f24b |  | https://web.fulcrumapp.com/photos/view?photos=8bdc9a9d-a4a8-4f52-9d86-cf25bee0f24b | Concrete | Circular Joint | Drummy |  | Not reinforcement
e424334b-f061-45dd-bf00-d6c9474c70ff | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 17:21:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 467 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36734 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 467, 8 o'clock, Segment Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 1246dfaa-2ce2-4165-9fcd-840777887e00 |  | https://web.fulcrumapp.com/photos/view?photos=1246dfaa-2ce2-4165-9fcd-840777887e00 | Concrete | Circular Joint | Drummy |  | Not reinforcement
e422a37e-ad1c-4aaf-8a09-83b86ae8bf51 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 14:19:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 468 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84025 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 468, 12 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | No | Walkway | - | Condition Monitoring Competent Supervisor | KP |  | Drummy concrete patch repair. Condition same as the last time. | no |  |  |  |  | cbe386b0-a5c5-48b7-b963-1e3a0327c144 |  | https://web.fulcrumapp.com/photos/view?photos=cbe386b0-a5c5-48b7-b963-1e3a0327c144 | Concrete | Radial Joint | Drummy
55cb69c9-614e-4c2f-87a3-06ef57bb2b39 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:13:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 468 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27251 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 468, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 2 corrosion. Steel channel bracket has Level 2 corrosion at 50% coverage. |  | Channel anchor bolts have Level 2 corrosion. Steel channel bracket has Level 2 corrosion at 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still the steel channel and bolt are heavily corroded | no |  |  |  |  | f906ca50-f994-4866-91af-e6d649b63a00 |  | https://web.fulcrumapp.com/photos/view?photos=f906ca50-f994-4866-91af-e6d649b63a00 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
64dcb100-d2f6-4b10-adf3-748e80079a59 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:08:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 468 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36736 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 468, 4 o'clock, Segment Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Delamination and drummy concrete. Size 120x150mm. Medium priority | [5 empty] | c84b0661-399f-466a-b984-23c2ffb5acb9 |  | https://web.fulcrumapp.com/photos/view?photos=c84b0661-399f-466a-b984-23c2ffb5acb9 | Concrete | Circular Joint | Drummy |  | Not reinforcement
59a7ec40-2f5e-4eb5-b219-fb088f536a15 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 | -20.3217 | 118.5853 | POINT (118.5853325 -20.3216769) | 2025-05-27 20:13:18 AEST | 2025-07-28 13:26:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 469 | 0 | Grout Injection Hole | Grout Injection Hole |  | 69357 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 469, 1 & 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Leaks inactive. Chloride induced. No changes. | [5 empty] | 70a48b55-fc75-458d-8803-c950c80b7314,6a79b2ef-3112-421b-b00a-84a57102a1a4 | , | https://web.fulcrumapp.com/photos/view?photos=70a48b55-fc75-458d-8803-c950c80b7314%2C6a79b2ef-3112-421b-b00a-84a57102a1a4 | Concrete | Grout Hole | Leaks |  | Not reinforcement
84dcb651-6dea-4ba1-81df-4b7a9b663edc | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:14:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 469 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101791 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 469, 4 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition Unchanged. | [5 empty] | c51acd90-8cdb-44ac-82d5-f9efcb45b852 |  | https://web.fulcrumapp.com/photos/view?photos=c51acd90-8cdb-44ac-82d5-f9efcb45b852 | Concrete | Circular Joint | Drummy
9e084e40-e3e0-4314-95bd-411c49363264 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:18:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 470 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84026 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 470, 4 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | Walkway | Excavation | Standard Repair Detail Competent Supervisor | Rt |  | Condition unchanged | [5 empty] | 06cd1e1a-fcda-4991-95fa-837e7b66abd6 |  | https://web.fulcrumapp.com/photos/view?photos=06cd1e1a-fcda-4991-95fa-837e7b66abd6 | Concrete | Circular Joint | Drummy
91a825e8-3fa3-4398-acc1-ebb795e0875c | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 12:46:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 470 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36737 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 470, 9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition exacerbated with presence of drumminess size 200x200mm. Condition 4 | [5 empty] | 28487f4c-f3b0-4fe8-b549-fae83db169fb |  | https://web.fulcrumapp.com/photos/view?photos=28487f4c-f3b0-4fe8-b549-fae83db169fb | Concrete | Grout Hole | Drummy,Leaks |  | Not reinforcement
38b323ca-7e99-4e28-82a1-7fa77bbd5271 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 17:01:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 471 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27255 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 471, 2 o'clock, Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout Injection hole has Leak - Active at time of inspection. |  | Grout Injection hole has Leak - Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Very Rare Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | No change in condition, it still has an active leak | no |  |  |  |  | 3a52e56a-af1c-4c98-9913-8c36ff716e20,3c2e15cb-7a21-4d53-a4b0-0f89d7f11183 | , | https://web.fulcrumapp.com/photos/view?photos=3a52e56a-af1c-4c98-9913-8c36ff716e20%2C3c2e15cb-7a21-4d53-a4b0-0f89d7f11183 | Concrete | Grout Hole | Leaks
7230a998-a600-42be-8d73-7f4481cc29f3 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:44:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 471 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101792 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 471, 7 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Circular joint had grout delamination with drummy concrete over an area of 100mm x 100mm | [5 empty] | b4e9d5da-8d15-4a48-bcf7-34d846c4cff1 |  | https://web.fulcrumapp.com/photos/view?photos=b4e9d5da-8d15-4a48-bcf7-34d846c4cff1 | Concrete | Circular Connection,Circular Joint | Drummy
4e25165d-2711-4a88-92d6-2a82e267d157 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:58:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 473 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26973 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 473, 1 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | Grout injection hole has mild water leak on the surface | no |  |  |  |  | ad71f826-588f-467c-9d37-2b015f3a7b3c |  | https://web.fulcrumapp.com/photos/view?photos=ad71f826-588f-467c-9d37-2b015f3a7b3c | Concrete | Grout Hole | Leaks |  | Not reinforcement
5b953764-09ec-43ca-aa4b-ee70c4f2ce19 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 | -20.3216 | 118.5853 | POINT (118.5853287 -20.321621) | 2025-05-27 20:13:18 AEST | 2025-07-25 12:36:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 473 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36738 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 473, 11 o'clock, Segment Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400 mm x 300 mm. Concrete spalling was observed with level 2 corrosion on reinforcement. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400 mm x 300 mm. Concrete spalling was observed with level 2 corrosion on reinforcement. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | Condition change as reinforcements are corroding and Drumminess in concrete is spreading | yes |  |  |  |  | 6c7e43fc-a773-4c31-9098-86d80fbe1d22 |  | https://web.fulcrumapp.com/photos/view?photos=6c7e43fc-a773-4c31-9098-86d80fbe1d22 | Concrete | Circular Joint | Drummy,Surface Damage |  | Not reinforcement
33ea0a6e-afba-45db-814c-de365c0c9a29 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 12:31:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 474 | 10 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26974 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 474, 10 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 25% coverage. Missing 1 anchor bolt on channel bracket support. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket has Level 2 Corrosion up to 25% coverage. Missing 1 anchor bolt on channel bracket support. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged. | no |  |  |  |  | b290646a-32fb-41db-a49f-b0b04968e26a,0133f008-c71f-4717-8c05-9b534e3230ff | , | https://web.fulcrumapp.com/photos/view?photos=b290646a-32fb-41db-a49f-b0b04968e26a%2C0133f008-c71f-4717-8c05-9b534e3230ff | Concrete,Steel | Channel Bracket-Bolt | Missing |  | Only bolt
5258f2fd-39f4-4fe4-ad0e-eff0a21dae34 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:50:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 474 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69359 |  | 6512 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Repair Verified | 22/12/2021 |  | 17/02/2023 | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 474, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts are missing. |  | Channel anchor bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Safety Risk to personnel | Priority: P3 |  |  |  | Replace missing and refasten loose anchor bolts as per original approved design. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | - | Maintenance Repair Competent Supervisor | KP |  | No change, steel channel is corroding and missing bolt. | no |  |  |  |  | b6417a66-9618-4d3d-a3eb-ae3bb5eab02b,7e260434-6db1-4bbc-a77e-bd7edcb62605 | , | https://web.fulcrumapp.com/photos/view?photos=b6417a66-9618-4d3d-a3eb-ae3bb5eab02b%2C7e260434-6db1-4bbc-a77e-bd7edcb62605 | Steel | Channel Bracket-Bolt | Missing |  | only bolt
59782b2c-209d-443f-a44b-d1efbd345b1c | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:44:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 475 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36739 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 475, 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | KP |  | The grout injection hole still had a active leak during inspection | no |  |  |  |  | 931d94fb-40f8-4399-adc0-85a9017af8e6,a609fef2-458f-4b97-bc7f-faeeee2abf14 | , | https://web.fulcrumapp.com/photos/view?photos=931d94fb-40f8-4399-adc0-85a9017af8e6%2Ca609fef2-458f-4b97-bc7f-faeeee2abf14 | Concrete | Grout Hole | Leaks |  | Not reinforcement
5a7bfefb-3b6c-40c3-8acc-1158c862bff1 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:42:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 475 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36740 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 475, 5 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at segment bolted joints over the size of 100mm x 100mm. |  | Grout Delamination / debonding at segment bolted joints over the size of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | The surface is still Drummy, no change in condition | no |  |  |  |  | 3b0b2cca-9ff3-4f90-b72c-2024138df82b |  | https://web.fulcrumapp.com/photos/view?photos=3b0b2cca-9ff3-4f90-b72c-2024138df82b | Concrete | Circular Joint | Drummy |  | Not reinforcement
90d67a7f-86af-46b8-bc87-0198a59b4ed3 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:38:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 476 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84027 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 476, 5 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition, still Drummy grout along the joint | no |  |  |  |  | e51ee7b1-9a07-471a-883e-721a55e901b2 |  | https://web.fulcrumapp.com/photos/view?photos=e51ee7b1-9a07-471a-883e-721a55e901b2 | Concrete | Circular Joint | Drummy
c14f3667-92e2-43d6-8aea-b0501a96870a | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:27:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 477 | 2 | Grout Injection Hole | Grout Injection Hole |  | 84030 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 477, 2 o'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | The grout injection has inactive water leak during inspection | yes |  |  |  |  | a8a85544-39fe-4aca-ba2d-636913b9887a |  | https://web.fulcrumapp.com/photos/view?photos=a8a85544-39fe-4aca-ba2d-636913b9887a | Concrete | Grout Hole | Leaks
fc5fb486-486f-4d98-97ca-10784f60b4ee | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:22:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 477 | 0 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93651 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 477, 8 & 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over two areas of 100mm x 200mm and 200mm x 400mm |  | Circle joint has grout Delamination / Drummy Grout over two areas of 100mm x 200mm and 200mm x 400mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Grout delamination / Drummy concrete at the circular joint has grown from initial area to 150mm x 200mm at 8 O’Clock and remains constant at 9 O’Clock | yes |  |  |  |  | cc554588-8343-4817-9ae5-17d24af56186,b125d5ff-1dab-4faf-abbb-b0162363a5e1 | , | https://web.fulcrumapp.com/photos/view?photos=cc554588-8343-4817-9ae5-17d24af56186%2Cb125d5ff-1dab-4faf-abbb-b0162363a5e1 | Concrete | Circular Connection,Circular Joint | Drummy
4b138bba-75fb-41ac-8a23-613187d351a7 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 12:20:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 478-479 | 11 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 101793 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Unknown | Unknown |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Between Ring 478 & 479, 11 O'clock, Hydrophilic Joint Seal (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Active leak at the Hydrophilic Joint Seal between Ring 478 and 479. |  | Active leak at the Hydrophilic Joint Seal between Ring 478 and 479. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | Inactive water leaks at the time of inspection | yes |  |  |  |  | 53c73bc7-3a89-4633-b115-cc009c3912e1 |  | https://web.fulcrumapp.com/photos/view?photos=53c73bc7-3a89-4633-b115-cc009c3912e1 | Concrete | Circular Joint | Leaks |  | Not reinforcement
db39dcaf-3b45-4d7c-b102-00dc52a32692 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:24:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 478 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84031 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4008 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 478, 3 o'Clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). |  | One channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | No change, steel channel is corroding and missing bolt. | no |  |  |  |  | dfa5571a-aefe-4fe0-bd3b-0493fe6184b4 |  | https://web.fulcrumapp.com/photos/view?photos=dfa5571a-aefe-4fe0-bd3b-0493fe6184b4 | Concrete,Steel | Channel Bracket-Bolt | Missing
be9d589c-938c-4e6e-9bf7-e65cff95ca82 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 | -20.3217 | 118.5854 | POINT (118.5853711 -20.3216688) | 2025-05-27 20:13:18 AEST | 2025-07-28 12:33:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 478 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84032 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 478, 5o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Double up of the existing defect | no |  |  |  |  | 49838c79-3be9-415b-a6fb-8700a20a1b6b |  | https://web.fulcrumapp.com/photos/view?photos=49838c79-3be9-415b-a6fb-8700a20a1b6b | Concrete | Circular Joint | Drummy
a016484f-0bf7-4b24-8340-ce3ee3397789 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:31:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 478 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36743 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 478, 5 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | Delimited/drummy grout still present along the circumferential joint | no |  |  |  |  | 6004a0b3-9b13-49e6-bf1e-67d276920298,30f7d58e-aa62-447d-8a69-d8db0a3e01bf | , | https://web.fulcrumapp.com/photos/view?photos=6004a0b3-9b13-49e6-bf1e-67d276920298%2C30f7d58e-aa62-447d-8a69-d8db0a3e01bf | Concrete | Circular Connection,Circular Joint | Drummy |  | Not reinforcement
9e28bd94-647b-4aa9-9e0a-5bd0707505e4 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:04:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 478 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 93318 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 478, 8 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Localised minor concrete spalling at the corner of the concrete shell over an area of 150mm x 150mm. |  | Localised minor concrete spalling at the corner of the concrete shell over an area of 150mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), upgraded to P3. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. | Not Specified | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS Inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | No signs of spalling, Drummy concrete at circular joint 150mm x 150mm. | yes |  |  |  |  | 377ef369-3a64-4f6f-a1d4-e99c0eea1351 |  | https://web.fulcrumapp.com/photos/view?photos=377ef369-3a64-4f6f-a1d4-e99c0eea1351 | Concrete | Circular Connection,Circular Joint,Corner | Drummy,Surface Damage
2eea81b9-cebf-412d-af17-b0dbfeecf76b | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 15:04:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 478 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26975 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 478,11 O'clock, Steel channel support bracket |  |  |  | Channel anchor bolts have Level 2 corrosion. Steel channel bracket has Level 3 corrosion at 5% coverage. Some channel anchor bolts are missing. One bolt is required per group of three bolt holes as per 117-C-00241/3 |  | Channel anchor bolts have Level 2 corrosion. Steel channel bracket has Level 3 corrosion at 5% coverage. Some channel anchor bolts are missing. One bolt is required per group of three bolt holes as per 117-C-00241/3 | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged , same as the last time | no |  |  |  |  | 3fc622ec-0438-4456-a170-c43c31abaf76 |  | https://web.fulcrumapp.com/photos/view?photos=3fc622ec-0438-4456-a170-c43c31abaf76 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
f6d4858c-7450-4e57-82e7-9f1ae14fa2d5 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 | -20.3216 | 118.5853 | POINT (118.5853033 -20.3216015) | 2025-05-27 20:13:18 AEST | 2025-07-28 09:23:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 478 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26976 |  | 6512 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 478,2 o'clock. Steel Channel Support Bracket | Rupture | Rupture |  | Steel Channel Support Bracket Not Secured at one end |  | Steel Channel Support Bracket Not Secured at one end | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of minor services (NOT water pipe) Risk of falling bracket and injury | Priority: P3 |  |  |  | Install Chem Set/ HILTI bolts for the missing bolts as per Original design / BHP Specifications. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | Scaffolding | Working at Heights, Confined Space, Hot Work, Excavation | Maintenance Repair Competent Supervisor | [11 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
14c37271-fd60-4e45-a88f-92db71cc4608 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 12:17:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 479 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84035 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 479, 11 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. Rust staining is observed in this area. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. Rust staining is observed in this area. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | Condition unchanged | no |  |  |  |  | b5a21a94-fc9a-40f1-aa6b-8e52abd13d80 |  | https://web.fulcrumapp.com/photos/view?photos=b5a21a94-fc9a-40f1-aa6b-8e52abd13d80 | Concrete | Circular Joint | Drummy
dc5ff31a-45ea-492c-a11a-a92b24be81da | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 12:16:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 479 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26978 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 479, 11 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Condition unchanged, inactive leak with chloride induced | no |  |  |  |  | 2fcba117-f548-4956-b221-3042e8de7b36 |  | https://web.fulcrumapp.com/photos/view?photos=2fcba117-f548-4956-b221-3042e8de7b36 | Concrete | Grout Hole | Leaks |  | Not reinforcement
dc6ac91a-51c2-444e-82cb-34e9263841a4 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 14:58:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 479 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36744 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 479, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of same size at 200 mm x 200 mm |  | Radial joint has Grout Delamination / Drummy Grout over two areas of same size at 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Dry leak chloride induced | [5 empty] | e831555e-b3d5-410e-834f-873d3129ea02 |  | https://web.fulcrumapp.com/photos/view?photos=e831555e-b3d5-410e-834f-873d3129ea02 | Concrete | Radial Joint | Drummy,Leaks |  | Not reinforcement
6e4d10da-22df-4bcb-b2cc-1f7b49a5cc9c | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 14:36:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 480 | 1 | Grout Injection Hole | Grout Injection Hole |  | 69360 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 480, 1 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition, still inactive leak | no |  |  |  |  | 039791e1-6032-4cde-a463-dc6294bdb898 |  | https://web.fulcrumapp.com/photos/view?photos=039791e1-6032-4cde-a463-dc6294bdb898 | Concrete | Grout Hole | Leaks |  | Not reinforcement
67e74e0f-fc51-40cd-80b2-d6f2d3e1adce | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 22 | -20.3179 | 118.5773 | POINT (118.5773218 -20.3178825) | 2025-07-25 12:05:05 AEST | 2025-07-29 15:17:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 480 | 10 O'Clock |  | Grout Injection Hole | [57 empty] | RT |  | Dry leak chloride induced in the grout injection hole. | [5 empty] | 804e1ca8-53b4-4f1b-b39c-ffaba885c1fa |  | https://web.fulcrumapp.com/photos/view?photos=804e1ca8-53b4-4f1b-b39c-ffaba885c1fa | Concrete | Grout Hole | Leaks
092cc59d-d2e9-4fc5-9a14-ff9558ff0199 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 22 | -20.3179 | 118.5773 | POINT (118.5773196 -20.317864) | 2025-07-25 12:24:44 AEST | 2025-07-29 15:18:19 AEST | 30011704-user5@smec.com | james.stone@smec.com | 477 | 8 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess close to circumferential joint size 150x150mm. Condition 3 |  | yes |  |  |  | 9c76ce49-54e2-481a-b17a-3b3f0f356ff7 |  | https://web.fulcrumapp.com/photos/view?photos=9c76ce49-54e2-481a-b17a-3b3f0f356ff7 | Concrete | Circular Connection,Circular Joint | Drummy
2da0a206-df4e-4c88-8300-c638cadd5b2d | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 22 | -20.3179 | 118.5773 | POINT (118.5773134 -20.317872) | 2025-07-25 12:27:08 AEST | 2025-07-29 15:21:55 AEST | 30011704-user5@smec.com | james.stone@smec.com | 477 | 9 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Grout delamination / Drummy concrete at circular joint over area 200mm x 200mm | [5 empty] | c5115bb4-1aa1-45c4-b70f-2299fe490790 |  | https://web.fulcrumapp.com/photos/view?photos=c5115bb4-1aa1-45c4-b70f-2299fe490790 | Concrete | Circular Connection,Circular Joint | Drummy
f31bbe3e-e9b1-4595-ae69-051606b98a0e | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 23 | -20.3179 | 118.5773 | POINT (118.5773179 -20.3178782) | 2025-07-25 12:22:48 AEST | 2025-07-27 08:46:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 478 | 12 O'Clock |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Hair line crack on the patch repair along radial joint | [5 empty] | 398e5dcf-ee69-43c8-bbbb-7a7bf3055ee6 |  | https://web.fulcrumapp.com/photos/view?photos=398e5dcf-ee69-43c8-bbbb-7a7bf3055ee6 | Concrete | Radial Joint | Crack
e1c9ae9d-731d-45ae-a9bc-1ba8d33355ce | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 23 | -20.3179 | 118.5773 | POINT (118.5773191 -20.3178746) | 2025-07-25 12:39:59 AEST | 2025-07-27 08:46:45 AEST | 30011704-user5@smec.com | james.stone@smec.com | 472 | 11 O'Clock |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Vertical hairline crack of 0.5mm between 2 radial joints | [5 empty] | 0f2c7bc8-244d-4028-8260-a0ea511e0697,99792ede-516e-4de7-ad88-45a952dd5a44 | , | https://web.fulcrumapp.com/photos/view?photos=0f2c7bc8-244d-4028-8260-a0ea511e0697%2C99792ede-516e-4de7-ad88-45a952dd5a44 | Concrete | Radial Joint | Crack
62ecc95f-1d9c-4908-8288-bf7848c37a06 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 23 | -20.3179 | 118.5773 | POINT (118.5773305 -20.3178999) | 2025-07-25 12:45:31 AEST | 2025-07-27 08:47:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 470 | 12 O'Clock |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Signs of chloride accumulation behind the radial patch repair. Need monitoring | [5 empty] | 932e0a89-31f7-4e77-b5a0-2a802fbb0b09 |  | https://web.fulcrumapp.com/photos/view?photos=932e0a89-31f7-4e77-b5a0-2a802fbb0b09 | Concrete | Radial Joint
d8b9dc7d-51a1-4dd8-be2a-b4333bc147b3 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 | -20.3179 | 118.5773 | POINT (118.5773159 -20.3178942) | 2025-07-25 14:12:47 AEST | 2025-07-27 08:47:46 AEST | 30011704-user5@smec.com | james.stone@smec.com | 468 | 10 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Dry seepage with salt built up and etched surface size 100x500mm. Condition 3 | [5 empty] | 6bba89f8-a2fb-4ea0-a0a2-f71c8e4ca502 |  | https://web.fulcrumapp.com/photos/view?photos=6bba89f8-a2fb-4ea0-a0a2-f71c8e4ca502 | Concrete | Grout Hole | Leaks |  | Grout Hole
95607d58-fb03-4486-986c-630549d4d830 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 | -20.3179 | 118.5773 | POINT (118.5773187 -20.3178974) | 2025-07-25 14:22:46 AEST | 2025-07-27 08:48:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 466 | 9 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Etched surface with slight drumminess. Size 500x1000mm. Condition 3 | [5 empty] | 1dc24f9c-ab97-4168-81f9-34bdbd81f887 |  | https://web.fulcrumapp.com/photos/view?photos=1dc24f9c-ab97-4168-81f9-34bdbd81f887 | Concrete | Grout Hole | Drummy |  | GRout Hole
06834bc5-d289-4dde-acb1-9c4c0826efc9 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 |  |  |  | 2025-07-25 14:30:14 AEST | 2025-07-25 14:32:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | 466 | 10 |  | Grout Injection Hole | [57 empty] | RT |  | Active leakage from grout injection hole. Water dripping onto support structure footing. Condition 4 | [5 empty] | f2a740e3-dab8-4809-bae4-5deed329e671,0fb62441-4433-47fb-bf03-f2b098096b4d | , | https://web.fulcrumapp.com/photos/view?photos=f2a740e3-dab8-4809-bae4-5deed329e671%2C0fb62441-4433-47fb-bf03-f2b098096b4d | Concrete | Grout Hole | Leaks
e30a7ee5-8226-4862-95f0-7d3145f06e1f | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 |  |  |  | 2025-07-25 14:32:36 AEST | 2025-07-25 14:34:21 AEST | 30011704-user5@smec.com | james.stone@smec.com | 464 | 7 |  |  | structure footing | [56 empty] | RT |  | Active rust on foot surface due to leakage from grout injection hole. Condition 4 | [5 empty] | dcbe8554-1628-43bf-8770-b482f35359d6 |  | https://web.fulcrumapp.com/photos/view?photos=dcbe8554-1628-43bf-8770-b482f35359d6 | Concrete | Grout Hole | Leaks
4c8539e4-eeaa-47f9-87ba-a8892801c343 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 |  |  |  | 2025-07-25 14:39:57 AEST | 2025-07-25 14:41:45 AEST | 30011704-user5@smec.com | james.stone@smec.com | 462 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Etched surface with slight drumminess 150x100mm. Condition 2 | [5 empty] | 7cfedf0e-1032-452c-9de5-d561792d2f27 |  | https://web.fulcrumapp.com/photos/view?photos=7cfedf0e-1032-452c-9de5-d561792d2f27 | Concrete | Grout Hole | Drummy |  | Grout hole
ba8860e0-9de6-4805-80f5-5130934dbba4 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 |  |  |  | 2025-07-25 14:53:14 AEST | 2025-07-25 14:55:12 AEST | 30011704-user5@smec.com | james.stone@smec.com | 457 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Patch work with drumminess. Size 100x150mm. Condition 3 | [5 empty] | 02fccd43-3639-4994-81bb-0729a1702819 |  | https://web.fulcrumapp.com/photos/view?photos=02fccd43-3639-4994-81bb-0729a1702819 | Concrete | Circular Joint | Drummy |  | Circular Joint
adb24e23-87d1-4ff7-b4e8-a9e8c4104536 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 |  |  |  | 2025-07-25 15:03:39 AEST | 2025-07-25 15:05:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 456 | 8 |  |  | Steel support structure | [56 empty] | RT |  | Rust on the structural footing. Condition 4 | [5 empty] | 65ec1eee-20c5-4aab-9a78-b51798c0589b,3f3afb71-a8c2-4c6f-aded-1778dc1e5ccb | , | https://web.fulcrumapp.com/photos/view?photos=65ec1eee-20c5-4aab-9a78-b51798c0589b%2C3f3afb71-a8c2-4c6f-aded-1778dc1e5ccb | Steel | Centre Support
934dc3db-7856-4e9c-9682-3d42930891ad | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 18 |  |  |  | 2025-07-26 17:12:19 AEST | 2025-07-26 19:39:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | 452 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate is corroding as well as the bolts have sheared off only one left. Structural steel supporting the walkway is heavily corroded from bottom.High priority. |  | yes |  |  |  | 6e1ac29a-1cab-4d76-a132-04631cc0b623,1684aebe-b097-49ca-91aa-0cd27e780702,d33f033e-4c43-42be-90f6-74c48c03f2cf | ,, | https://web.fulcrumapp.com/photos/view?photos=6e1ac29a-1cab-4d76-a132-04631cc0b623%2C1684aebe-b097-49ca-91aa-0cd27e780702%2Cd33f033e-4c43-42be-90f6-74c48c03f2cf | Steel | Centre Support,Centre Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Centre Support and Bolt not Channel Bracket
04a7dc54-bf20-4c2a-a094-c7dce66eb608 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 18 |  |  |  | 2025-07-26 17:20:40 AEST | 2025-07-26 19:39:33 AEST | 30011704-user5@smec.com | james.stone@smec.com | 456 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base plate is corroding as well as the bolts are heavily corroded with one of the bolt has shear off. Structural steel supporting the walkway is also heavily corroded from bottom.High priority. |  | yes |  |  |  | 836e96bb-3487-49ab-aa26-d4213c4e8089,11f139ed-88f7-4233-8251-1756375a1677,c17872de-4628-4324-8509-126ccdf31e7e | ,, | https://web.fulcrumapp.com/photos/view?photos=836e96bb-3487-49ab-aa26-d4213c4e8089%2C11f139ed-88f7-4233-8251-1756375a1677%2Cc17872de-4628-4324-8509-126ccdf31e7e | Steel | Centre Support,Centre Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Centre support and bolt not steel channel
3d97a772-955e-4835-9e13-6e873353852d | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 18 |  |  |  | 2025-07-26 17:30:41 AEST | 2025-07-26 19:39:39 AEST | 30011704-user5@smec.com | james.stone@smec.com | 460 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Bottom slab has multiple cracks and base plate is corroding as well as the bolts are heavily corroded with two of the bolt has shear off. Structural steel supporting the walkway is corroded from bottom.High priority. |  | yes |  |  |  | 5146fe41-6e6b-4ce9-8a05-6cf9048f8a2f,baf69f97-0fd6-4e58-82bd-e0f4f382e94e,568c5c0f-914d-4fe0-af79-20115eeca3f4 | ,, | https://web.fulcrumapp.com/photos/view?photos=5146fe41-6e6b-4ce9-8a05-6cf9048f8a2f%2Cbaf69f97-0fd6-4e58-82bd-e0f4f382e94e%2C568c5c0f-914d-4fe0-af79-20115eeca3f4 | Steel | Centre Support,Centre Support-Bolt | Crack |  | Centre support and bolt not steel channel
b6de03ba-9ed9-4ad6-8bb6-bca8f21bfb30 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 18 |  |  |  | 2025-07-26 17:38:50 AEST | 2025-07-26 19:39:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 464 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Bottom slab have multiple cracks of different size and base plate is corroding as well as the bolts are heavily corroded with two of the bolt have shear off. Structural steel supporting the walkway is corroded from the bottom.High priority. |  | yes |  |  |  | 6981a8ea-e9a4-4472-9466-478beb03c943,63147da8-3f5d-42d4-b693-b02f0a1f375e,217e77ed-9b62-41d7-b5ad-8410e3db039a | ,, | https://web.fulcrumapp.com/photos/view?photos=6981a8ea-e9a4-4472-9466-478beb03c943%2C63147da8-3f5d-42d4-b693-b02f0a1f375e%2C217e77ed-9b62-41d7-b5ad-8410e3db039a | Steel | Centre Support,Centre Support-Bolt | Crack |  | Centre support and bolt not steel channel
5156b82d-abf6-481d-b3bd-80af9cc8f334 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 18 |  |  |  | 2025-07-26 17:49:04 AEST | 2025-07-26 19:39:57 AEST | 30011704-user5@smec.com | james.stone@smec.com | 468 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | Bottom slab had drummy concrete and base plate has corroding as well as the bolts have shear off due to corroding.Structural steel supporting the walkway is corroded from bottom.High priority. |  | yes |  |  |  | 80e2ca71-58e6-472c-8b55-bd95740e0562,859cc310-c94f-4fe7-a1ea-d4b40be88bb6,ea4960f0-830c-4381-922e-57b58bbde1b0 | ,, | https://web.fulcrumapp.com/photos/view?photos=80e2ca71-58e6-472c-8b55-bd95740e0562%2C859cc310-c94f-4fe7-a1ea-d4b40be88bb6%2Cea4960f0-830c-4381-922e-57b58bbde1b0 | Concrete,Steel | Centre Support,Centre Support-Bolt | Drummy |  | Centre support and bolt not steel channel
626f55e7-8190-4eab-a382-89e76ccd4ea6 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 18 |  |  |  | 2025-07-26 17:55:04 AEST | 2025-07-26 19:40:03 AEST | 30011704-user5@smec.com | james.stone@smec.com | 476 | 6 o’clock | [59 empty] | KP |  | Bottom slab has cracked and base plate as well as the bolts are heavily corroded. Structural steel supporting the walkway is also heavily corroded from bottom.High priority. |  | yes |  |  |  | cf71b8b8-49a8-4c54-9e7c-91568ce968cf,88a5c1ea-f6ef-4f47-b8a7-abe60ff3427f,e0c762a0-b030-4ff7-a6f1-9643eaf807d5 | ,, | https://web.fulcrumapp.com/photos/view?photos=cf71b8b8-49a8-4c54-9e7c-91568ce968cf%2C88a5c1ea-f6ef-4f47-b8a7-abe60ff3427f%2Ce0c762a0-b030-4ff7-a6f1-9643eaf807d5 | Steel | Walkway Support,Centre Support | Crack |  | Walkway Support and centre support
72e81dee-ce7b-4ec7-bcc8-1b4bcb5f48d0 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 18 |  |  |  | 2025-07-26 18:01:58 AEST | 2025-07-26 19:40:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 480 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base slab has delimitated, but the steel structure appears have surface corrosion while bolts appear to be in fair condition, supporting structure to walkway had corroded from bottom , medium priority | [5 empty] | bead915a-332d-4373-9a32-2e0b42361d4c,6bb74619-a3f4-4f91-a2ef-a565d6ca0cf7 | , | https://web.fulcrumapp.com/photos/view?photos=bead915a-332d-4373-9a32-2e0b42361d4c%2C6bb74619-a3f4-4f91-a2ef-a565d6ca0cf7 | Steel | Centre Support,Centre Support-Bolt | Corrosion-Surface |  | Centre support and bolt not Steel Channel
ae8e4acf-8c3f-4c08-bc37-b46edf5f206e | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 | -20.3179 | 118.5773 | POINT (118.5773102 -20.317914) | 2025-07-25 15:10:36 AEST | 2025-07-27 08:52:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 455 | 10 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drummy concrete close to the circumferential joint. Size 100x130mm. Condition 3 | [5 empty] | 238ebbdd-80a1-48ee-bca9-3753df67d19d |  | https://web.fulcrumapp.com/photos/view?photos=238ebbdd-80a1-48ee-bca9-3753df67d19d | Concrete | Circular Connection,Circular Joint | Drummy
84e039ca-5c9b-4b7a-8eea-07581fe770d3 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 | -20.3178 | 118.5797 | POINT (118.5796991 -20.3178127) | 2025-07-25 15:17:16 AEST | 2025-07-27 08:55:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 454 | 10 O'Clcok |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drummy concrete at the circumferential Joint. Size 150x100mm. Low priority | [5 empty] | 09ae75ca-f2fe-4f4e-a028-3afe21908f66 |  | https://web.fulcrumapp.com/photos/view?photos=09ae75ca-f2fe-4f4e-a028-3afe21908f66 | Concrete | Circular Connection,Circular Joint | Drummy
519e94a8-fac7-41f3-b916-34720c576824 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 20 | -20.3179 | 118.5773 | POINT (118.5773274 -20.317898) | 2025-07-25 15:45:36 AEST | 2025-07-27 08:54:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 451 | 9 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drummy concrete close to circular joint. size 100x150mm. Low priority | [5 empty] | afb436cb-7ff2-4d6d-a068-47ccdb22ac7e |  | https://web.fulcrumapp.com/photos/view?photos=afb436cb-7ff2-4d6d-a068-47ccdb22ac7e | Concrete | Circular Connection,Circular Joint | Drummy
8c072594-ff50-4461-8998-b04128a2912a | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 21 | -20.3179 | 118.5773 | POINT (118.5773299 -20.3179015) | 2025-07-25 14:23:01 AEST | 2025-07-27 08:53:08 AEST | 30011704-user5@smec.com | james.stone@smec.com | 467 | 12 O'Clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy patch repair along the circumferential joint | [5 empty] | edb2750d-f952-4e88-847f-69c3aa0e7d1e,b3166f01-856d-4f79-b3a0-3d621ca1059d | , | https://web.fulcrumapp.com/photos/view?photos=edb2750d-f952-4e88-847f-69c3aa0e7d1e%2Cb3166f01-856d-4f79-b3a0-3d621ca1059d | Concrete | Circular Connection,Circular Joint | Drummy
167c6c49-6cf5-4624-a069-476d28d2fa30 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 21 | -20.3179 | 118.5773 | POINT (118.5773157 -20.3179252) | 2025-07-25 14:32:20 AEST | 2025-07-27 08:52:12 AEST | 30011704-user5@smec.com | james.stone@smec.com | 465 | 11 O'Clock |  | Grout Injection Hole | [57 empty] | KP |  | Chloride induced- with inactive water leakage during inspection from grout injection hole | [5 empty] | f9d7fee2-ed6e-459c-bd2a-f5ec310a3198 |  | https://web.fulcrumapp.com/photos/view?photos=f9d7fee2-ed6e-459c-bd2a-f5ec310a3198 | Concrete | Grout Hole | Leaks
04a32039-d363-4b29-a4af-d88d90dbf196 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 21 | -20.3179 | 118.5773 | POINT (118.5773167 -20.3179259) | 2025-07-25 14:35:21 AEST | 2025-07-27 08:51:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 465 | 10 O'Clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Hairline crack of 1.0mm was observed on patch repair along the circumferential joint | [5 empty] | 4844a1d2-b7d2-4744-b090-2ff76520a02f |  | https://web.fulcrumapp.com/photos/view?photos=4844a1d2-b7d2-4744-b090-2ff76520a02f | Concrete | Circular Connection,Circular Joint | Crack
718dac72-b397-42fb-9d0e-a4db851f4ca0 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 21 | -20.3179 | 118.5773 | POINT (118.5773215 -20.3179279) | 2025-07-25 14:50:55 AEST | 2025-07-27 08:51:17 AEST | 30011704-user5@smec.com | james.stone@smec.com | 462 | 10 O'Clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy patch repair along the circumferential joint | [5 empty] | cf7eb6b8-4152-4fe7-825f-e23c2a9ec1ae |  | https://web.fulcrumapp.com/photos/view?photos=cf7eb6b8-4152-4fe7-825f-e23c2a9ec1ae | Concrete | Circular Connection,Circular Joint | Drummy
5c2f6fdf-7d27-48fe-8d07-4924551b2968 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 21 | -20.3179 | 118.5773 | POINT (118.5773437 -20.3179198) | 2025-07-25 14:56:22 AEST | 2025-07-27 08:51:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 460 | 11 O'Clock |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Drummy patch repair along the radial joint. | [5 empty] | 926f8bf7-8020-4f9d-879e-4c6129cef329 |  | https://web.fulcrumapp.com/photos/view?photos=926f8bf7-8020-4f9d-879e-4c6129cef329 | Concrete | Radial Joint | Drummy
32e8969b-b183-42d5-bedb-46175b9b1942 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 21 | -20.3179 | 118.5773 | POINT (118.5773392 -20.3179197) | 2025-07-25 15:01:44 AEST | 2025-07-27 08:50:39 AEST | 30011704-user5@smec.com | james.stone@smec.com | 458 | 11 O'Clock |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Hairline crack was observed along the radial joint | [5 empty] | 1640ac65-c659-4f65-995c-8ddfbabeaf64 |  | https://web.fulcrumapp.com/photos/view?photos=1640ac65-c659-4f65-995c-8ddfbabeaf64 | Concrete | Radial Joint | Crack
4ef82560-8fd1-4948-beb2-160ff0ae0235 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 21 | -20.3179 | 118.5773 | POINT (118.5773182 -20.3179087) | 2025-07-25 15:12:41 AEST | 2025-07-27 08:50:29 AEST | 30011704-user5@smec.com | james.stone@smec.com | 454 | 11 O'Clock |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Patch repair along the radial joint has hairline cracks | [5 empty] | b622af8c-db31-4d9c-b0d0-670d5e96bcfd,f9c3be56-c92d-4137-b133-0afbe711ecd1 | , | https://web.fulcrumapp.com/photos/view?photos=b622af8c-db31-4d9c-b0d0-670d5e96bcfd%2Cf9c3be56-c92d-4137-b133-0afbe711ecd1 | Concrete | Radial Joint | Crack
ae557618-61dc-4605-bd74-b72f203a6826 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 19 | -20.3179 | 118.5773 | POINT (118.5773199 -20.3179057) | 2025-07-26 16:24:38 AEST | 2025-07-27 08:50:16 AEST | 30011704-user5@smec.com | james.stone@smec.com | 452 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess close to radial joints. Size 150x150mm. Priority low | [5 empty] | f613f015-102f-458e-9bac-15e8f423d77e |  | https://web.fulcrumapp.com/photos/view?photos=f613f015-102f-458e-9bac-15e8f423d77e | Concrete | Radial Joint | Drummy
9da268df-7654-42e3-bb69-05309b87629a | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 19 | -20.3179 | 118.5773 | POINT (118.5773217 -20.3179013) | 2025-07-26 17:01:00 AEST | 2025-07-27 08:49:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 461 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess close to circular joint. Size 150x250mm. Priority low | [5 empty] | 92f8a2cd-f0f0-4b48-b76d-1399bde00bf2 |  | https://web.fulcrumapp.com/photos/view?photos=92f8a2cd-f0f0-4b48-b76d-1399bde00bf2 | Concrete | Circular Connection,Circular Joint | Drummy
b62e02ab-c9d0-45f5-8032-4c0a35cd74ca | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 19 | -20.3179 | 118.5773 | POINT (118.5773086 -20.3179304) | 2025-07-26 17:06:59 AEST | 2025-07-27 08:49:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 462 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess close to circular joint. Size 150x250mm. Priority low | [5 empty] | 9e67f0a4-ebd6-4441-877a-b40404fc79c2 |  | https://web.fulcrumapp.com/photos/view?photos=9e67f0a4-ebd6-4441-877a-b40404fc79c2 | Concrete | Circular Connection,Circular Joint | Drummy
4d4dc2bd-95a7-4bea-ae57-edc35e0f152f | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 19 | -20.3179 | 118.5773 | POINT (118.5773132 -20.3179032) | 2025-07-26 17:42:28 AEST | 2025-07-27 08:49:12 AEST | 30011704-user5@smec.com | james.stone@smec.com | 477 | 8 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drummy concrete close to circular joint. Size 50x400mm. Low priority | [5 empty] | 46ec1188-8b59-45d3-ac32-5cfa80114aa4 |  | https://web.fulcrumapp.com/photos/view?photos=46ec1188-8b59-45d3-ac32-5cfa80114aa4 | Concrete | Circular Connection,Circular Joint | Drummy
2def551c-2d8d-4612-81b2-dccf95176dd8 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 19 | -20.3179 | 118.5773 | POINT (118.577305 -20.3178939) | 2025-07-26 17:51:50 AEST | 2025-07-27 08:48:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | 479 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drummy concrete close to circular joint. Size 100x500mm and 250x300mm. Low priority | [5 empty] | 355316b5-231e-4f00-9c36-e0c453c3f764,9bf5394a-ddfe-4e57-945c-1e2209a2bff9 | , | https://web.fulcrumapp.com/photos/view?photos=355316b5-231e-4f00-9c36-e0c453c3f764%2C9bf5394a-ddfe-4e57-945c-1e2209a2bff9 | Concrete | Circular Connection,Circular Joint | Drummy
6f28ebff-cd1d-4d57-86c4-38767192ecaf | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 19 | -20.3179 | 118.5773 | POINT (118.5773139 -20.3178967) | 2025-07-26 17:58:38 AEST | 2025-07-29 14:43:26 AEST | 30011704-user5@smec.com | james.stone@smec.com | 480 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Grout delamination / Drummy concrete at circular joint over an area 150mmx500mm. Priority low. | [5 empty] | 87a60bf7-9426-4475-8cc0-8d530041f8d0 |  | https://web.fulcrumapp.com/photos/view?photos=87a60bf7-9426-4475-8cc0-8d530041f8d0 | Concrete | Circular Connection,Circular Joint | Drummy
b2d7a0fd-12d6-4f5e-851a-38980f0f7afb | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 13 |  |  |  | 2025-07-27 17:05:31 AEST | 2025-07-29 15:17:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 471 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [32 empty] | Ring 471, 4 o’clock | [24 empty] | KP |  | Drummy concrete 100x200mm along the circumferential joint | [5 empty] | 9a9564ff-d50b-4045-9dde-a10872955547 |  | https://web.fulcrumapp.com/photos/view?photos=9a9564ff-d50b-4045-9dde-a10872955547 | Concrete | Circular Connection,Circular Joint | Drummy
7c5dd692-c351-4779-9be0-daf54a5b7f62 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 13 |  |  |  | 2025-07-27 17:20:35 AEST | 2025-07-29 15:17:15 AEST | 30011704-user5@smec.com | james.stone@smec.com | 467 | 3 o’clock |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | KP |  | Drummy / Grout delamination along the circular joint. | [5 empty] | 3709aa29-c6b2-4784-a2d7-59be6cd3da8f |  | https://web.fulcrumapp.com/photos/view?photos=3709aa29-c6b2-4784-a2d7-59be6cd3da8f | Concrete | Circular Connection,Circular Joint | Drummy
04ffbf9a-04f7-4f8d-bc39-76b70fcbf49d | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 13 |  |  |  | 2025-07-27 17:22:15 AEST | 2025-07-29 15:17:29 AEST | 30011704-user5@smec.com | james.stone@smec.com | 467 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy / delaminated grouting along the circumferential joint | [5 empty] | f21274be-718f-49f9-a5fe-427b202013aa |  | https://web.fulcrumapp.com/photos/view?photos=f21274be-718f-49f9-a5fe-427b202013aa | Concrete | Circular Connection,Circular Joint | Drummy
fc8448ad-4af7-4c34-bdaa-591c9daefd75 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 13 | -20.3216 | 118.5853 | POINT (118.5853116 -20.3216462) | 2025-07-27 17:26:54 AEST | 2025-07-29 15:16:35 AEST | 30011704-user5@smec.com | james.stone@smec.com | 466 | 1 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummer patch repair work along the circumferential and radial joint | [5 empty] | b8011c34-dda3-47c5-982a-a7d25c082068 |  | https://web.fulcrumapp.com/photos/view?photos=b8011c34-dda3-47c5-982a-a7d25c082068 | Concrete | Circular Joint,Radial Joint
790584b0-c6d3-48b4-a4e8-644e27ef62ec | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 14 | -20.3216 | 118.5854 | POINT (118.5853663 -20.3216386) | 2025-07-27 16:39:46 AEST | 2025-07-29 15:16:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 460 | 4 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | KP |  | Condition change as reinforcements are corroding and Drumminess in concrete is spreading | [8 empty] | Concrete | Circular Joint,Reinforcement | Drummy
530df6ac-6641-4063-b565-e531f360e529 | ee16eb52-4620-4d27-8038-a3c93bf88107 | ee16eb52-4620-4d27-8038-a3c93bf88107 | 14 | -20.3216 | 118.5853 | POINT (118.5852977 -20.3216314) | 2025-07-27 16:44:26 AEST | 2025-07-29 15:16:54 AEST | 30011704-user5@smec.com | james.stone@smec.com | 461 | 4 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Grout delamination / drummy concrete over an area 100mm x 180mm. Medium priorty | [5 empty] | b4189f20-8b11-467f-afff-5e0b116411dc |  | https://web.fulcrumapp.com/photos/view?photos=b4189f20-8b11-467f-afff-5e0b116411dc | Concrete | Circular Joint | Drummy
a840aaf4-0b0e-481e-8dc0-976d7054bca8 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:09:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 481 | 0 | Grout Injection Hole | Grout Injection Hole |  | 69361 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 481, 1 & 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change, still inactive | no |  |  |  |  | b6389484-7b78-4818-8f97-ea020f79e940 |  | https://web.fulcrumapp.com/photos/view?photos=b6389484-7b78-4818-8f97-ea020f79e940 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
157a07e8-3b77-48b3-962c-8475adf5d9e7 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 | -20.3216 | 118.5853 | POINT (118.5852709 -20.3216342) | 2025-05-27 20:13:18 AEST | 2025-07-30 11:29:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 482 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69364 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.2915 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 482, 10 & 11 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts are missing in three locations. |  | Channel anchor bolts are missing in three locations. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged, still bolts are missing along three locations | no |  |  |  |  | dbb415bb-7be8-464a-ae9a-beae945498bd |  | https://web.fulcrumapp.com/photos/view?photos=dbb415bb-7be8-464a-ae9a-beae945498bd | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
cb4b02b8-0241-4d7e-9f48-9cad399fcf31 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:02:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 482 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27552 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 482, 3 o'clock, Hydrophilic Joint Seal - Circle Joint | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak - Active at time of inspection. |  | Joint seal (Circle joint) has Leak - Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Defect area should be Hydrophilic Joint Seal (Circle Joint). Consequence is changed for consistency with others defects of the same type. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | The leak was inactive at the time of inspection with chloride buildup | yes |  |  |  |  | 21af359f-c7c6-442f-b712-06e3127f97d4 |  | https://web.fulcrumapp.com/photos/view?photos=21af359f-c7c6-442f-b712-06e3127f97d4 | Concrete | Circular Joint | Leaks |  | Not Reinforcement
ef077bf8-13e6-40e8-b05a-00816d5ad3f7 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 16:01:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 482 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 69362 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.2889 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 482, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Minor corrosion on the steel channel as well as missing bolt, no change | no |  |  |  |  | fa7465e0-a933-4b23-babe-f0bd15629377 |  | https://web.fulcrumapp.com/photos/view?photos=fa7465e0-a933-4b23-babe-f0bd15629377 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
5bba9d21-9c62-4b7b-9548-67f38f147cdf | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 12:00:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 483 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36745 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 483, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Condition unchanged, chloride leak is inactive | no |  |  |  |  | 8d308a2f-8556-4223-888e-0c0eafaf4d1b |  | https://web.fulcrumapp.com/photos/view?photos=8d308a2f-8556-4223-888e-0c0eafaf4d1b | Concrete | Grout Hole | Leaks |  | Not Reinforcement
f8daa63c-56df-4abc-b836-332f5b55e9e9 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:39:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 483 | 2 | Grout Injection Hole | Grout Injection Hole |  | 69365 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 483, 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout injection hole had inactive leak at the time of inspection. No change | no |  |  |  |  | 0789484c-deda-4270-b32a-d14860f78633 |  | https://web.fulcrumapp.com/photos/view?photos=0789484c-deda-4270-b32a-d14860f78633 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
e530ac57-ff6e-4862-9e94-23b14f65ad4a | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:44:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 484 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84036 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 484, 7 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | KP |  | Delimited/ drummy grout still present along the circumferential joint, no change in the condition | no |  |  |  |  | 8b9e309c-a5c0-4b8c-8edd-3df7a913082d |  | https://web.fulcrumapp.com/photos/view?photos=8b9e309c-a5c0-4b8c-8edd-3df7a913082d | Concrete | Circular Connection,Circular Joint | Drummy
f929755b-e4b5-48a7-8e11-78a64bc383b3 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 15:48:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 485 | 0 | Grout Injection Hole | Grout Injection Hole |  | 69366 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 485, 1 & 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Inactive leak from grout injection hole, no charge | no |  |  |  |  | c44b9e07-7856-482d-9f8b-f18b671abc0e |  | https://web.fulcrumapp.com/photos/view?photos=c44b9e07-7856-482d-9f8b-f18b671abc0e | Concrete | Grout Hole | Leaks |  | Not Reinforcement
23b9db31-845a-47a0-8fed-98ffd579f2b2 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 11:56:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 485 | 11 | Hydrophilic Joint Seal (Circle Joint) | Hydrophilic Joint Seal (Circle Joint) |  | 84038 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4109 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 485, 11 o'clock, Hydrophilic Joint Seal (Circle Joint) |  |  |  | Hydrophilic Joint Seal (Circle Joint) has 5mm offset at circumferential joint between Ring 485 and 486 |  | Hydrophilic Joint Seal (Circle Joint) has 5mm offset at circumferential joint between Ring 485 and 486 | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged, still it appears to have 5mm offset at 11 o’clock on circumferential joint | no |  |  |  |  | 89d7ffdb-71d4-48e2-8843-db11cfc2b20a |  | https://web.fulcrumapp.com/photos/view?photos=89d7ffdb-71d4-48e2-8843-db11cfc2b20a | Concrete | Circular Connection,Circular Joint | Displacement
da681681-39fb-4435-8f27-304838bfe237 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 11:50:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 486 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26979 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 486, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Steel channel corroded and has 2 bolts missing at 11 o’clock | no |  |  |  |  | 743f571f-3e02-4cd8-822c-d3b713dda153 |  | https://web.fulcrumapp.com/photos/view?photos=743f571f-3e02-4cd8-822c-d3b713dda153 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
e13e74ce-5820-4221-bead-c5a1393c864c | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 11:43:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 487 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36746 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 487, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | Kp |  | Condition unchanged, inactive leak and source of chloride induced. | no |  |  |  |  | 75a3f8b1-f01a-44bd-882d-7915c32defa9 |  | https://web.fulcrumapp.com/photos/view?photos=75a3f8b1-f01a-44bd-882d-7915c32defa9 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
9bc8cd74-4177-48b5-a399-5c26e6980265 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 11:47:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 487 | 11 | Hydrophilic Joint Seal (Circle Joint) | Hydrophilic Joint Seal (Circle Joint) |  | 84043 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4178 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 487, 11 o'clock, Hydrophilic Joint Seal (Circle Joint) |  |  |  | Hydrophilic Joint Seal (Circle Joint) has 5mm offset at circumferential joint between Ring 486 and 487 |  | Hydrophilic Joint Seal (Circle Joint) has 5mm offset at circumferential joint between Ring 486 and 487 | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged | no |  |  |  |  | 330744ff-e53e-4d48-8e34-ebbdb9893d5f |  | https://web.fulcrumapp.com/photos/view?photos=330744ff-e53e-4d48-8e34-ebbdb9893d5f | Concrete | Circular Connection,Circular Joint | Displacement
f03ce7bf-6157-4204-bffd-57871c7144e7 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 | -20.3216 | 118.5853 | POINT (118.5852921 -20.321602) | 2025-05-27 20:13:18 AEST | 2025-07-26 18:12:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 488 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36747 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 488, 12 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Leak was Inactive at the time of inspection. | no |  |  |  |  | 0b9957a4-d1b7-4c99-9080-9ed24e4787b6,43379417-4059-454e-98bb-bfe1a81951b6 | , | https://web.fulcrumapp.com/photos/view?photos=0b9957a4-d1b7-4c99-9080-9ed24e4787b6%2C43379417-4059-454e-98bb-bfe1a81951b6 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
fec4e0f3-e545-4112-be0e-ea5b204255e6 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 | -20.3217 | 118.5853 | POINT (118.5853201 -20.3216563) | 2025-05-27 20:13:18 AEST | 2025-07-26 18:14:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 488 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84044 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4196 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 488, 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 50% coverage. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | The steel channel has rusted, with inactive leaks | no |  |  |  |  | 408f597a-c3d0-48ef-b85c-6c93a0bf37ca |  | https://web.fulcrumapp.com/photos/view?photos=408f597a-c3d0-48ef-b85c-6c93a0bf37ca | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Leaks
cbaa1a0c-30c2-4cd0-acde-27c3f99078b4 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 | -20.3217 | 118.5853 | POINT (118.5853248 -20.3216531) | 2025-05-27 20:13:18 AEST | 2025-07-25 07:27:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 490 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26980 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 490, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts are missing at 2 locations at 10 O'clock 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Channel anchor bolts are missing at 2 locations at 10 O'clock 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the steel channel is as per previous inspection. The bolt at 11 o'clock is not fully engaged. The channel does not appear to be secured between 9 and 12 o'clock. Medium priority. | yes | no |  | no |  | 206c5e10-2226-489a-a13d-72bf2026edb1,b469cc28-e969-4e2e-8d6b-44192acc0760,5539fe87-a5f8-4d75-8564-bf4f5882a071 | ,, | https://web.fulcrumapp.com/photos/view?photos=206c5e10-2226-489a-a13d-72bf2026edb1%2Cb469cc28-e969-4e2e-8d6b-44192acc0760%2C5539fe87-a5f8-4d75-8564-bf4f5882a071 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
5a405394-6ab8-494c-8404-a75fa724857c | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:49:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 490 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84046 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4212 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 490, 2 o'Clock, Channel Anchor Bolts |  |  |  | Channel anchor bolt missing nut. |  | Channel anchor bolt missing nut. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Nut is still missing. Low priority defect. | no | no |  | no |  | 498cbb38-c86c-4c7d-99c9-f7a68dd6c99c |  | https://web.fulcrumapp.com/photos/view?photos=498cbb38-c86c-4c7d-99c9-f7a68dd6c99c | Steel | Channel Bracket-Bolt | Missing
a02575b0-46fb-4ff3-b375-2327c79fd563 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:57:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 490 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 101794 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 490, 5 O'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Condition remains unchanged. Location at 4 O Clock not 5 | no | yes |  | yes | Location to 4 O Clock | 6b57fcca-4567-4091-ac28-ef5a05a9cc8a |  | https://web.fulcrumapp.com/photos/view?photos=6b57fcca-4567-4091-ac28-ef5a05a9cc8a | Concrete | Radial Joint | Drummy
9215294c-6007-4ee4-918d-3d096c2f859e | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 | -20.3782 | 118.6321 | POINT (118.6320895 -20.3781787) | 2025-05-27 20:13:18 AEST | 2025-07-30 11:29:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 490 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36748 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 490, 9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. The seal bolt is in good condition. | no | yes |  | no |  | 45276cbd-5a5b-49e5-97eb-4cf75bf8740c,7e65d7c7-7f9b-44ea-9e21-e97c8ad5f8b1 | , | https://web.fulcrumapp.com/photos/view?photos=45276cbd-5a5b-49e5-97eb-4cf75bf8740c%2C7e65d7c7-7f9b-44ea-9e21-e97c8ad5f8b1 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
1410fae6-531f-4106-91c3-fc47ec46b422 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 07:21:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 491 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27277 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 491, 11 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of production and services | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding, Walkway | Working at Heights | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. Salt deposits are noted on the hole walls. The seal bolt is missing. | yes | yes |  | no |  | 655ff908-8a09-497b-9d1a-6dfea866e4b2,8679ef88-6edb-4f15-bd16-dc85da3b5f5d | , | https://web.fulcrumapp.com/photos/view?photos=655ff908-8a09-497b-9d1a-6dfea866e4b2%2C8679ef88-6edb-4f15-bd16-dc85da3b5f5d | Concrete | Grout Hole | Leaks,Missing |  | Not Reinforcement
625c1300-c7ed-4a1c-bb0d-054df6caae9f | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:50:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 492 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26981 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 492, 1 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | Dr |  | Major leak still present and active. Salt deposits are still present and has corroded the pipe below and walkway as well. High priority defect. | yes | yes |  |  |  | d8d82f5c-2c04-4f2f-abf6-860e0ef36802,216f497e-da60-4854-ba6c-77c1f8bacf9f,7661700e-2260-4a8b-950b-7186676f5bbd,a14f9d37-8709-462b-83ad-8221c9bf0dd9,7ff5c47f-8502-44fa-9259-490849ff02dd,7bafc784-7c44-4171-a905-fe7dd45d78a1 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=d8d82f5c-2c04-4f2f-abf6-860e0ef36802%2C216f497e-da60-4854-ba6c-77c1f8bacf9f%2C7661700e-2260-4a8b-950b-7186676f5bbd%2Ca14f9d37-8709-462b-83ad-8221c9bf0dd9%2C7ff5c47f-8502-44fa-9259-490849ff02dd%2C7bafc784-7c44-4171-a905-fe7dd45d78a1 | Concrete | Grout Hole,Misc (Pipes/Cable Tray/etc),Reinforcement | Leaks
05622f5c-1efb-4621-87d5-d55dcb4bde81 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:08:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 492 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36751 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.6019 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 492, 2 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support anchor bolts are missing. |  | Steel channel support anchor bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | There is no steel channel present during the inspection in the section from 12 o’clock to 2 o’clock | yes |  |  |  |  | 4a4fb6f0-f02a-405a-9fae-2cf7a1ed80ae |  | https://web.fulcrumapp.com/photos/view?photos=4a4fb6f0-f02a-405a-9fae-2cf7a1ed80ae | Steel | Channel Bracket,Channel Bracket-Bolt | Missing |  | Duplicate - Remove
70653b66-0084-47c3-a5a2-0b832569532f | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:57:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 492 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69368 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 492, 5 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints over an area of 300mm x 200mm. |  | Grout Delamination / debonding at radial segment bolted joints over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Component should be "Segmented Bolted Joint (Radial Joint)". Adopted default consequence Health & Safety - Level 2. | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Delimited/drummy grout still present along the joint | no |  |  |  |  | 50ec3db5-50a5-435c-9ddd-809de33368ef |  | https://web.fulcrumapp.com/photos/view?photos=50ec3db5-50a5-435c-9ddd-809de33368ef | Concrete | Circular Joint,Radial Joint | Drummy
755443ca-f4e6-475a-96ff-09da9b92dd2d | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 07:17:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 492 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36749 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 492, 9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. The defect do not appear to advance. | no | yes |  | no |  | 540cea46-4ae6-4d2f-a33b-69e15b57c696,5d4da366-cc46-4057-ac96-940b2e20575a | , | https://web.fulcrumapp.com/photos/view?photos=540cea46-4ae6-4d2f-a33b-69e15b57c696%2C5d4da366-cc46-4057-ac96-940b2e20575a | Concrete | Grout Hole | Leaks |  | Not Reinforcement
edaf97c4-2f7f-4a99-a23d-539a6731eb6f | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:08:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 492 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36750 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 43901.6012 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 492, 12 O'clock: Grout Injection Hole. |  |  |  | Active leak. |  | Active leak. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | Grout injection hole had active leak during inspection | no |  |  |  |  | 3b5ebb2c-7c73-44e2-bdb1-a54bfb356a17 |  | https://web.fulcrumapp.com/photos/view?photos=3b5ebb2c-7c73-44e2-bdb1-a54bfb356a17 | Concrete | Grout Hole | Leaks
424df112-9de0-46c3-a55f-4a4b4699cfa2 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 07:11:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 494 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 84057 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4402 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 494, 11 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 1 Corrosion. One anchor bolt missing. One bolt is required per group of three bolt holes as per 117-C-00241/3. Steel channel support bracket has Level 2 Corrosion up to 5% coverage. |  | Channel anchor bolts have Level 1 Corrosion. One anchor bolt missing. One bolt is required per group of three bolt holes as per 117-C-00241/3. Steel channel support bracket has Level 2 Corrosion up to 5% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the steel is as per previous inspection. Low priority. | no | yes |  | no |  | e096f6fb-7722-42b9-a574-e6f0c3fc1784 |  | https://web.fulcrumapp.com/photos/view?photos=e096f6fb-7722-42b9-a574-e6f0c3fc1784 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
ff7111fe-314b-4248-9a08-cd40084f49bf | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:38:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 494 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84047 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.423 |  |  | No | Missing |  |  |  | 2 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 494, 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Minor corrosion are still present. Condition remains unchanged. Low priority Defect. | no | no |  | no |  | 7ea81f1d-370f-4035-8da5-427b590389a1 |  | https://web.fulcrumapp.com/photos/view?photos=7ea81f1d-370f-4035-8da5-427b590389a1 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
caaf7bac-2c3d-4a06-bf71-f1353bdadd27 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:51:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 494 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 101795 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 494, 4 O'clock | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Defect still present with no change in condition. | no | yes |  |  |  | 60057a6a-5853-4001-9d06-14cc345f236b,302f3758-1580-4727-b163-6902a5b8cc6a | , | https://web.fulcrumapp.com/photos/view?photos=60057a6a-5853-4001-9d06-14cc345f236b%2C302f3758-1580-4727-b163-6902a5b8cc6a | Concrete | Radial Joint | Drummy
f33770a4-d944-4756-8911-e4f2db2516c6 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:43:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 495 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93652 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 495, 7 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The defect has not changed. The defect is considered superficial with no structural implication. Low priority | no | yes |  | no |  | 83771ec2-8971-4fbc-8335-9c2a4c949c3a |  | https://web.fulcrumapp.com/photos/view?photos=83771ec2-8971-4fbc-8335-9c2a4c949c3a | Concrete | Radial Joint | Drummy
2f28e6a0-8b89-4bb6-ab92-1f9f1987ea6c | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:30:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 496 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 93321 |  | 8714 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 496, 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Steel channel support bracket has Level 4 corrosion |  | Steel channel support bracket has Level 4 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace corroded channel bracket and anchor bolts. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | Dr |  | Condition remains unchanged. Severe corrosion still present. | no | yes |  | no |  | fbca9772-4df3-46b7-8c00-92bb5865554d |  | https://web.fulcrumapp.com/photos/view?photos=fbca9772-4df3-46b7-8c00-92bb5865554d | Steel | Channel Bracket | Corrosion-Heavy
bd1863c2-665d-4f21-adcc-e65a95e1da28 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 23:08:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 496 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 93322 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 496, 3 O'clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Active leak shall be assessed as P2 as discussed with BHP AIMS. | Not Specified | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | Leak still remains active on steel bolt channel. Severe level 5 corrosion noted. High priority defect. | yes | no |  |  |  | 09be2354-dfd1-4927-bf25-20bdb710006e,6c4c1495-095a-4420-a089-27112e71446c,cb492a97-ec5f-4993-ac2c-ee168ecbfbe4,7a1a269a-7198-4cb9-996c-851d3bd8d098,73a16de5-b885-460d-835e-5c3a23b37a28 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=09be2354-dfd1-4927-bf25-20bdb710006e%2C6c4c1495-095a-4420-a089-27112e71446c%2Ccb492a97-ec5f-4993-ac2c-ee168ecbfbe4%2C7a1a269a-7198-4cb9-996c-851d3bd8d098%2C73a16de5-b885-460d-835e-5c3a23b37a28 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Leaks |  | Channel Bracket and Bolt
ae13645e-0749-4c93-ba22-17a9b4adaea6 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:49:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 497 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84049 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 497, 4 o'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has spalling damage over an area of 100mm x 100mm. |  | Concrete shell segment has spalling damage over an area of 100mm x 100mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), upgraded to P3. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. | Not Specified | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | Yes | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | Dr |  | Condition remains unchanged. Priority can be reduced | no | yes |  |  |  | 03f5265d-3c38-405c-8804-25ae77078c02 |  | https://web.fulcrumapp.com/photos/view?photos=03f5265d-3c38-405c-8804-25ae77078c02 | Concrete | Circular Connection,Circular Joint | Surface Damage |  | Circular Connection and Joint
62dfc0a9-11c4-4dd5-bd94-071c7e424dd5 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 07:05:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 498 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69369 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.3456 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 498, 10, 11 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 2 Corrosion. |  | Channel anchor bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the steel is as per previous inspection. Low priority. | no | yes |  | no |  | 75f963e2-c113-40d5-9790-04250fb226fc,cd99d63e-c870-4e18-b3b4-6266330b6a6e | , | https://web.fulcrumapp.com/photos/view?photos=75f963e2-c113-40d5-9790-04250fb226fc%2Ccd99d63e-c870-4e18-b3b4-6266330b6a6e | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface |  | not heavy
96e1b8cb-427d-4ea7-ab55-4fade02324f2 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:25:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 498 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27566 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 498, 3 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. | Loss of services. |  | Loss of services. |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Condition remains unchanged. Low priority defect. | no | no |  | no |  | 606ee1dc-fd12-4762-b0a1-fa7b7ce25b57,75e7fd3c-8a1d-496e-9ab4-3aa2f1db0d62,f405d986-a2cc-4b52-9931-5a9d177a5b8e | ,, | https://web.fulcrumapp.com/photos/view?photos=606ee1dc-fd12-4762-b0a1-fa7b7ce25b57%2C75e7fd3c-8a1d-496e-9ab4-3aa2f1db0d62%2Cf405d986-a2cc-4b52-9931-5a9d177a5b8e | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface |  | not heavy
6b88abb9-928e-4f3a-a71c-4b9ad271bd32 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:46:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 498 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 101796 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 498, 4 O'clock | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Condition remains unchanged. | no | yes |  | no |  | 9bf13312-a8dc-4ba3-adfc-e40117ff3299 |  | https://web.fulcrumapp.com/photos/view?photos=9bf13312-a8dc-4ba3-adfc-e40117ff3299 | Concrete | Radial Joint | Drummy
529f9cae-a3ae-4890-bb24-a45cb92ba27a | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:38:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 499 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36752 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 499, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The defect has not changed. The defect is superficial with no structural implication. Low priority | no | yes |  | no |  | cd25993b-86e7-4953-a39e-89956c3b5124 |  | https://web.fulcrumapp.com/photos/view?photos=cd25993b-86e7-4953-a39e-89956c3b5124 | Concrete | Radial Joint | Drummy |  | Not Reinforcement
5bfe748c-9dfe-43bc-89d6-958dd1629e9b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:41:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 501 | 4 | Grout Injection Hole | Grout Injection Hole |  | 69372 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 22/12/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 501, 4 o'clock. Concrete Shell Segment Radial Joint Connection. | Break up of grout and water leaks | Break up of grout and water leaks |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Remediate grout as per BHP Standards and specifications | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | Dr |  | Condition remains unchanged. Grout delamination and drumminess is still present. Defect is located at 5 O Clock. Not Present at 4. | no | yes |  | yes | Location to 5 O Clock | 3f0dfd0a-7a59-4416-8c41-33c52b90a396,9806a6b9-32fe-4345-a460-3b7bdfaf50f6 | , | https://web.fulcrumapp.com/photos/view?photos=3f0dfd0a-7a59-4416-8c41-33c52b90a396%2C9806a6b9-32fe-4345-a460-3b7bdfaf50f6 | Concrete | Grout Hole,Radial Joint | Drummy,Leaks |  | Not Reinforcement
43b5ff74-4980-4ecb-a237-d6af378647b4 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:33:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 501 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84059 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 501, 7 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The defect has not changed. The defect is considered superficial with no structural implication. | no | yes |  | no |  | 88bf9dd6-df90-455d-ba50-d6487d189215,794f2174-5dce-4845-a661-8a3b669456c7 | , | https://web.fulcrumapp.com/photos/view?photos=88bf9dd6-df90-455d-ba50-d6487d189215%2C794f2174-5dce-4845-a661-8a3b669456c7 | Concrete | Circular Joint | Drummy
adb42c82-18ce-4870-bb62-304f50204a39 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:31:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 501 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36753 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 501, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 400 mm |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 400 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The condition of the defect has changed with the area of drummy mortar broken. The defect is considered superficial with no structural implication | yes | yes |  | no |  | 055d3c25-75ac-45c9-a05e-0f5c9785e418,7341fce0-f1d6-41a5-b6c5-89407b3d58e6 | , | https://web.fulcrumapp.com/photos/view?photos=055d3c25-75ac-45c9-a05e-0f5c9785e418%2C7341fce0-f1d6-41a5-b6c5-89407b3d58e6 | Concrete | Mortar,Radial Joint | Drummy |  | Not Reinforcement
848d37e7-abc2-46e7-947f-af88dec208cb | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:26:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 501 | 8 | Grout Injection Hole | Grout Injection Hole |  | 84061 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 501, 8 o'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The leak is active at the time of inspection. Hole is sealed by salt deposits. The condition of the steel nut is not able to be assessed. | no | yes |  | no |  | 4b2fbbb4-e5f1-4afe-8ab3-0fe540605dcd,76b2d5eb-0410-4852-a0a7-a08ac3b1e577 | , | https://web.fulcrumapp.com/photos/view?photos=4b2fbbb4-e5f1-4afe-8ab3-0fe540605dcd%2C76b2d5eb-0410-4852-a0a7-a08ac3b1e577 | Steel | Grout Hole | Leaks
eb4697a4-96a0-428d-8b41-c6484484b5e6 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:14:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 502 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26982 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 502, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Condition remains unchanged to previous inspection. Level 2 corrosion still present on the steel bracket. | no | yes |  | no |  | 32c1e639-8ab5-4787-8322-00e8a6413e4d,39312999-9e80-494b-99fe-a63616603457 | , | https://web.fulcrumapp.com/photos/view?photos=32c1e639-8ab5-4787-8322-00e8a6413e4d%2C39312999-9e80-494b-99fe-a63616603457 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
fd9af572-0990-4191-bc62-e183efb997ba | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:58:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 502 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 84064 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4483 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 502, 11 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 5% coverage. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 5% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the defect has not changed. Priority low. | no | yes |  | no |  | 5bd93695-851e-409b-acb7-1bc2c103db87 |  | https://web.fulcrumapp.com/photos/view?photos=5bd93695-851e-409b-acb7-1bc2c103db87 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
d729411f-8899-4b7f-b20c-e30a7edd7b79 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:21:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 502 | 8 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84063 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 502, 8 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | Superficial defect with no structural implication. Low priority | no | yes |  | no |  | cf5c26a4-f84a-46f9-8e8c-61785569d36d |  | https://web.fulcrumapp.com/photos/view?photos=cf5c26a4-f84a-46f9-8e8c-61785569d36d | Concrete | Radial Joint | Drummy
d71c38e7-21a4-4e4f-810f-213d654e4967 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:56:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 503 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84067 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 503, 12 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The condition of the defect is similar to the initial inspection. Defect is considered cosmetic with no structural implications. | no | yes |  | no |  | 85342b15-b6b5-4bd9-b9f9-0f386d70306d |  | https://web.fulcrumapp.com/photos/view?photos=85342b15-b6b5-4bd9-b9f9-0f386d70306d | Concrete | Radial Joint | Drummy
59abdf73-6cbb-4418-97ac-90b2e2c82122 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:17:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 503 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84066 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 503, 7 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Walkway | Excavation | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The condition of the defect has not changed. Superficial defect with no structural implication. | no | yes |  | no |  | 7d7666d3-f185-4e65-93d7-911ca72b64c8 |  | https://web.fulcrumapp.com/photos/view?photos=7d7666d3-f185-4e65-93d7-911ca72b64c8 | Concrete | Radial Joint | Drummy
117dc8c4-9e37-43d6-aed5-72e5ca3355c4 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:38:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 505 | 4 | Grout Injection Hole | Grout Injection Hole |  | 69367 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 505, 4 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | DR |  | Incorrect defect location. Leak has been previously present at 1 O clock on the grout injection hole. Leak is inactive at time of inspection. No leak at 4 O Clock | no | yes |  | yes | Location to be changed to 1 O Clock from 4 O clock. | 45eac75c-2f85-4835-aa70-f5912be29dc5 |  | https://web.fulcrumapp.com/photos/view?photos=45eac75c-2f85-4835-aa70-f5912be29dc5 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
533389dd-c5d3-4f99-86fa-4adcdebb559c | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 23:02:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 506 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26983 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 506, 2,3 & 12 o'clock, Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 corrosion. Missing 2 anchor bolts. Steel channel Support Bracket has Level 2 corrosion at 5% coverage. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket anchor bolts have Level 2 corrosion. Missing 2 anchor bolts. Steel channel Support Bracket has Level 2 corrosion at 5% coverage. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Condition remains mostly unchanged. Corrosion still remains at same level, little less than what's specified in previous inspection. Bolts are still missing. Low priority defect. | no | no |  | no |  | b2b1e9e0-385a-4ad7-a65a-1c7139896e84,23ac56b1-bcc3-4be5-ab2d-5486cc190b67 | , | https://web.fulcrumapp.com/photos/view?photos=b2b1e9e0-385a-4ad7-a65a-1c7139896e84%2C23ac56b1-bcc3-4be5-ab2d-5486cc190b67 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
6be783b5-9d5a-4664-8a04-69a25287bf6d | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:36:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 509 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84068 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 509, 12 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | Defect condition as per previous inspection. The defect is not considered structural. Low priority. | no | no |  | no |  | 6cb3a5c4-7aeb-4646-9d7e-6771fb201ed0 |  | https://web.fulcrumapp.com/photos/view?photos=6cb3a5c4-7aeb-4646-9d7e-6771fb201ed0 | Concrete | Radial Joint | Drummy
2206b693-93d8-43d8-a641-115809157569 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:32:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 509 | 8 | Grout Injection Hole | Grout Injection Hole |  | 69370 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 509, 8 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. No significant salt deposits visible. The seal bolt is in good condition. Low priority | no | yes |  | no |  | f36dd8b8-f1b7-4359-ab60-394ea66b9e9d,fda8a759-2313-48ac-a34e-4e195af8f044,f185e400-8c76-4e2a-b008-b927fa35b6e0 | ,, | https://web.fulcrumapp.com/photos/view?photos=f36dd8b8-f1b7-4359-ab60-394ea66b9e9d%2Cfda8a759-2313-48ac-a34e-4e195af8f044%2Cf185e400-8c76-4e2a-b008-b927fa35b6e0 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
713b8a3b-a92e-4117-ba5f-d6dbaa44a649 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 | -20.3782 | 118.6321 | POINT (118.6320721 -20.3781756) | 2025-05-27 20:13:18 AEST | 2025-07-30 11:28:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 510 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69371 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.3483 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 510, 10, 11 & 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion at 10% coverage. Channel anchor bolts have level 2 corrosion. Some of the anchor bolts are missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket has Level 2 corrosion at 10% coverage. Channel anchor bolts have level 2 corrosion. Some of the anchor bolts are missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The steel channel is in the same condition as per previous inspection. No additional bolts are required. Low priority | no | no |  | no |  | ba16d8fa-1166-414f-b3d8-485dd440f8b4,1d2bcb6a-39e3-4761-b2c2-834141e3289d | , | https://web.fulcrumapp.com/photos/view?photos=ba16d8fa-1166-414f-b3d8-485dd440f8b4%2C1d2bcb6a-39e3-4761-b2c2-834141e3289d | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
9442f102-b8ba-4ae8-9461-7e3e68da95ae | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:29:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 510 | 12 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26984 |  | 6512 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 510, 12 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket anchor bolts have Level 3 - Medium Corrosion and several bolts missing. |  | Steel channel support bracket anchor bolts have Level 3 - Medium Corrosion and several bolts missing. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services | Priority: P3 |  |  |  | Install Chem Set/ HILTI bolts for the missing bolts as per Original design / BHP Specifications. Blast and paint the affected area as per BHP specifications | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | Scaffolding | Working at Heights | Corrosion Repair Competent Supervisor | Bogdan Stanca |  | Steel channel condition as per previous inspection. Sufficient anchor bolts are present. Low priority. | no | no |  | no |  | 218702db-177f-4480-9ab3-56ce9ade254a |  | https://web.fulcrumapp.com/photos/view?photos=218702db-177f-4480-9ab3-56ce9ade254a | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
ff856252-a4da-4e51-abde-19a871e9eb82 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:49:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 510 | 2 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 101775 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 45553.5793 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 510, 2 O'clock, Segmented Bolted Joint (Radial Joint) |  |  |  | 0.3mm crack at radial segment bolted joint grout. |  | 0.3mm crack at radial segment bolted joint grout. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Crack still remains same size. Condition is unchanged. Low priority defect. | no | no |  | no |  | 5df8f33c-fbd9-49d6-8ba2-4963c2b6ddc7,148573c6-6216-4c55-8200-46ca5520e076 | , | https://web.fulcrumapp.com/photos/view?photos=5df8f33c-fbd9-49d6-8ba2-4963c2b6ddc7%2C148573c6-6216-4c55-8200-46ca5520e076 | Concrete | Radial Joint | Crack
468f0bb1-a409-4550-bd57-018fabe895e7 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 28 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:32:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 510 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84069 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 510, 4 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. | Loss of production and services | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | Section of drummy concrete is still present at the radial joint. No change in condition. Low priority defect. | no | yes |  | no |  | 6d534d2f-03e3-44e3-8f9e-d876b5b50245,63110c83-7c80-40c6-948e-c51ae37410ea,bd8591fc-d78d-47b2-8437-ce6e22f9333e | ,, | https://web.fulcrumapp.com/photos/view?photos=6d534d2f-03e3-44e3-8f9e-d876b5b50245%2C63110c83-7c80-40c6-948e-c51ae37410ea%2Cbd8591fc-d78d-47b2-8437-ce6e22f9333e | Concrete | Radial Joint | Drummy
b721a11f-f796-43f1-b256-63c75717d54e | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 22 | -20.3177 | 118.5782 | POINT (118.5781672 -20.3177013) | 2025-07-25 11:29:53 AEST | 2025-07-30 11:28:24 AEST | 30011704-user5@smec.com | james.stone@smec.com | 489 | 10 O'Clock |  | Grout Injection Hole | [57 empty] | RT |  | Dry leak chloride induced. Condition unchanged |  |  |  | no |  | fdbe02f5-7f5e-467c-827a-ceae29452287 |  | https://web.fulcrumapp.com/photos/view?photos=fdbe02f5-7f5e-467c-827a-ceae29452287 | Concrete | Grout Hole | Leaks
f3ad5841-ac4a-4d29-b189-c6b1aaae1fa3 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 22 | -20.318 | 118.5777 | POINT (118.5776726 -20.3180421) | 2025-07-25 11:34:30 AEST | 2025-07-27 08:42:35 AEST | 30011704-user5@smec.com | james.stone@smec.com | 487 | 9 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Etched surface size 200x600mm. Condition 2 | [5 empty] | dda6db20-5b69-454e-a030-03d4d204f285 |  | https://web.fulcrumapp.com/photos/view?photos=dda6db20-5b69-454e-a030-03d4d204f285 | Concrete | Circular Joint |  |  | Circular Joint
84bc133a-08d0-4881-9015-2f6e0f6eef2e | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 20 |  |  |  | 2025-07-25 22:33:27 AEST | 2025-07-25 22:37:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 509 | 7 o'clock |  | Segment Bolted Joint (Radial Joint) | [38 empty] | Radial joint grout delamination 100x100mm. | [12 empty] | Yes |  | Yes |  |  |  | Bogdan Stanca |  | Grout delamination at radial joint 7 o'clock. Superficial defect with no structural implication. Low priority. |  |  |  | no |  | d5d5cdc8-7935-444e-8ab9-9f8e86dd8eaa |  | https://web.fulcrumapp.com/photos/view?photos=d5d5cdc8-7935-444e-8ab9-9f8e86dd8eaa | Concrete | Radial Joint | Drummy
c4d7a713-ba06-4557-8337-9539ed8227fb | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 20 |  |  |  | 2025-07-25 23:47:18 AEST | 2025-07-29 10:09:15 AEST | 30011704-user5@smec.com | james.stone@smec.com | 492 | 5 o'clock |  |  | Steel support column | [37 empty] | Leveling grout under the base plate is heavenly cracked. | [18 empty] | Bogdan Stanca |  | The mortar under the base plate is heavenly cracked and delaminated. Is no longer providing adequate support to the base plate. Medium priority. Structural steel supporting the walkway is heavily corroded. High priority. |  |  |  | no |  | 2f494006-6be8-45e1-ae2c-3aa593c5ad49,d5f1f87f-0859-4536-805d-7cceca70f7b4,7f44584c-8d40-4e66-9dd2-5056e6d0540f,6231ca83-319b-46fc-954d-e2c135e86d4e,f1878a3e-804c-4736-bbcc-901d32c317c4,12466592-75b0-47b3-a334-112c08eb8414,9719c508-cd4a-4118-ba76-05aa3ac38547,900f7b03-b715-49da-888e-35634b5bc414,07b10bb3-b8c8-4ce0-8db2-74483930fd99 | ,,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=2f494006-6be8-45e1-ae2c-3aa593c5ad49%2Cd5f1f87f-0859-4536-805d-7cceca70f7b4%2C7f44584c-8d40-4e66-9dd2-5056e6d0540f%2C6231ca83-319b-46fc-954d-e2c135e86d4e%2Cf1878a3e-804c-4736-bbcc-901d32c317c4%2C12466592-75b0-47b3-a334-112c08eb8414%2C9719c508-cd4a-4118-ba76-05aa3ac38547%2C900f7b03-b715-49da-888e-35634b5bc414%2C07b10bb3-b8c8-4ce0-8db2-74483930fd99 | Steel | Centre Support | Crack,Drummy |  | Centre Support
681c70dc-46d6-4421-8fe4-5c9c8e866190 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 22 | -20.318 | 118.5775 | POINT (118.5774637 -20.3180343) | 2025-07-25 11:41:05 AEST | 2025-07-30 11:27:42 AEST | 30011704-user5@smec.com | james.stone@smec.com | 485 | 10 O'Clock |  | Grout Injection Hole | [57 empty] | RT |  | Dry leak chloride induced. No signs of further leakage. Not a structural issue, only cosmetic. | [5 empty] | 13bbd88d-25f7-43c6-a6b9-cc3e57e10db4,16e9243c-383f-482d-9469-04ebda747d7e | , | https://web.fulcrumapp.com/photos/view?photos=13bbd88d-25f7-43c6-a6b9-cc3e57e10db4%2C16e9243c-383f-482d-9469-04ebda747d7e | Concrete | Grout Hole | Leaks
0ce8b2c6-ee1f-4f38-b9b6-40834d217efe | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 22 | -20.3179 | 118.5773 | POINT (118.5772776 -20.3179407) | 2025-07-25 11:51:43 AEST | 2025-07-29 10:04:42 AEST | 30011704-user5@smec.com | james.stone@smec.com | 484 | 10 O'Clock |  | Grout Injection Hole | [57 empty] | RT |  | Dry leak chloride induced, damage to grout injection with concrete starting to show signs of wear/tear. | [5 empty] | f2bc4d11-b7e1-4c2c-b225-a496a35f36ce |  | https://web.fulcrumapp.com/photos/view?photos=f2bc4d11-b7e1-4c2c-b225-a496a35f36ce | Concrete | Grout Hole | Leaks
e80be846-8e96-44d2-b906-2c7e83a56754 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 22 | -20.3179 | 118.5773 | POINT (118.5773181 -20.3179051) | 2025-07-25 11:57:40 AEST | 2025-07-31 04:51:14 AEST | 30011704-user5@smec.com | james.stone@smec.com | 482 | 8 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Etched surface size 500x1000mm. No structural implications, only cosmetic defect. | [5 empty] | 56993c56-9a17-43ae-8db2-fd54034a2c94 |  | https://web.fulcrumapp.com/photos/view?photos=56993c56-9a17-43ae-8db2-fd54034a2c94 | Concrete |  |  |  | Duplicate - Remove
47599ba9-4b85-4a6f-84e8-81801b188eec | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 24 |  |  |  | 2025-07-25 06:43:13 AEST | 2025-07-25 06:49:36 AEST | 30011704-user5@smec.com | james.stone@smec.com | 507 | 11 o'clock |  | Grout Injection Hole | [38 empty] | Concrete delamination at the grout hole due to leaking. Currently the leak is not active. | [18 empty] | Bogdan Stanca |  | Due to the salt water leak at the grout hole, the concrete matrix has been weakened and concrete delamination is noted to a depth of 25mm. The extent of delamination is contained around the hole for a radius of 100mm. |  |  |  | no |  | cabc84eb-8d3e-4bca-84ce-0db26369a0f8,20e34bca-5e31-47f1-8190-0c8de2d51972,c6b01c82-0ce4-4b58-8bfa-ae5bf0ed92a4 | ,, | https://web.fulcrumapp.com/photos/view?photos=cabc84eb-8d3e-4bca-84ce-0db26369a0f8%2C20e34bca-5e31-47f1-8190-0c8de2d51972%2Cc6b01c82-0ce4-4b58-8bfa-ae5bf0ed92a4 | Concrete | Grout Hole | Drummy,Leaks
4d887bd5-45c6-4c2b-9994-0dad4f1b4cce | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 24 |  |  |  | 2025-07-25 07:05:33 AEST | 2025-07-29 10:11:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 498 | 11 o'clock |  | Segment Bolted Joint (Radial Joint) | [51 empty] | Yes | [5 empty] | Bogdan Stanca |  | Fine crack at the radial connection at 11 o'clock. Not considered structural. Low priority. |  |  |  | no |  | ed4f0aee-2815-444c-9cd4-1bb3e4388aef,0fe230f4-3db3-4e1d-ac12-494993a4204d,b6d87319-38ca-4743-9297-fdc6d93193fa | ,, | https://web.fulcrumapp.com/photos/view?photos=ed4f0aee-2815-444c-9cd4-1bb3e4388aef%2C0fe230f4-3db3-4e1d-ac12-494993a4204d%2Cb6d87319-38ca-4743-9297-fdc6d93193fa | Concrete | Radial Connection,Radial Joint | Crack
b644991a-2bf3-4abf-af52-223e2af1e722 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 23 | -20.318 | 118.5773 | POINT (118.5772759 -20.3179802) | 2025-07-25 12:02:12 AEST | 2025-07-29 10:11:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 483 | 11 o'clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy patch repair at the circumferential joint | [5 empty] | 938bff1d-67ac-4924-b07a-4ba86338ea85 |  | https://web.fulcrumapp.com/photos/view?photos=938bff1d-67ac-4924-b07a-4ba86338ea85 | Concrete | Circular Connection,Circular Joint | Drummy
55ad6b1d-590a-4701-a0d0-f0d60bc625ac | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 23 | -20.3179 | 118.5773 | POINT (118.5773253 -20.317904) | 2025-07-25 12:03:33 AEST | 2025-07-29 10:11:35 AEST | 30011704-user5@smec.com | james.stone@smec.com | 483 | 10 O'Clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy patch repair at the circumferential joint | [5 empty] | effec798-4b3c-4b85-8dad-cb7b83b95e02 |  | https://web.fulcrumapp.com/photos/view?photos=effec798-4b3c-4b85-8dad-cb7b83b95e02 | Concrete | Circular Connection,Circular Joint | Drummy
2a675681-3e3c-4bec-bef1-75604afc911b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 21 |  |  |  | 2025-07-25 22:54:20 AEST | 2025-07-29 10:11:16 AEST | 30011704-user5@smec.com | james.stone@smec.com | 508 | 1 O clock |  | Segment Bolted Joint (Circle Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 | [29 empty] | DR |  | Drumminess at concrete patchwork on the circumferential joint. |  | yes |  | no |  | 1b29942d-59dd-4f88-aa05-e5d877fba3c9 |  | https://web.fulcrumapp.com/photos/view?photos=1b29942d-59dd-4f88-aa05-e5d877fba3c9 | Concrete | Circular Connection,Circular Joint | Drummy
4ec2dfaf-cea5-41e0-9393-5c38afe75366 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 21 |  |  |  | 2025-07-25 23:08:50 AEST | 2025-07-29 10:11:01 AEST | 30011704-user5@smec.com | james.stone@smec.com | 504 | 2 O'Clock |  | Segment Bolted Joint (Radial Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 2 | [6 empty] | Poor Construction Methods |  |  | Severity Level 2 |  |  | Possible (Failure within 5 Years) | [26 empty] | Dr |  | Drumminess of concrete at the patchwork on the radial joint. |  | yes |  | no |  | a8ec0a85-448a-4a6a-8d71-3f754d141e06,60fb66ac-b1b5-4f0c-b872-155fad560d74 | , | https://web.fulcrumapp.com/photos/view?photos=a8ec0a85-448a-4a6a-8d71-3f754d141e06%2C60fb66ac-b1b5-4f0c-b872-155fad560d74 | Concrete | Radial Joint | Drummy
432e2953-8930-48ea-a37b-f976724b6441 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 18 | -20.3179 | 118.5773 | POINT (118.5773232 -20.3179033) | 2025-07-26 18:07:12 AEST | 2025-07-29 10:10:55 AEST | 30011704-user5@smec.com | james.stone@smec.com | 583 | 7 O'Clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Grout delamination / Drummy concrete near CP on circular joint over an area of 100mm x 500mm. No structural implications. | [5 empty] | 2cfe3870-ee29-45e5-877c-11a971e83124 |  | https://web.fulcrumapp.com/photos/view?photos=2cfe3870-ee29-45e5-877c-11a971e83124 | Concrete | Circular Connection,Circular Joint | Drummy
7cf3b110-6226-4732-8e48-7ca35b582ca1 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 11 |  |  |  | 2025-07-27 15:43:58 AEST | 2025-07-29 09:55:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | 486 | 1 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The steel channel and anchor bolts are heavily corroded | [5 empty] | 1d5f3168-f56f-4c13-bd17-e8a0ff3bbd30 |  | https://web.fulcrumapp.com/photos/view?photos=1d5f3168-f56f-4c13-bd17-e8a0ff3bbd30 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
5a7519eb-635f-4bfe-b45c-797c31a520a4 | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 09309c02-2c9e-4aea-9ab5-b39f583cd12b | 11 |  |  |  | 2025-07-27 16:09:12 AEST | 2025-07-29 09:55:26 AEST | 30011704-user5@smec.com | james.stone@smec.com | 481 | 4 o’clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | KP |  | Drummy concrete with etched surface 200x200mm | [5 empty] | c34f231b-b153-4f9d-bb48-e5bb8756c6ac |  | https://web.fulcrumapp.com/photos/view?photos=c34f231b-b153-4f9d-bb48-e5bb8756c6ac | Concrete | Middle of Panel | Drummy |  | Middle of panel
911dd1cd-2db0-4de5-9553-0509258645c9 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:21:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 511 | 0 | Grout Injection Hole | Grout Injection Hole |  | 36755 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Environment |  | Environment | Chloride Induced |  | Chloride Induced | Severity Level 3. Substantial impact, ecosystem recovery takes >=1 but < 3 years |  | Severity Level 3. Substantial impact, ecosystem recovery takes >=1 but < 3 years | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 511, 2 & 12 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 22/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | There is no 2 o'clock injection hole. 12 o'clock injection hole leak is not active at the time of inspection. Steel plug in good condition. Low priority. | no | yes |  | no |  | e016402f-5c0b-40b6-853d-53a284cbdfce,f3c23e7e-b2df-4649-a4ac-4f819b87c85d | , | https://web.fulcrumapp.com/photos/view?photos=e016402f-5c0b-40b6-853d-53a284cbdfce%2Cf3c23e7e-b2df-4649-a4ac-4f819b87c85d | Steel | Grout Hole | Leaks |  | Not Reinforcement
f33a16bd-ff45-42b1-83f1-343bfa547d49 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:24:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 511 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26985 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 511, 8 O'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The grout hole is sealed by salt deposits. Not active at the time of inspection. The condition of the seal bolt is not known. | yes | yes |  | no |  | f138d6a1-4601-4bff-90b3-f8281ac1c2f4,2d9836dd-9fa8-4f71-957e-e883bf1b416d | , | https://web.fulcrumapp.com/photos/view?photos=f138d6a1-4601-4bff-90b3-f8281ac1c2f4%2C2d9836dd-9fa8-4f71-957e-e883bf1b416d | Concrete | Grout Hole | Leaks |  | Not Reinforcement
eec5bc4b-7497-40f8-aea4-0448ed229b91 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:22:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 511 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36754 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring: 511, 7 O'clock: Segment Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at segment bolted joints over an area of 200mm x 200mm. |  | Grout Delamination / debonding at segment bolted joints over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The defect condition has not changed. Superficial defect with no structural implication. | no | no |  | no |  | 599513c5-98f0-4946-8529-606dae0ae033 |  | https://web.fulcrumapp.com/photos/view?photos=599513c5-98f0-4946-8529-606dae0ae033 | Concrete | Radial Joint | Drummy |  | Not Reinforcement
69123bf7-7304-4aaa-883d-7ad748643e37 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:13:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 514 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36756 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.6088 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 514, 10, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel bracket has Level 1 corrosion up to 5% coverage. Steel channel support bracket anchor bolts have Level 1 Corrosion |  | Steel channel bracket has Level 1 corrosion up to 5% coverage. Steel channel support bracket anchor bolts have Level 1 Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The condition of the steel channel is the same as per previous inspection. | no | yes |  | no |  | 77901ef9-8bc4-49a4-9c2f-0156263a52e8,205b0cbf-1059-4664-9c6a-8b262e5394ef | , | https://web.fulcrumapp.com/photos/view?photos=77901ef9-8bc4-49a4-9c2f-0156263a52e8%2C205b0cbf-1059-4664-9c6a-8b262e5394ef | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
d3a5bea6-a56c-4c00-9009-a93fcf11ee38 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:39:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 514 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84070 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4611 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 514, 3 o'clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). |  | One channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | DR |  | Condition remains unchanged. Low priority defect. Priority to be reduced | no | no |  |  |  | 0f4628dc-c756-4820-b2df-3ef606901bac |  | https://web.fulcrumapp.com/photos/view?photos=0f4628dc-c756-4820-b2df-3ef606901bac | Concrete | Channel Bracket-Bolt | Missing
f3cea49e-0201-43de-aa15-31fb1cf1b2ed | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:25:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 516 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93653 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 516, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over two areas of the same size around 200mm x 400mm each. |  | Radial joint has grout Delamination / Drummy Grout over two areas of the same size around 200mm x 400mm each. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | DR |  | Condition remains unchanged. Delamination and drummy concrete still present at the radial joint. Location of defect is not at 4 O Clock but at 5 O Clock. Medium priority defect. | yes | no |  | yes | Location of defect must be updated. | 85b5d078-55d2-4620-a4e4-04becd55bcb8,e76b3104-d0c9-475b-a005-ad2b91e39e73,163057c7-6c0d-4bfe-ba5b-fe83a61499a5 | ,, | https://web.fulcrumapp.com/photos/view?photos=85b5d078-55d2-4620-a4e4-04becd55bcb8%2Ce76b3104-d0c9-475b-a005-ad2b91e39e73%2C163057c7-6c0d-4bfe-ba5b-fe83a61499a5 | Concrete | Radial Joint | Drummy
3a60f485-5f35-4f81-9f9c-26398d0ea994 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:33:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 517 | 1 | Grout Injection Hole | Grout Injection Hole |  | 36758 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 517, 1 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak remains inactive no change to condition. Priority to be changed to P2 | yes | no |  |  |  | 3833da5a-8221-4559-bb5a-65181885bf37 |  | https://web.fulcrumapp.com/photos/view?photos=3833da5a-8221-4559-bb5a-65181885bf37 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
cadf1eaa-8ed7-40a5-90f6-1832d6e8b4d6 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:13:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 517 | 8 | Grout Injection Hole | Grout Injection Hole |  | 84071 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 517, 8 o'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The condition of the defect has not changed. The leak is active at the time of inspection. Hole sealed by salt deposits. The condition of the seal bolt is not known. | no | yes |  | no |  | 3c73278f-a8b5-4b99-821c-e2ab2d6bbd2d,e2948b69-2bd7-4a29-9517-3712a49585dc,02f673b9-dd04-4fa9-bbc5-054891e7a864 | ,, | https://web.fulcrumapp.com/photos/view?photos=3c73278f-a8b5-4b99-821c-e2ab2d6bbd2d%2Ce2948b69-2bd7-4a29-9517-3712a49585dc%2C02f673b9-dd04-4fa9-bbc5-054891e7a864 | Concrete | Grout Hole | Leaks
ebee3af5-ddf3-4363-9cd4-1890a489b5ee | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:01:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 520 | 9 | Grout Injection Hole | Grout Injection Hole |  | 101797 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 518, 9 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The identified defect is on Ring 520. The leak is not active at the time of inspection. The hole appears to have been sealed. Salt deposits observed. Defect to be monitored. | yes | no |  | no |  | 5dda0774-5ff8-4870-8249-46c6e7be9076,3464c5f8-6233-4461-ba36-4ae5bb92f3ed | , | https://web.fulcrumapp.com/photos/view?photos=5dda0774-5ff8-4870-8249-46c6e7be9076%2C3464c5f8-6233-4461-ba36-4ae5bb92f3ed | Concrete | Grout Hole | Leaks |  | Not Reinforcement
07129a47-bea8-43e9-b3e7-4bfc8d55a0ab | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:31:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 519 | 1 | Grout Injection Hole | Grout Injection Hole |  | 36760 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Severity Level 2 |  | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 519, 1 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak remains inactive at time of inspection. | no | yes |  | no |  | b8dc72b0-5248-4a44-aec3-95ce3683b050 |  | https://web.fulcrumapp.com/photos/view?photos=b8dc72b0-5248-4a44-aec3-95ce3683b050 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
6713631d-1b16-4ba3-afec-69ade51b4d1b | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:08:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 519 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36759 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 519, 11 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection. The plug bolt is in good condition. | yes | no |  | no |  | f37ee0a6-64f2-4584-a95f-03218038a558,e41223e8-80b0-426d-bd4b-ccc96b7026e9 | , | https://web.fulcrumapp.com/photos/view?photos=f37ee0a6-64f2-4584-a95f-03218038a558%2Ce41223e8-80b0-426d-bd4b-ccc96b7026e9 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
9da1f90b-b505-452d-bdf0-f829ccc5ab82 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:06:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 519 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84072 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 519, 12 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The defect condition as per previous inspection. Defect is not considered structural. Low priority. | no | no |  | no |  | 54bb646b-a211-47fa-a350-b845f0320257 |  | https://web.fulcrumapp.com/photos/view?photos=54bb646b-a211-47fa-a350-b845f0320257 | Concrete | Radial Joint | Drummy
7ad85d8c-427c-44ac-ba7c-73d758266e0d | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 22:16:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 520 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93654 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 520, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 250mm x 300mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 250mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Condition remains unchanged. Drummy concrete still present at the same size. | no | yes |  | no |  | b06af977-46de-4128-86f5-d5202b72f730,2f2d8212-864d-43af-b8d8-4a54f5924c7f | , | https://web.fulcrumapp.com/photos/view?photos=b06af977-46de-4128-86f5-d5202b72f730%2C2f2d8212-864d-43af-b8d8-4a54f5924c7f | Concrete | Radial Joint | Drummy
47c11975-42d8-4354-b20a-53aa4422eb0f | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:10:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 521 | 1 | Grout Injection Hole | Grout Injection Hole |  | 36761 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 521, 1 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | DR |  | Condition remains unchanged. Leak is still inactive at time of inspection. Low priority. | no | yes |  | no |  | 05a50ee1-0d24-4c28-9edd-05a940db95dc |  | https://web.fulcrumapp.com/photos/view?photos=05a50ee1-0d24-4c28-9edd-05a940db95dc | Concrete | Grout Hole | Leaks |  | Not Reinforcement
164d7424-4cd7-4d60-970e-b4ad3e0c28e8 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 05:51:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 521 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93655 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 521, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | Defect in the same condition as per previous inspection. Structural capacity not affected. Low priority defect. | no | no |  | no |  | 8b3cf771-4b69-4fab-bbed-63c92c61db01,efb50eef-aae9-4859-a558-28a8ebc9ffca | , | https://web.fulcrumapp.com/photos/view?photos=8b3cf771-4b69-4fab-bbed-63c92c61db01%2Cefb50eef-aae9-4859-a558-28a8ebc9ffca | Concrete | Radial Joint | Drummy
b497697a-7787-436c-983c-ad1a2c14fbf2 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 05:48:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 522 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36762 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.6157 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 522, 11 to 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion. Steel channel support bracket is missing one bolt at 1 O'clock. Channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion. Steel channel support bracket is missing one bolt at 1 O'clock. Channel anchor bolts have Level 2 corrosion. | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | Condition as per previous inspection. Concentrate corrosion at pre drilled holes in the steel channel. Not affecting the structural capacity. Low priority | no | yes |  | no |  | a666dbcf-94f1-4ad8-a9d3-777604b30317,40611876-57ee-40a5-8edd-79a2fa034e1b,d9717fcc-fb24-4462-a912-3c38dc181916 | ,, | https://web.fulcrumapp.com/photos/view?photos=a666dbcf-94f1-4ad8-a9d3-777604b30317%2C40611876-57ee-40a5-8edd-79a2fa034e1b%2Cd9717fcc-fb24-4462-a912-3c38dc181916 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
d4ca2867-dae0-4c1b-8390-8e437051f288 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:06:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 522 | 4 | Grout Injection Hole | Grout Injection Hole |  | 69373 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 22/12/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | 2 |  | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 522, 4 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | Dr |  | Leak is inactive at time of inspection. Repair seems to have been carried out. Location incorrect - leak at is previously noted only at 11 O clock and not 4 O clock. | yes | no |  | yes | Severity and condition to be reduced. Location to be changed. | 51c2d5a5-18ea-4d65-b194-1a1a717136d2,aefbdcc1-7048-47de-903f-67c3229f1b41 | , | https://web.fulcrumapp.com/photos/view?photos=51c2d5a5-18ea-4d65-b194-1a1a717136d2%2Caefbdcc1-7048-47de-903f-67c3229f1b41 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
0050bad4-0aa3-4a9a-9ef1-e3883aee8189 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 22:00:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 524 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26990 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 524, 1 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects | No | Off-Line | Yes | Scaffolding | Working at Heights | Standard Repair Detail Competent Supervisor | Dr |  | Severe active leak still present with salt deposits from the grout injection hole to 2 O. Clock. Causing major corrosion | no | yes |  | no |  | a382b70f-09f4-4da4-b2f8-24a6dfb8c038,19ea13f8-6100-4eda-9838-ae0520c84b6a | , | https://web.fulcrumapp.com/photos/view?photos=a382b70f-09f4-4da4-b2f8-24a6dfb8c038%2C19ea13f8-6100-4eda-9838-ae0520c84b6a | Concrete | Grout Hole | Leaks |  | Not Reinforcement
95905f07-1297-4cab-9dfa-c67e02dfcb26 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 03:41:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 524 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27299 |  | 8714 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 524, 2 & 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 to 5 corrosion. Steel channel support bracket anchor bolts have Level 4 corrosion. |  | Steel channel support bracket has Level 4 to 5 corrosion. Steel channel support bracket anchor bolts have Level 4 corrosion. | Loss of services |  | Loss of services | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services | Priority: P3 |  |  |  | Replace corroded channel bracket and anchor bolts. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | Dr |  | Corrosion has advanced corrosion has extended or further to the steel panel in front. Caused by severe leak. | yes | no | High priority | no |  | 9c26dd09-13fa-43f4-88a7-692b7fe9888e,208e637a-6b19-42bc-93a3-fcd2d3bac6cc,c537fa4a-7853-4069-a88b-6734aa720176,b22e3043-b6d6-41ca-aae2-e623625370b2 | ,,, | https://web.fulcrumapp.com/photos/view?photos=9c26dd09-13fa-43f4-88a7-692b7fe9888e%2C208e637a-6b19-42bc-93a3-fcd2d3bac6cc%2Cc537fa4a-7853-4069-a88b-6734aa720176%2Cb22e3043-b6d6-41ca-aae2-e623625370b2 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Leaks
2ef587db-1b03-4539-b340-27e94101794f | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 05:46:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 526 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 69374 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.3555 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 526, 11 to 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolt have level 2 corrosion. Channel anchor bolts are missing at 5 locations. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolt have level 2 corrosion. Channel anchor bolts are missing at 5 locations. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | Steel channel corrosion has advanced around the pre drilled holes. Low priority defect. | yes | yes |  | no |  | 33f82413-3b41-48de-9e6a-d18132692188,ea3a4c4d-8568-4e83-bacf-9330f340c913 | , | https://web.fulcrumapp.com/photos/view?photos=33f82413-3b41-48de-9e6a-d18132692188%2Cea3a4c4d-8568-4e83-bacf-9330f340c913 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
c7084ee7-cf3e-4843-8ad5-e31876fa0609 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 21:51:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 526 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84073 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4659 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 1 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 526, 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Corrosion. Steel channel support bracket has Level 2 Corrosion up to 5% coverage. |  | Channel anchor bolts have Level 2 Corrosion. Steel channel support bracket has Level 2 Corrosion up to 5% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Corrosion of steel bracket is present, however not to the severity of Level 2 corrosion. Severity level 1 and condition level 2 | yes | no |  |  |  | 770bfb51-114a-411a-91d8-c4c9e2ecbd4a,4c49c77a-858b-4b84-927f-7ee33cba7807,fe5256d0-faaa-4608-8ffc-a97c373322c1 | ,, | https://web.fulcrumapp.com/photos/view?photos=770bfb51-114a-411a-91d8-c4c9e2ecbd4a%2C4c49c77a-858b-4b84-927f-7ee33cba7807%2Cfe5256d0-faaa-4608-8ffc-a97c373322c1 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
b1a090bc-caba-4143-b0a2-48179f5709da | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 03:17:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 526 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69375 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 526, 4 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints at two locations. Each grout patch size is 200mm x 200mm. |  | Grout Delamination / debonding at circle segment bolted joints at two locations. Each grout patch size is 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | Defect is still present at the radial joint. Concrete spalling and cracking. Medium priority | no | no |  | yes |  | 2985edae-a663-437e-b1af-2b2f93534bb7,71eb524a-f415-4c86-9865-83c2cc09a8b9 | , | https://web.fulcrumapp.com/photos/view?photos=2985edae-a663-437e-b1af-2b2f93534bb7%2C71eb524a-f415-4c86-9865-83c2cc09a8b9 | Concrete | Circular Joint,Radial Joint | Crack,Drummy,Surface Damage
e6e28df1-eaef-4bbe-a023-9fe85451858e | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 05:39:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 526 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36763 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 526, 9 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - active at time of inspection. |  | Grout injection hole has Leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | Leak not active at the time of inspection. The grout hole is sealed. The condition of the plug bolt is not known. Low priority repair. | yes | no |  | yes | Check with Tunnel engineer | 4b9e6109-e082-471d-af9c-b6c8e67b05c1,e0ba5cd6-547a-491f-b028-15192b0bbedc,ec6eb040-c2f5-412d-b3f5-fcb5c8f7627e | ,, | https://web.fulcrumapp.com/photos/view?photos=4b9e6109-e082-471d-af9c-b6c8e67b05c1%2Ce0ba5cd6-547a-491f-b028-15192b0bbedc%2Cec6eb040-c2f5-412d-b3f5-fcb5c8f7627e | Concrete | Grout Hole | Leaks |  | Not Reinforcement
b7d62bc9-b535-4582-90d6-17c7f651069c | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 21:42:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 528 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 101776 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 45553.5802 |  |  | No | Missing |  |  |  | 1 | [8 empty] | Severity Level 2 | Severity Level 1 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 528, 2 O'clock, Steel Channel Bracket and Anchor Bolts |  |  |  | Steel channel support bracket has wide spread Level 1 corrosion at 3 o'clock. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has wide spread Level 1 corrosion at 3 o'clock. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Very minor corrosion observed. Not as severe as mentioned in the previous inspections. | no |  |  |  |  | 32185605-4729-454e-98a9-832843203a14 |  | https://web.fulcrumapp.com/photos/view?photos=32185605-4729-454e-98a9-832843203a14 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
4e0e9c50-f33a-408f-89ca-22c4392a82b0 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 21:53:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 529 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101798 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 529, 4 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | Condition remains unchanged. Drummy concrete is still present at the specified location. | no | yes |  | no |  | d7e61fcd-086d-4162-9237-e96f93ecf830,e713080f-5526-41fc-b428-afbe6d11afe5,4416ac2c-204a-4647-814a-b49d7d541527 | ,, | https://web.fulcrumapp.com/photos/view?photos=d7e61fcd-086d-4162-9237-e96f93ecf830%2Ce713080f-5526-41fc-b428-afbe6d11afe5%2C4416ac2c-204a-4647-814a-b49d7d541527 | Concrete | Circular Joint | Drummy
a16c791c-0ff2-4a2e-bd73-8dda029cb3f1 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 07:16:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 530 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26992 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing |  |  |  | 1 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 530, 11 to 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Steel channel anchor bolt have Level 2 corrosion. Missing bolt at 11 O'Clock. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Steel channel anchor bolt have Level 2 corrosion. Missing bolt at 11 O'Clock. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Minor corrosion has been observed, contrary to previous inspection. | yes |  |  |  |  | d391a3b3-ced9-4a1d-8a68-28e2a707832b |  | https://web.fulcrumapp.com/photos/view?photos=d391a3b3-ced9-4a1d-8a68-28e2a707832b | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
0ca38715-4059-49bf-be73-85dedf292dc0 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 07:15:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 530 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 84074 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4675 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 530, 2 & 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 corrosion . |  | Channel anchor bolts have Level 2 corrosion . | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Corrosion is present, however not Level 2. Condition rating to be reduced to 2. | no |  |  |  |  | 5c8b26c5-9799-41c7-a6b6-9d6d6245328f,6ba267e8-06ec-4109-b7cf-ca4ffe31dbb8,512dbf06-62a2-459e-b3c2-f695ef37ab84 | ,, | https://web.fulcrumapp.com/photos/view?photos=5c8b26c5-9799-41c7-a6b6-9d6d6245328f%2C6ba267e8-06ec-4109-b7cf-ca4ffe31dbb8%2C512dbf06-62a2-459e-b3c2-f695ef37ab84 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
ed9b19b8-e824-450f-9f3f-3f0f7116cba0 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 07:09:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 531 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36765 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | 1 |  | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 531, 2 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak has been repaired and remains inactive at the time of inspection. Current condition has been updated. | yes |  |  |  |  | 291f3878-0726-4eae-b573-19c9d5b68926 |  | https://web.fulcrumapp.com/photos/view?photos=291f3878-0726-4eae-b573-19c9d5b68926 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
a2b67c4a-a130-4424-aad9-770b9186f517 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 | -20.318 | 118.5774 | POINT (118.5774377 -20.3179829) | 2025-05-27 20:13:18 AEST | 2025-07-31 00:52:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 532 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36766 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 532, 12 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is active at time of inspection with salt deposits collected from the grout injection hole. Severe corrosion present on steel bracket and on pipe below. Grid mesh on walkway has been replaced during the shit due to severe corrosion. High priority defect. | yes | no | High | no |  | be4afb89-b0db-4375-9612-9d0ed0e9823e,00debf6a-03ef-4e51-b725-7818096e2170,a898d8ae-ffd3-459e-8256-99fcd18db57a,cc507814-2682-4353-87f7-1e1726041949 | ,,, | https://web.fulcrumapp.com/photos/view?photos=be4afb89-b0db-4375-9612-9d0ed0e9823e%2C00debf6a-03ef-4e51-b725-7818096e2170%2Ca898d8ae-ffd3-459e-8256-99fcd18db57a%2Ccc507814-2682-4353-87f7-1e1726041949 | Steel | Grout Hole,Misc (Pipes/Cable Tray/etc),Reinforcement | Corrosion-Heavy,Leaks
deeca34b-cba7-412e-882d-ce37adb1b588 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 03:50:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 532 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84075 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 532, 4 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The defect is in the same condition and not considered structural. | no | no |  | no |  | 6893f655-d95f-48fa-b19d-1e09d61aa0f5,f6f5a66c-26f5-4807-83b9-c26bb69fd2a1 | , | https://web.fulcrumapp.com/photos/view?photos=6893f655-d95f-48fa-b19d-1e09d61aa0f5%2Cf6f5a66c-26f5-4807-83b9-c26bb69fd2a1 | Concrete | Circular Joint | Drummy
9b25a666-9539-440d-b5df-592ab47bf78f | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 23:52:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 533 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36767 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 533, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The leak is not active at the time of inspection.No further damage noted. Low priority - Monitoring | no | no |  | no |  | 2b1c02c2-68fb-4db6-a379-a5bfc537c4f8 |  | https://web.fulcrumapp.com/photos/view?photos=2b1c02c2-68fb-4db6-a379-a5bfc537c4f8 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
4182279d-0ec5-420b-a481-cc88fb98b924 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 03:48:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 533 | 8 | Grout Injection Hole | Grout Injection Hole |  | 84076 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 533, 8 o'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | Leak not active at the time of inspection. Injection hole sealed by salt deposits. Condition of steel plug not known. | yes | yes |  | no |  | 79f44103-0055-4b38-8974-c7e84c6de8ed,a82762ba-4976-4114-bb0a-b2c202debe59 | , | https://web.fulcrumapp.com/photos/view?photos=79f44103-0055-4b38-8974-c7e84c6de8ed%2Ca82762ba-4976-4114-bb0a-b2c202debe59 | Steel | Grout Hole | Leaks
44c073a0-0dd7-4674-9367-bf878bb3c458 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 01:46:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 534 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27579 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing |  |  |  | 2 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 534, 1 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 3 Corrosion. |  | Steel channel support bracket anchor bolts have Level 3 Corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | Steel Chanel is heavenly corroded with the anchor bolts nuts fully corroded. Active water leak at the injection hole has accelerated the corrosion process. The light bracket is also affected. Urgent repairs are required. | yes | yes |  | no |  | 587b6b79-8c6c-457c-97dd-ceeb58269681,f6ef397c-8000-49db-91ae-83ac4da14312,3f7a4dbc-ce38-4cdc-b2cd-61aaba07bf9f,aee439e4-fc3a-44b6-a5ef-39bd72e2b385,9a949e5b-515a-4daf-9497-5e9b03c1cc78,3a453ba1-131b-4525-a882-9d58d45d31ae,6e065ccb-0ef7-4258-91e3-dd425ea55653,2a86d350-421a-4a61-995c-8d8f534f10e0 | ,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=587b6b79-8c6c-457c-97dd-ceeb58269681%2Cf6ef397c-8000-49db-91ae-83ac4da14312%2C3f7a4dbc-ce38-4cdc-b2cd-61aaba07bf9f%2Caee439e4-fc3a-44b6-a5ef-39bd72e2b385%2C9a949e5b-515a-4daf-9497-5e9b03c1cc78%2C3a453ba1-131b-4525-a882-9d58d45d31ae%2C6e065ccb-0ef7-4258-91e3-dd425ea55653%2C2a86d350-421a-4a61-995c-8d8f534f10e0 | Steel | Channel Bracket,Channel Bracket-Bolt,Grout Hole,Misc (Pipes/Cable Tray/etc) | Leaks |  | Misc as well
915049f7-8c3b-4f5f-ace2-806585809d3a | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 01:52:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 534 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84077 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 534, 1 to 12 o'clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Active leak shall be assessed as P2 as discussed with BHP AIMS. | Not Specified | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | Leak active with collateral damage as steel channel, light fixture, water pipe and its support, walkway grating. Leak repair and steel components repair and/or replacement required urgent. | no | yes |  | no |  | 71f5712c-eb5a-4802-9216-419f87af7a2e,a1a95f24-b5d0-4cc9-8e5d-ad5ced0171e1,63bbc5b7-41aa-4c1c-a572-78bb094bf3d7,d2f282dd-2671-4467-999a-39f5af0930f1,b824194b-7707-4f10-aa3f-7a5a6fb02988,fb06090f-be9d-434f-8b85-b1993ab33005 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=71f5712c-eb5a-4802-9216-419f87af7a2e%2Ca1a95f24-b5d0-4cc9-8e5d-ad5ced0171e1%2C63bbc5b7-41aa-4c1c-a572-78bb094bf3d7%2Cd2f282dd-2671-4467-999a-39f5af0930f1%2Cb824194b-7707-4f10-aa3f-7a5a6fb02988%2Cfb06090f-be9d-434f-8b85-b1993ab33005 | Concrete,Steel | Misc (Pipes/Cable Tray/etc) | Leaks
213afb1b-7abf-48b7-941a-543839d70ab5 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-30 02:14:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 534 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 101777 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 45553.5809 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 534, 2 O'clock, Steel Channel Bracket and Anchor Bolts |  |  |  | Steel channel support bracket has Level 1 corrosion around the anchor bolts. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion around the anchor bolts. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Severe level 5 corrosion due to leak. High priority | yes | no | High |  |  | 879e381a-27ae-4e14-bdc3-748ea3f11f1e,a2487185-90f8-4a29-8515-2c831d79021b | , | https://web.fulcrumapp.com/photos/view?photos=879e381a-27ae-4e14-bdc3-748ea3f11f1e%2Ca2487185-90f8-4a29-8515-2c831d79021b | Steel | Channel Bracket,Channel Bracket-Bolt | Leaks,Corrosion-Heavy |  | Corrosion heavy
ab8a65f9-5fa2-4222-a2c3-e8898f54b634 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 23:04:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 535 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36778 |  | 8516 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 23/06/2023 |  | 24/10/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 535, 12 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | Dr |  | No change to condition. Leak is still inactive at time of inspection. | no | yes |  | no |  | 17185102-1f30-462a-a866-4611783b771d |  | https://web.fulcrumapp.com/photos/view?photos=17185102-1f30-462a-a866-4611783b771d | Concrete | Grout Hole | Leaks |  | Not Reinforcement
9414b49b-83d2-43a0-9099-3e8474aa40b6 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 03:44:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 535 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84079 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 535, 7 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | No further deterioration noted. Defect not considered structural. | no | no |  | no |  | d7f77cad-6458-40d6-94e7-f8a91a99e9a8,d42f1244-6a65-4154-ae2a-ee8432164359 | , | https://web.fulcrumapp.com/photos/view?photos=d7f77cad-6458-40d6-94e7-f8a91a99e9a8%2Cd42f1244-6a65-4154-ae2a-ee8432164359 | Concrete | Circular Joint | Drummy
ba8281d4-a58b-4e39-bf76-8aeb8baa4f8b | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:49:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 537 | 2 | Grout Injection Hole | Grout Injection Hole |  | 36779 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 537, 2 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | Dr |  | Condition remains unchanged. Leak inactive at time of inspection. | no |  |  |  |  | 80a096f0-c40a-426a-b3a7-2177a47c6b6a |  | https://web.fulcrumapp.com/photos/view?photos=80a096f0-c40a-426a-b3a7-2177a47c6b6a | Concrete | Grout Hole | Leaks |  | Not Reinforcement
ace90406-422e-4783-85a2-502533849961 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 23:41:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 538 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 26995 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing |  |  |  | 1 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 538, 11 o'clock, Steel Channel Support Bracket |  |  |  | Channel Support Bracket has level 2 low corrosion |  | Channel Support Bracket has level 2 low corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | Corrosion does not appear to advance. | no | yes |  | no |  | 4dcfd7a8-1a06-4a75-9477-2994d95cb8ef,0b6e3fb3-950f-4337-a70d-ed0b2ea3b3f3,2cbdf808-ee85-4d40-957b-55b18a597c58 | ,, | https://web.fulcrumapp.com/photos/view?photos=4dcfd7a8-1a06-4a75-9477-2994d95cb8ef%2C0b6e3fb3-950f-4337-a70d-ed0b2ea3b3f3%2C2cbdf808-ee85-4d40-957b-55b18a597c58 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
1aefe787-5950-4bbd-910e-08bd2b527775 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 17 | -20.3218 | 118.5847 | POINT (118.5846567 -20.3218117) | 2025-05-27 20:13:18 AEST | 2025-07-25 01:40:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 539 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84081 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 539, 12 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The defect has not advanced. The defect is cosmetic not structural with low priority. | no | no |  | yes | Check with Tunnel engineer | cf9eaef1-3789-450c-8e4d-618571fecf3b |  | https://web.fulcrumapp.com/photos/view?photos=cf9eaef1-3789-450c-8e4d-618571fecf3b | Concrete | Radial Joint | Drummy
98968752-32a7-401c-8cb7-e3dbb11fa7f0 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 13 |  |  |  | 2025-07-25 06:58:14 AEST | 2025-07-25 07:02:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 534 | 1 O'Clock |  | Steel Channel Bracket | [16 empty] | Active leak | 3 |  |  |  | Health & Safety |  |  |  | Active sea water leak through grout injection hole on the steel bracket |  | Severity Level 3 |  |  | Likely (Failure within 2 Years) | [9 empty] | Leaks through tunnel liner, leading to accelerated concrete damage locally | [8 empty] | Repair of leak at grout injection hole and replacement of steel bracket. | [7 empty] | Dr |  | Active sea water leak through grout injection hole. Causing a deposit of salt to be formed in the steel bracket and onto the pipe below it. Excessive corrosion is observed on the platform below due to seepage of water. |  | yes |  |  |  | 88276af4-9064-45c4-a32d-84a4fac371e4,e0ede327-5f91-437f-bf9c-fc3695daf96e,685db193-0aab-46bd-9e7c-58a8fff7ce3d | ,, | https://web.fulcrumapp.com/photos/view?photos=88276af4-9064-45c4-a32d-84a4fac371e4%2Ce0ede327-5f91-437f-bf9c-fc3695daf96e%2C685db193-0aab-46bd-9e7c-58a8fff7ce3d | Steel | Channel Bracket,Grout Hole,Misc (Pipes/Cable Tray/etc) | Leaks,Corrosion-Heavy |  | Corrosion HEavy
04c363db-fcc0-4db9-b57d-5b64bb04aae1 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 13 |  |  |  | 2025-07-25 07:07:16 AEST | 2025-07-25 07:08:08 AEST | 30011704-user5@smec.com | james.stone@smec.com | 532 | 1 O'Clock |  | Hydrophilic Joint Seal (Circle Joint) | [17 empty] | 2 | [39 empty] | Dr |  | Drumminess observed at patchwork on the circumferential joint. | [5 empty] | b36e879a-42ce-44f9-a8e0-da42ea701eb4 |  | https://web.fulcrumapp.com/photos/view?photos=b36e879a-42ce-44f9-a8e0-da42ea701eb4 | Concrete | Circular Connection,Circular Joint | Drummy
6bfc9ebe-c041-41ae-9ed9-5201da839565 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 13 |  |  |  | 2025-07-25 07:11:15 AEST | 2025-07-25 07:12:27 AEST | 30011704-user5@smec.com | james.stone@smec.com | 531 | 2 O'Clock |  | Grout Injection Hole | [17 empty] | 2 | [39 empty] | Dr |  | Drumminess observed above grout injection hole which previously contained an active leak. | [5 empty] | 51da5014-384e-416c-b3f5-347fefd13a15 |  | https://web.fulcrumapp.com/photos/view?photos=51da5014-384e-416c-b3f5-347fefd13a15 | Concrete | Grout Hole | Drummy,Leaks
ea50c178-407c-4e74-90d0-7785e72ac9e5 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 13 |  |  |  | 2025-07-25 07:27:44 AEST | 2025-07-25 07:28:50 AEST | 30011704-user5@smec.com | james.stone@smec.com | 528 | 2 O'Clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | Dr |  | Drumminess 100*100 observed at this circumferential joint | [5 empty] | cc4b5abf-f394-4e0a-97a5-87f227d86d97 |  | https://web.fulcrumapp.com/photos/view?photos=cc4b5abf-f394-4e0a-97a5-87f227d86d97 | Concrete | Circular Connection,Circular Joint | Drummy
db48871b-4f57-4d02-a912-1d9fccfd452a | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 10 |  |  |  | 2025-07-25 21:58:33 AEST | 2025-07-25 22:01:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 527 | 7 o'clock |  | Segment Bolted Joint (Circle Joint) | [37 empty] | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | [19 empty] | Bogdan Stanca |  | Drummy grout at the circular joint. Low priority |  |  |  | no |  | 823c4cbc-b192-443f-8345-bd55eb0848e4 |  | https://web.fulcrumapp.com/photos/view?photos=823c4cbc-b192-443f-8345-bd55eb0848e4 | Concrete | Circular Connection,Circular Joint | Drummy
90fd64ec-a31e-4b72-8ade-da6ed7ccb5c9 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 11 |  |  |  | 2025-07-25 22:29:11 AEST | 2025-07-25 22:30:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 519 | 2 O' Clock |  | Segment Bolted Joint (Circle Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 2 | [39 empty] | Dr |  | Drumminess of concrete present at circumferential joint. |  | yes |  | no |  | 991dbbaf-20d4-42ac-8e85-bee0a9b53ccc |  | https://web.fulcrumapp.com/photos/view?photos=991dbbaf-20d4-42ac-8e85-bee0a9b53ccc | Concrete | Circular Connection,Circular Joint | Drummy
d26a3809-6f30-4627-9ef7-e9a29840100c | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 11 |  |  |  | 2025-07-25 22:41:42 AEST | 2025-07-25 22:43:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | 512 | 3 o clock |  | Steel Channel Bracket | [17 empty] | 1 | [9 empty] | Severity Level 1 | [29 empty] | Dr |  | Minor corrosion and chipping of bolt holes on the steel bracket. Low priority defect. |  | yes |  | no |  | 3b501969-13bb-423d-bd4a-654d9fd303e3 |  | https://web.fulcrumapp.com/photos/view?photos=3b501969-13bb-423d-bd4a-654d9fd303e3 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
b6b7bb41-23bd-44c9-aefd-8485c406b7b8 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 9 |  |  |  | 2025-07-26 16:38:46 AEST | 2025-07-26 16:39:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 455 | 7 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Close to circular joint. Size 120x120mm. Priority low | [5 empty] | 5fc9c5b5-d866-4c1f-8d15-19d99a7ca674 |  | https://web.fulcrumapp.com/photos/view?photos=5fc9c5b5-d866-4c1f-8d15-19d99a7ca674 | Concrete | Radial Joint |  |  | Radial Joint
245678aa-4965-4eb5-b3ae-a7a5e5a92d66 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 8 |  |  |  | 2025-07-28 22:25:53 AEST | 2025-07-28 22:27:21 AEST | 30011704-user5@smec.com | james.stone@smec.com | 516 | 5 O Clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | Dr |  | Drummy and delaminated concrete at area 300X300mm. Medium priority |  | yes |  |  |  | 1a99e449-d6e4-4080-9435-35f16c9fb362,e38623d0-b673-4127-a69a-f6429186fb47 | , | https://web.fulcrumapp.com/photos/view?photos=1a99e449-d6e4-4080-9435-35f16c9fb362%2Ce38623d0-b673-4127-a69a-f6429186fb47 | Concrete | Circular Joint | Drummy
858a63dc-8fe0-428c-8c0f-140ba7d3d777 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | c9ea2c15-0ed7-4087-aec4-bba00101f9d3 | 5 |  |  |  | 2025-07-30 02:14:34 AEST | 2025-07-30 02:15:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 534 | 2 and 3 | [17 empty] | Corrosion of Reinforcement | [41 empty] | Dr |  | Severe corrosion on bracket and anchor bolts. High priority |  | yes |  |  |  | 01d8bc26-426e-4e0b-9a9f-c9d5e8af22c0,06ff63bc-1d68-42ac-9ee8-b7b41ca5fbec,7146caf4-d3d7-4708-9c12-d5472ba6f501,eff3eb9a-a890-4cd3-a24d-a58efb5b893d,11b026bb-32a4-43c1-8ada-4f3f497c7e6c | ,,,, | https://web.fulcrumapp.com/photos/view?photos=01d8bc26-426e-4e0b-9a9f-c9d5e8af22c0%2C06ff63bc-1d68-42ac-9ee8-b7b41ca5fbec%2C7146caf4-d3d7-4708-9c12-d5472ba6f501%2Ceff3eb9a-a890-4cd3-a24d-a58efb5b893d%2C11b026bb-32a4-43c1-8ada-4f3f497c7e6c | Concrete |  | Corrosion-Heavy |  | Not Reinforcement
1cffd234-5bd3-4636-bab3-fbb71ff9a404 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3742 | 118.6339 | POINT (118.6338949 -20.3741854) | 2025-05-27 20:13:18 AEST | 2025-07-29 00:14:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 542 | 12 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 101800 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 45553.623 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 542, 12 O'clock |  |  |  | 0.25mm crack within the radial segment bolted joint grout. |  | 0.25mm crack within the radial segment bolted joint grout. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The defect did not advance. Cosmetic defect with no structural implications. | no | no |  | yes | Confirmation with Tunnel engineer the construction methodology and design intent for the segment joints. | 3da9c3fd-ab5a-4917-a811-5a4cab262fa5 |  | https://web.fulcrumapp.com/photos/view?photos=3da9c3fd-ab5a-4917-a811-5a4cab262fa5 | Concrete | Radial Joint | Crack
d1d258f0-f613-43d2-9a4d-ca564e7a49bd | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:38:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 542 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84082 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4791 |  |  | No | Missing |  |  |  | 2 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 542, 3 o'Clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). |  | One channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | Dr |  | Condition remains unchanged. Bolts are still missing | no |  |  |  |  | be10bd77-e276-43b4-afad-3d361d2f8b75 |  | https://web.fulcrumapp.com/photos/view?photos=be10bd77-e276-43b4-afad-3d361d2f8b75 | Concrete | Channel Bracket-Bolt | Missing
da7d2b15-cca0-4410-b09f-b090fb871785 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 23:19:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 543 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 84080 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 44859.476 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 543, 11 o'clock, Grout Injection Hole |  |  |  | Minor concrete spalling at the corner of concrete shell. |  | Minor concrete spalling at the corner of concrete shell. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Bogdan Stanca |  | The sealing bolt is heavily corroded. It does not appear that the stainless steel bolt has been used. Replacement of bolt with a SS bolt is advisable. Medium priority white is still enough head to remove the bolt.Slight humidity around the bolt head noted. | yes | yes |  | yes | Confirmation with Tunnel engineer is required for replacement methodology. | 305c1b3c-e92d-4723-abb1-43ddafc2d314,32fc599e-94cb-45b2-8450-0bae5e271c91,95d130b4-41c1-49cc-9878-2dcef40daf11 | ,Bolt head Ring 543 11 o'clock ,Bolt head at Ring 544 11 o'clock | https://web.fulcrumapp.com/photos/view?photos=305c1b3c-e92d-4723-abb1-43ddafc2d314%2C32fc599e-94cb-45b2-8450-0bae5e271c91%2C95d130b4-41c1-49cc-9878-2dcef40daf11 | Concrete,Steel | Grout Hole | Surface Damage |  | Not corner
f5ed45f2-ed81-4b97-81e1-52cb2cb471dc | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 23:09:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 544 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36780 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 543, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | Defect location not correct. Should be 544. The leak was not active at the time of inspection and didn't expand from the last inspection. Risk of failure low. Monitoring is required typically for this type of defect. | no | no |  | no |  | 032b0786-0786-4d90-b9c5-242bb24f60da |  | https://web.fulcrumapp.com/photos/view?photos=032b0786-0786-4d90-b9c5-242bb24f60da | Concrete | Grout Hole | Leaks |  | Not reinforcement
22074b0e-68ce-47b3-b8a6-0a04903eb3a5 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:31:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 544 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84084 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.481 |  |  | No | Missing |  |  |  | 1 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 544, 3 o'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion up to 50% coverage. |  | Steel channel support bracket has Level 2 Minor Corrosion up to 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | DR |  | Not corroded up to 50%. Minor corrosion is observe | yes |  |  |  |  | e2e4e35c-a63e-4a96-b6f6-27535c0d0108,ce080088-b60b-49db-9c32-fdcc8677eb4f | , | https://web.fulcrumapp.com/photos/view?photos=e2e4e35c-a63e-4a96-b6f6-27535c0d0108%2Cce080088-b60b-49db-9c32-fdcc8677eb4f | Steel | Channel Bracket | Corrosion-Surface
8ef87280-384a-420c-8ed9-60e7671010af | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 03:34:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 544 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27586 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 544, 7 o'clock, Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 500mm x 250mm. |  | Concrete shell segment has drummy concrete over an area of 500mm x 250mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Remediate concrete as per BHP Standards and specifications | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | Bogdan Stanca |  | The area affected has lost the concrete cover, especially near the circular joint. No reinforcement visible and concrete beneath is sound. Low priority repair. | yes | no |  | no |  | ca1158b6-a85a-400b-af51-594bf6f5ddec,816ff37d-7fc8-448b-9419-64e825b8c36c,13973486-4636-47c4-acb2-72b42f808f17 | ,, | https://web.fulcrumapp.com/photos/view?photos=ca1158b6-a85a-400b-af51-594bf6f5ddec%2C816ff37d-7fc8-448b-9419-64e825b8c36c%2C13973486-4636-47c4-acb2-72b42f808f17 | Concrete | Circular Connection,Circular Joint | Drummy,Missing |  | Not Reinforcement
4c0f4e20-2cd3-4fc5-ba8f-e1a500e8a603 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-26 21:25:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 546 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84086 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4825 |  |  | No | Missing |  | Corrosion - Connection |  | 2 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 546, 3 o'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion up to 50% coverage. |  | Steel channel support bracket has Level 2 Minor Corrosion up to 50% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Minor surface corrosion. Not 50% like specified in previous inspection report. Low priority repair | yes |  |  |  |  | 75aa6f59-2dbf-4c81-8530-c4c9459cf994 |  | https://web.fulcrumapp.com/photos/view?photos=75aa6f59-2dbf-4c81-8530-c4c9459cf994 | Steel | Channel Bracket | Corrosion-Surface
eb6b5018-881d-49fa-bd68-98ba9180ac44 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 03:23:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 547 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69376 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 547, 7 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Component should be "Segmented Bolted Joint (Circle Joint)". Adopted default consequence Financial - Level 3. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | No change from the last installation. The defect is not considered structural. Low priority | no | no |  | no |  | 7fcaf0b9-9fa1-4d29-a9a6-9b487d179706,fd0c99fb-782f-4786-be49-730154276f85 | , | https://web.fulcrumapp.com/photos/view?photos=7fcaf0b9-9fa1-4d29-a9a6-9b487d179706%2Cfd0c99fb-782f-4786-be49-730154276f85 | Concrete | Circular Joint,Radial Joint | Drummy
b2ae012c-e396-4ce5-96f6-63cb629a8e38 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 03:20:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 549 | 7 | Grout Injection Hole | Grout Injection Hole |  | 69377 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 549, 7 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | Leak not active at the time of inspection. The grout hole appears to be sealed by salt deposits.the condition of the seal bolt cannot be estimated. | yes | yes |  | no |  | a2b00b31-56ad-4c8f-8ab5-93b500876491,cd653ab1-ba2e-4e59-a21a-3a221d44859b | , | https://web.fulcrumapp.com/photos/view?photos=a2b00b31-56ad-4c8f-8ab5-93b500876491%2Ccd653ab1-ba2e-4e59-a21a-3a221d44859b | Concrete | Grout Hole,Reinforcement | Leaks
43e13e2c-0f8d-4479-adb8-e802c5665bee | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:21:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 550 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84087 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4838 |  |  | No | Missing |  |  |  | 2 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 550, 3 o'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 100% coverage. |  | Steel channel support bracket has Level 2 Corrosion up to 100% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 |  |  |  | Replacement of steel bracket. |  | Yes | Off-Line |  |  |  |  | Dr |  | Steel bracket is severely corroded. Condition seems to have worsened | yes |  |  |  |  | d10ca0cd-e5ce-4a19-b870-b5ad07298e2a |  | https://web.fulcrumapp.com/photos/view?photos=d10ca0cd-e5ce-4a19-b870-b5ad07298e2a | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
d2a74b2f-83de-4081-b0c0-20ac7fd28b65 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 06:18:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 550 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26996 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | 3 |  | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 550, 3 o'clock, Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has leak from behind steel channel Active at time of inspection. |  | Concrete shell segment has leak from behind steel channel Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Loss of production and services | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | DR |  | Leaks have been repaired with concrete seal. Leak is inactive at time of inspection. | yes | no |  | no |  |  |  |  | Concrete,Steel | Reinforcement | Leaks
e405b056-0b99-4881-81af-64dcad55e2bd | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 03:15:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 550 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27344 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 550, 7 o'clock, Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has section of concrete cover removed and reinforcement exposed. Cut depth is 35mm. Reinforcement has corrosion Level 3 corrosion. |  | Concrete shell segment has section of concrete cover removed and reinforcement exposed. Cut depth is 35mm. Reinforcement has corrosion Level 3 corrosion. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | Defect in similar condition. | no | yes |  | yes | Specific repair methodology may be required due to overall damage depth. Up to 100mm | b625c6d9-a46f-4d77-8756-5174a1460516,c300c2e1-5ec1-4bc2-81b7-2a1f3c496684,8fed6e89-3f17-464d-9ac9-a08d22898734 | ,, | https://web.fulcrumapp.com/photos/view?photos=b625c6d9-a46f-4d77-8756-5174a1460516%2Cc300c2e1-5ec1-4bc2-81b7-2a1f3c496684%2C8fed6e89-3f17-464d-9ac9-a08d22898734 | Concrete | Reinforcement | Corrosion-Heavy,Corrosion-Surface
80bac8f9-9286-4855-8fdf-af67c7dd33ad | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 22:51:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 551 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36781 |  | 6856 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 24/10/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 551, 12 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Engineering Repair Methodology Required Competent Engineer | Bogdan Stanca |  | Evidence of water ingress is still visible. Not active at date of inspection. The defect has not charged. Low priority. | no | no |  | yes | Discuss with the tunnel engineer the failure mechanism. Typical defect. | 68fc7197-1f11-4aee-9f10-badb40b8f175,44c98264-7c14-479b-afb2-bc2be7842a87,ef765d78-f44d-429b-a332-58917d8408f4 | ,, | https://web.fulcrumapp.com/photos/view?photos=68fc7197-1f11-4aee-9f10-badb40b8f175%2C44c98264-7c14-479b-afb2-bc2be7842a87%2Cef765d78-f44d-429b-a332-58917d8408f4 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
90b409f9-1905-42e9-87c7-0ac78ba34874 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 15:00:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 552 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69381 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 552, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over and area 250mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over and area 250mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering Repair Methodology Required | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The defect is at a circular joint with Ring 551 and appears to extend to the depth of cover. High repair priority to ensure that the joint seal will not be compromised. | yes | no |  | yes |  | dd264e82-7b29-4866-972d-b73007ad9548,0d0a5e0d-ed38-452d-bc32-ed1d4e815f85,6eb0ed77-784b-4581-afff-1aff270f9e67,4c10c965-ed13-420f-92a5-17433316f39f | ,,, | https://web.fulcrumapp.com/photos/view?photos=dd264e82-7b29-4866-972d-b73007ad9548%2C0d0a5e0d-ed38-452d-bc32-ed1d4e815f85%2C6eb0ed77-784b-4581-afff-1aff270f9e67%2C4c10c965-ed13-420f-92a5-17433316f39f | Concrete | Circular Connection,Circular Joint,Radial Joint | Drummy |  | Location to be changed to 551
6b118a08-34f4-4f8e-9eb5-8cf9c2393bc4 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 22:30:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 553 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93656 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 553, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | The defect has not advanced. The defect is cosmetic and should not affect the structural integrity of the tunnel. | no | no |  | no |  | 37e47209-468f-4b87-9cb6-de8d4320d84d |  | https://web.fulcrumapp.com/photos/view?photos=37e47209-468f-4b87-9cb6-de8d4320d84d | Concrete | Circular Joint | Drummy
61fa58c5-1684-44ad-851e-f805bdc7c705 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-30 02:19:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 553 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69382 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 553, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt Component should be "Segmented Bolted Joint (Radial Joint)". Adopted default consequence Health & Safety - Level 2. |  | Shear failure of bolt Component should be "Segmented Bolted Joint (Radial Joint)". Adopted default consequence Health & Safety - Level 2. | Radial joint has Grout Delamination / Drummy Grout over one location of size 200mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over one location of size 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | No change. Same area is delaminated and drummy. | no | yes |  |  |  | 68de15c8-bea5-4484-8a1f-9c96fc0ddcb7,8e540a05-1b75-41a3-a50e-322136e38421 | , | https://web.fulcrumapp.com/photos/view?photos=68de15c8-bea5-4484-8a1f-9c96fc0ddcb7%2C8e540a05-1b75-41a3-a50e-322136e38421 | Concrete | Circular Joint,Radial Joint | Drummy
1121dad4-7c99-4ecb-af67-829c5006e521 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 02:38:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 553 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 26997 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 553, 8 O'clock, Concrete Element | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The injection hole has self seal with salt deposits and was dry at time of inspection. The seal bolt is not visible for inspection. Injection hole to be repaired in to avoid any leaks when the seal bolt fails. Priority high. | yes | yes |  | no |  | abae6e06-b4bd-4499-920d-457328b1c41c,adb74f3c-f824-4001-a8cb-6eb6c2976469 | , | https://web.fulcrumapp.com/photos/view?photos=abae6e06-b4bd-4499-920d-457328b1c41c%2Cadb74f3c-f824-4001-a8cb-6eb6c2976469 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
fd775fc4-b6f1-4897-86c0-e58577359d50 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 22:23:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 554 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84088 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4853 |  |  | No | Missing |  |  |  | 2 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 554, 11 to 12 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have level 1 corrosion. |  | Channel anchor bolts have level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 |  |  |  | Replacement of anchor bolts at next maintenance cycle |  | Yes | On-Line |  |  |  |  | Bogdan Stanca |  | No evident change in condition | no | yes |  | no |  | 78095e82-5084-46fb-93a3-26ca89045c25,6c65c00a-b857-4969-8c91-4cd99964f6f2,1af0e007-1da5-4882-ad8b-b034dbea6189 | ,, | https://web.fulcrumapp.com/photos/view?photos=78095e82-5084-46fb-93a3-26ca89045c25%2C6c65c00a-b857-4969-8c91-4cd99964f6f2%2C1af0e007-1da5-4882-ad8b-b034dbea6189 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
6f08549a-16c4-4578-847b-79cb93396197 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 05:55:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 554 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84089 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4867 |  |  | No | Missing |  | Corrosion of Reinforcement |  | 2 |  |  |  | Health & Safety |  |  | Localised Corrosion EXT |  | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 554, 2 & 3 o'Clock, Steel Channel Bracket |  | Shear failure of bolt |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 10% coverage. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 10% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 |  |  |  | Review and monitor condition. Can be replaced at next maintenance cycle. |  | Yes | On-Line |  |  |  | Replacement of the bolts. | DR |  | Condition remains mostly the same with minor corrosion on the bolts. | no | no |  |  |  | 8c8af548-6d60-464d-94fd-9414f57c6fbc |  | https://web.fulcrumapp.com/photos/view?photos=8c8af548-6d60-464d-94fd-9414f57c6fbc | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface |  | Not Reinforcement
f1cde006-478d-4bb7-bc21-982c0f62969a | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 21:58:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 554 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69383 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million | Severity Level 2 |  | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 554, 4 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout of size 300mm x 400mm. |  | Circle joint has Grout Delamination / Drummy Grout of size 300mm x 400mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | DR |  | Defect is still present with no change. | yes | no |  | no |  | 1a9837b7-a645-4b3f-9e36-612006c195d8,c9122b96-58ba-4b90-b57b-a2de55bd4a4e | , | https://web.fulcrumapp.com/photos/view?photos=1a9837b7-a645-4b3f-9e36-612006c195d8%2Cc9122b96-58ba-4b90-b57b-a2de55bd4a4e | Concrete | Radial Joint | Drummy |  | Radial Joint not Circular
3e84547a-eace-49d3-bd4f-799b1cdfe967 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-25 05:46:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 556 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27345 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | 2 |  | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 556, 2 o'clock, Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has cracking of 0.5mm width. |  | Concrete shell segment has cracking of 0.5mm width. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | Not Specified | Priority: P3 |  |  |  | Continue to monitor for further deterioration. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | DR |  | Defect is still present with no change. Same 5mm cracks present in the concrete. Severity level has been reduced | no | no |  | no |  | 7b7ecd0b-4aee-46dd-86d3-20dfd3a9f2bf,e50003b6-37bd-41c0-82ba-0b5b5ec7a8bc | , | https://web.fulcrumapp.com/photos/view?photos=7b7ecd0b-4aee-46dd-86d3-20dfd3a9f2bf%2Ce50003b6-37bd-41c0-82ba-0b5b5ec7a8bc | Concrete | Circular Joint | Crack |  | Crack at Circular Joint not reinforcement
ce417d40-bc99-4031-9257-8b381977cf50 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3782 | 118.6321 | POINT (118.6320961 -20.3781835) | 2025-05-27 20:13:18 AEST | 2025-07-30 11:26:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 556 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 26999 |  | 8714 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | 2 |  | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Severity Level 2 |  | Almost Certain (Failure within 1 Year) | Likely (Failure within 2 Years) |  | Ring 556, 3 o'clock, Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 5 corrosion. Steel channel support bracket anchor bolts have Level 5 corrosion. |  | Steel channel support bracket has Level 5 corrosion. Steel channel support bracket anchor bolts have Level 5 corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services | Priority: P3 |  |  |  | Replace corroded channel bracket and anchor bolts. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor | DR |  | There's no change to the condition of the bolt. Condition rating has been reduced. | no | no |  | no |  | 696a62de-0a3e-41d6-9a72-27b7fbb8ca58,3d9806ad-618e-48e2-bf68-f20946447927 | , | https://web.fulcrumapp.com/photos/view?photos=696a62de-0a3e-41d6-9a72-27b7fbb8ca58%2C3d9806ad-618e-48e2-bf68-f20946447927 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
d5693e54-e160-495d-ace4-291f0b33587b | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:59:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 556 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 101801 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | 2 |  | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Possible (Failure within 5 Years) |  | Ring 556, 4 O'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Bogdan Stanca |  | No change to the defect. Spalling of area at junction not considered structurally critical. | no | no |  | yes | Confirmation with Tunnel engineer required | 80a28181-4363-4b58-8ac9-2a0ad4118be5 |  | https://web.fulcrumapp.com/photos/view?photos=80a28181-4363-4b58-8ac9-2a0ad4118be5 | Concrete | Radial Joint | Drummy,Surface Damage
41b08b51-f460-4f42-b012-37b288c57624 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 12:59:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 556 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84090 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 556, 4 o'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has spalling damage over an area of 100mm x 100mm. |  | Concrete shell segment has spalling damage over an area of 100mm x 100mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | Concrete edge damage at the junction to ring 555. Possible during installation of CP system . There is no evidence of further deterioration. Low priority. Mostly esthetic damage. | no | yes |  | yes | Check with Tunnel engineer | b43c0848-d8ca-463a-9794-9327a93be0b9,b6499197-4393-43ef-94f0-23e0d127b478 | , | https://web.fulcrumapp.com/photos/view?photos=b43c0848-d8ca-463a-9794-9327a93be0b9%2Cb6499197-4393-43ef-94f0-23e0d127b478 | Concrete | Circular Connection,Circular Joint | Surface Damage |  | Circular connection. Circular joint.
a00fb53c-0af2-45bd-9a32-f2c3de75b9e1 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:25:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 558 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27000 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 558, 11 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 25% coverage. Channel anchor bolt are missing at some locations. |  | Steel channel support bracket has Level 2 Corrosion up to 25% coverage. Channel anchor bolt are missing at some locations. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition remains unchanged, heavily corroded in some sections of steel channel and bolts | no |  |  |  |  | 446c80eb-e6c5-45bd-83e9-e51a32262951,932ad484-59ef-46e1-ae55-f00c764d4fad,f7120f10-f045-4151-adf4-3c5efb87232c | ,, | https://web.fulcrumapp.com/photos/view?photos=446c80eb-e6c5-45bd-83e9-e51a32262951%2C932ad484-59ef-46e1-ae55-f00c764d4fad%2Cf7120f10-f045-4151-adf4-3c5efb87232c | Steel | Channel Bracket-Bolt | Missing |  | only bolt
3328dbe6-0c9c-4c12-87dd-547b66fb2b12 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:25:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 558 | 12 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27600 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 558, 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [15 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
d42e11df-381e-444c-9f86-e2ce451c014e | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3216 | 118.5853 | POINT (118.5853325 -20.3216346) | 2025-05-27 20:13:18 AEST | 2025-07-28 12:59:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 558 | 5 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 69384 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 44552.3836 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 558, 4 o'clock. Concrete Shell Segment Radial Joint Connection. |  |  |  | Radial joint has Grout Delamination / Drummy Grout |  | Radial joint has Grout Delamination / Drummy Grout | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | RT |  | Condition unchanged | [5 empty] | 93d4aea9-74f3-4ee3-92ce-f8e09ed0ddc5 |  | https://web.fulcrumapp.com/photos/view?photos=93d4aea9-74f3-4ee3-92ce-f8e09ed0ddc5 | Concrete | Circular Joint | Drummy |  | Circular joint not radial
7aa3866e-116d-479a-a6f6-58ee8b52d774 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:26:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 559 | 10 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84091 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 559, 10 o'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | KP |  | Condition unchanged | no |  |  |  |  | 55732382-2ac4-4b73-ba55-c75d54fbd9be |  | https://web.fulcrumapp.com/photos/view?photos=55732382-2ac4-4b73-ba55-c75d54fbd9be | Concrete | Circular Joint | Drummy
0e5dd022-85b9-40c3-b56a-56c9e590bfbf | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:02:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 559 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101778 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 559, 3 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition Unchanged | [5 empty] | 1d5acdac-c463-4fdb-b623-854b1bade972 |  | https://web.fulcrumapp.com/photos/view?photos=1d5acdac-c463-4fdb-b623-854b1bade972 | Concrete | Circular Joint | Drummy
ad4a92ae-cd46-40b8-9b45-570f67fc8419 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:28:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 559 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69385 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 559, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 400mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 400mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | loss of production | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged. Grout delamination / Drummy concrete at radial joint over an area of 400mm x 400mm. | no |  |  |  |  | 7e608d91-ed25-4c67-b2b8-e5fb48fc1279,b673b1d6-c9de-4355-bbf8-7a934d54743a,5216151c-0fa4-46fd-be9a-1844cf1fcf92 | ,, | https://web.fulcrumapp.com/photos/view?photos=7e608d91-ed25-4c67-b2b8-e5fb48fc1279%2Cb673b1d6-c9de-4355-bbf8-7a934d54743a%2C5216151c-0fa4-46fd-be9a-1844cf1fcf92 | Concrete | Radial Joint | Drummy
51e9ac3c-8eae-4fc5-8372-7d951104f824 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:15:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 560 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84092 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.492 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 560, 1 & 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 10% coverage. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 10% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | RT |  | Condition unchanged | no |  |  |  |  | 5ebc78a2-d2bc-45bc-b9e1-d6026b6792da |  | https://web.fulcrumapp.com/photos/view?photos=5ebc78a2-d2bc-45bc-b9e1-d6026b6792da | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
a9e982e7-f12e-490e-a944-82b1659c268a | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:12:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 560 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101779 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 560, 3 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | ff4d1dd6-902d-4b1f-b492-17fc5480c091 |  | https://web.fulcrumapp.com/photos/view?photos=ff4d1dd6-902d-4b1f-b492-17fc5480c091 | Concrete | Circular Joint | Drummy
1d9fad43-29d6-4edb-b364-069b4171689d | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:16:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 560 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27346 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 560, 4 o'clock, Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete |  | Concrete shell segment has drummy concrete | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Remediate concrete as per BHP Standards and specifications | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | KP |  | Delimited/Drummy concrete still present, no change | no |  |  |  |  | a0919fdd-f25e-47f1-8a72-105924131508,ec4a2410-8321-47f4-b05f-abfbe7722594 | , | https://web.fulcrumapp.com/photos/view?photos=a0919fdd-f25e-47f1-8a72-105924131508%2Cec4a2410-8321-47f4-b05f-abfbe7722594 | Concrete | Circular Joint | Drummy |  | Circular Not Reinforcement
77d0ba55-c0e4-4065-8fd3-7e3269a41620 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-30 02:10:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 560 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 69386 |  | 6856 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 24/10/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 560, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 200mm x 200mm |  | Concrete shell segment has drummy concrete over an area of 200mm x 200mm | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | Remediate concrete as per BHP Standards and specifications | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | Area of drummy concrete has not changed. | no | yes |  |  |  | 2eabfdd4-c311-4bc3-b3bc-389cbe9c957e |  | https://web.fulcrumapp.com/photos/view?photos=2eabfdd4-c311-4bc3-b3bc-389cbe9c957e | Concrete | Reinforcement | Drummy
322fd7e4-b38e-450f-aa99-40328c22e73f | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 19:00:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 561 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36782 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 561, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Possible Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | KP |  | Condition unchanged same as last observation | no |  |  |  |  | 6ea713c9-534c-4080-a95a-f5d8d1b34987 |  | https://web.fulcrumapp.com/photos/view?photos=6ea713c9-534c-4080-a95a-f5d8d1b34987 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
60f0f633-9b63-475e-9206-40c2f99ec54b | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:50:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 561 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69387 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 561, 7 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | loss of production | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition, still drummy patch repair during inspection | no |  |  |  |  | eea55205-5bb0-4ea8-9e10-82f56b8f19da,a7d65f75-857c-4815-8ee0-37e5453a7fe3 | , | https://web.fulcrumapp.com/photos/view?photos=eea55205-5bb0-4ea8-9e10-82f56b8f19da%2Ca7d65f75-857c-4815-8ee0-37e5453a7fe3 | Concrete | Radial Joint | Drummy
f662ad97-99e1-4913-baa1-c3d062ff3490 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:29:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 562 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84093 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.4935 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 562, 1 & 3 o'Clock, Channel Anchor Bolts |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion |  | Channel anchor bolts have Level 2 Medium Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | Double up of same structure components | no |  |  |  |  | facf9536-c30b-45d8-bc6d-8b22b5838786,d4390758-406d-40eb-8c5e-fc0373fc4d42 | , | https://web.fulcrumapp.com/photos/view?photos=facf9536-c30b-45d8-bc6d-8b22b5838786%2Cd4390758-406d-40eb-8c5e-fc0373fc4d42 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
9dc3d5f0-b1bd-4869-a76d-b54c0703f06e | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 18:58:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 562 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84095 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.5059 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 562, 1 to 12 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged | no |  |  |  |  | 2367bb92-1024-4e28-9137-9d910877f8f1 |  | https://web.fulcrumapp.com/photos/view?photos=2367bb92-1024-4e28-9137-9d910877f8f1 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
76be4cf1-36aa-419f-973d-72cd4aaa2397 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 18:56:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 562 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27001 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 562, 11 to 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolt has Level 1 Corrosion. Steel channel support bracket has Level 2 corrosion at 10% coverage. |  | Steel channel support bracket anchor bolt has Level 1 Corrosion. Steel channel support bracket has Level 2 corrosion at 10% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged observed to be in the same condition as last time | no |  |  |  |  | afde44f9-05ff-4d50-9a06-ef478f70d92d,934e69ca-9979-4347-aee3-1e04e27b9747 | , | https://web.fulcrumapp.com/photos/view?photos=afde44f9-05ff-4d50-9a06-ef478f70d92d%2C934e69ca-9979-4347-aee3-1e04e27b9747 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
e4a92923-3893-42fe-9d51-a60fb64abd6b | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:30:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 562 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93657 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 562, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout delamination / drummy grout over an area of 150mm x 300mm. |  | Radial joint has grout delamination / drummy grout over an area of 150mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Radial Joint | Drummy
81469e87-06ba-4899-a0b7-6c7a20b4c94f | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 14:53:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 563 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36783 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 563, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | KP |  | Unchanged in the condition ( no active leakage of water) | no |  |  |  |  | 7f35cf6d-449c-4e70-a3a6-c16cd6eb37da |  | https://web.fulcrumapp.com/photos/view?photos=7f35cf6d-449c-4e70-a3a6-c16cd6eb37da | Concrete | Grout Hole | Leaks |  | Not Reinforcement
6d8e31c5-8f72-4243-aa43-05da883ea29d | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3742 | 118.6339 | POINT (118.6338718 -20.3741509) | 2025-05-27 20:13:18 AEST | 2025-07-24 18:52:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 564 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36785 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 564, 12 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | KP |  | On further signs of active leakage | yes |  |  |  |  | bc5b3571-0d0f-4f4e-b5c4-93b890af738f |  | https://web.fulcrumapp.com/photos/view?photos=bc5b3571-0d0f-4f4e-b5c4-93b890af738f | Concrete | Grout Hole | Leaks |  | Not Reinforcement
510b4f60-be1b-4913-9afe-f59c212a1efb | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:55:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 564 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84096 |  | 8714 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 564, 2 to 3 o'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolts have Level 4 corrosion. Steel channel support bracket has Level 3 Corrosion up to 100% coverage. |  | Channel anchor bolts have Level 4 corrosion. Steel channel support bracket has Level 3 Corrosion up to 100% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace corroded channel bracket and anchor bolts. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and 000-S-12598. | No | On-Line | No | Walkway | - | Replace Component Competent Supervisor | RT |  | Condition unchanged | [5 empty] | 7142b810-3aec-4df9-9292-c719e4217c32 |  | https://web.fulcrumapp.com/photos/view?photos=7142b810-3aec-4df9-9292-c719e4217c32 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
3aea9a6a-0a12-4cbe-bcd4-363be17f0585 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3741 | 118.6339 | POINT (118.6338592 -20.3741138) | 2025-05-27 20:13:18 AEST | 2025-07-29 07:13:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 564 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84094 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 564, 4 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Repair patch has drummy | no |  |  |  |  | 116b8420-fe54-413e-9088-1dd44882cb8e |  | https://web.fulcrumapp.com/photos/view?photos=116b8420-fe54-413e-9088-1dd44882cb8e | Concrete | Circular Joint | Drummy |  | Circular not radial
207ff220-01c3-4ae5-8ecb-5c8f3d2aca4a | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3741 | 118.6339 | POINT (118.6339004 -20.3741257) | 2025-05-27 20:13:18 AEST | 2025-07-29 00:29:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 564 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36784 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 564, 9 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Inactive dry leak chloride induced. No signs for further deterioration. | no |  |  |  |  | fecf379c-f19f-4b7f-8a04-0f1363a18a42 |  | https://web.fulcrumapp.com/photos/view?photos=fecf379c-f19f-4b7f-8a04-0f1363a18a42 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
ab4a1442-4e7a-4c6c-ac52-cf23aa127060 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3741 | 118.6339 | POINT (118.6339066 -20.3741235) | 2025-05-27 20:13:18 AEST | 2025-07-29 00:27:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 566 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27002 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 566, 11 o'clock, Steel Channel Support Bracket. |  |  |  | One channel anchor bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | One channel anchor bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged same as the last time (missing one bolt) | no |  |  |  |  | 17dda8f4-1ff3-4b40-a6e2-59cd00e3ed72 |  | https://web.fulcrumapp.com/photos/view?photos=17dda8f4-1ff3-4b40-a6e2-59cd00e3ed72 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
1d206914-4f0e-4834-87c3-51dd806664c8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 00:27:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 566 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27608 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 566, 11, 12 & 1 o'clock, Steel Channel Support Bracket |  |  |  | Steel channel support has Level 1 corrosion. One channel anchor bolt is missing at 1 O'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support has Level 1 corrosion. One channel anchor bolt is missing at 1 O'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the existing conditions, steel channel and bolts are corroded | no |  |  |  |  | 0ef27470-5e39-480b-ad25-42667e4c7f60,1d8668a1-0420-4399-9b0b-7b4cdc09d91e | , | https://web.fulcrumapp.com/photos/view?photos=0ef27470-5e39-480b-ad25-42667e4c7f60%2C1d8668a1-0420-4399-9b0b-7b4cdc09d91e | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
770ebc7f-acab-4331-8fcf-47cee4a324d2 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 09:37:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 566 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84097 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.5122 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 566, 2 & 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 1 Surface Corrosion up to 25% coverage. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. Steel channel support bracket has Level 1 Surface Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | The steel channel and anchor bolts are severely corroded | yes |  |  |  |  | 9e5ddd81-272d-4f00-a7e3-0f62ae94eba0,5892d739-9889-4d89-aa52-8a0a96b48c7f | , | https://web.fulcrumapp.com/photos/view?photos=9e5ddd81-272d-4f00-a7e3-0f62ae94eba0%2C5892d739-9889-4d89-aa52-8a0a96b48c7f | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
99bd14d3-bf82-495f-9d6c-5575ca2edb28 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3741 | 118.6339 | POINT (118.6339101 -20.3741186) | 2025-05-27 20:13:18 AEST | 2025-07-29 00:27:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 566 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 101802 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 566, 4 O'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition, drummy grout | no |  |  |  |  | 9d959311-565e-45e2-93d0-6c29f4511b4c |  | https://web.fulcrumapp.com/photos/view?photos=9d959311-565e-45e2-93d0-6c29f4511b4c | Concrete | Radial Joint | Drummy
3948424f-fcbe-42dc-9a92-62a8827d837c | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3741 | 118.6339 | POINT (118.6339035 -20.3741168) | 2025-05-27 20:13:18 AEST | 2025-07-29 00:26:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 567 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 36786 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 567, 8 o'clock, Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 400 mm x 400 mm. |  | Concrete shell segment has drummy concrete over an area of 400 mm x 400 mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), downgraded to P3 and defect to be monitored. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | No Changes, drummy concrete over an area of 400mm x 400mm | no |  |  |  |  | 1daa2006-0fe1-469b-a557-ab01b74ae17d |  | https://web.fulcrumapp.com/photos/view?photos=1daa2006-0fe1-469b-a557-ab01b74ae17d | Concrete |  | Drummy |  | Not reinforcement
87fe79d4-95e1-4465-ab95-4364ba632343 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 00:24:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 568 | 1 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 84098 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 568, 1 o'clock, Segment Bolted Joint (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Component should be "Segmented Bolted Joint (Circle Joint)". Adopted default consequence Financial - Level 3. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition | no |  |  |  |  | 9536c71a-e886-4005-bfcf-413f9a59a21c |  | https://web.fulcrumapp.com/photos/view?photos=9536c71a-e886-4005-bfcf-413f9a59a21c | Concrete | Circular Joint | Drummy
672087ca-f730-4868-93fc-f4cbaf4ceabd | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3741 | 118.6339 | POINT (118.6338949 -20.3741093) | 2025-05-27 20:13:18 AEST | 2025-07-29 00:24:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 568 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84099 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 568, 7 o'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Cathodic Protection continuity cable severed. |  | Cathodic Protection continuity cable severed. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), upgraded to P2. | Not Specified | Priority: P2 |  |  |  | Reinstate Cathodic Protection Continuity Cable. | Cathodic Protection Technician | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor | KP |  | No change in the condition, still disconnected | no |  |  |  |  | ef42c834-386d-4455-9762-b296e81553ee,641ce645-d785-4e60-99f3-042bf516dc58,934291b5-2dba-4251-ad63-c05e1b921b04 | ,, | https://web.fulcrumapp.com/photos/view?photos=ef42c834-386d-4455-9762-b296e81553ee%2C641ce645-d785-4e60-99f3-042bf516dc58%2C934291b5-2dba-4251-ad63-c05e1b921b04 | Concrete
2fe6a353-58d2-4894-828e-b6c74e94f617 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 00:23:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 569 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36787 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 569, 11 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No further active leakage of water | no |  |  |  |  | 6050f205-72b6-4402-baec-e4a042a79c02 |  | https://web.fulcrumapp.com/photos/view?photos=6050f205-72b6-4402-baec-e4a042a79c02 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
e43c5c9c-ebf2-481c-a705-42a298a8fe6b | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 00:23:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 570 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101781 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 570, 3 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | The steel channel and anchor bolt is severely corroded | yes |  |  |  |  | a613cda9-6f5e-44f8-ab38-2fb923621527 |  | https://web.fulcrumapp.com/photos/view?photos=a613cda9-6f5e-44f8-ab38-2fb923621527 | Concrete,Steel | Circular Joint | Corrosion-Heavy |  | Corrosion Heavy. Not Drummy
df08a433-b2fd-4a96-a528-587903340619 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3741 | 118.634 | POINT (118.6339794 -20.3741208) | 2025-05-27 20:13:18 AEST | 2025-07-29 00:23:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 570 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69388 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 570, 11 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout delamination with cracks at patch repair at circle segment bolted joints |  | Grout delamination with cracks at patch repair at circle segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | KP |  | Unchanged grout delimitation | no |  |  |  |  | 67b560ae-8cd4-4874-9b2a-f036bb14449f |  | https://web.fulcrumapp.com/photos/view?photos=67b560ae-8cd4-4874-9b2a-f036bb14449f | Concrete | Circular Joint | Crack,Drummy
87155e74-c392-4abf-b5ec-ecbe112c006a | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 00:23:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 570 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27005 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 570, 11 to 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Channel anchor bolt are missing at some locations. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Channel anchor bolt are missing at some locations. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged | no |  |  |  |  | 3bd32e81-8ddc-40c0-a3f7-ef1edaaedc66,5ca3dc35-0562-4c1f-b431-ccfe96cf3e0e | , | https://web.fulcrumapp.com/photos/view?photos=3bd32e81-8ddc-40c0-a3f7-ef1edaaedc66%2C5ca3dc35-0562-4c1f-b431-ccfe96cf3e0e | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
d6e5b39d-0681-474a-95e3-a93c4b3908d0 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-29 00:22:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 570 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 69389 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 570, 4 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition, drumming grout | no |  |  |  |  | 863bbc74-e871-4c61-ad84-241fc0282d2d |  | https://web.fulcrumapp.com/photos/view?photos=863bbc74-e871-4c61-ad84-241fc0282d2d | Concrete | Radial Joint | Drummy
0d81c508-bc11-478e-9cfa-17584b33ad60 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 27 | -20.3741 | 118.6339 | POINT (118.6339146 -20.3741403) | 2025-05-27 20:13:18 AEST | 2025-07-29 00:22:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 570 | 7 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 84101 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 570, 7 o'clock, Segment Bolted Joint (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Circle joint has Grout Delamination / Drummy Grout with rust staining over an area of 100mm x 400mm. |  | Circle joint has Grout Delamination / Drummy Grout with rust staining over an area of 100mm x 400mm. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Component should be "Segmented Bolted Joint (Circle Joint)". Adopted default consequence Financial - Level 3. | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Repair patch has failed and grout delamination / drummy concrete and no signs of rust stains. | no |  |  |  |  | 4e232012-a245-41dc-abde-816db007e84c |  | https://web.fulcrumapp.com/photos/view?photos=4e232012-a245-41dc-abde-816db007e84c | Concrete | Circular Joint | Drummy
7993e36c-8566-4b10-948f-975a555f6226 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 20 | -20.3742 | 118.6339 | POINT (118.6338704 -20.3741504) | 2025-07-24 22:31:07 AEST | 2025-07-29 00:04:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 553 | 9 o'clock |  | Segment Bolted Joint (Radial Joint) | [16 empty] | Segment corner crack at radial joint | 1 | [14 empty] | Ring 553, 9 o'clock radial joint, corner crack. 0.3mm wide | [5 empty] | Corner crack possible at installation.Crack is dry. | [12 empty] | Yes | Off-line | Yes |  |  |  | Bogdan Stanca |  | Low priority |  |  |  | no |  | e4085888-2257-4452-80a4-89f607a77e94 |  | https://web.fulcrumapp.com/photos/view?photos=e4085888-2257-4452-80a4-89f607a77e94 | Concrete | Corner,Radial Joint | Crack
083972d4-8a7a-4ffc-9276-c543ca4834d4 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 20 | -20.3742 | 118.6339 | POINT (118.6338819 -20.3741823) | 2025-07-25 02:09:56 AEST | 2025-07-29 00:15:31 AEST | 30011704-user5@smec.com | james.stone@smec.com | 556 | 5 o'clock |  |  | Steel post | [15 empty] | Corrosion | 2 | [14 empty] | Lower part of post, under walkway, baseplate and anchor bolts. | [5 empty] | Corrosion protection coating failure that lead to surface corrosion with loss of section up to 1mm | [14 empty] | Yes |  |  |  | Bogdan Stanca |  | Corrosion protection to the conveyor support and connection to walkway support is required. Priority Medium. |  |  |  | yes | Details of repairs to be added. | 8920fa02-607b-4452-9036-30f6f81c04c4,9fa5c5bc-2c7b-4254-8529-6b5387b33269,f4775342-9d7a-4014-bb4c-c1f8a71f4e83 | ,, | https://web.fulcrumapp.com/photos/view?photos=8920fa02-607b-4452-9036-30f6f81c04c4%2C9fa5c5bc-2c7b-4254-8529-6b5387b33269%2Cf4775342-9d7a-4014-bb4c-c1f8a71f4e83 | Steel | Walkway Support,Walkway Support-Bolt | Coating Failure,Corrosion-Surface
492391ad-41eb-4b7c-9d5b-87c211b30a79 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 20 | -20.3742 | 118.6339 | POINT (118.6338847 -20.3741834) | 2025-07-25 02:42:16 AEST | 2025-07-29 00:18:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | 552 | 7 o'clock |  | Steel Channel Bracket | [15 empty] | Corrosion - Connection |  | 3 | [14 empty] | 7 o'clock Chanel connection to concrete shell. | [5 empty] | Anchors level corrosion. Lower anchor bolt nut fully corroded. | [14 empty] | Yes |  |  |  | Bogdan Stanca |  | Surface corrosion to the base plate is not structurally significant. Hold down bolts and nuts have advanced corrosion to the point that the lower nut is fully corroded. Medium priority. |  |  |  | no |  | 63fe1308-0fbf-41d4-b434-a4000de15c05,f94db4a4-9483-4b92-8a1d-aff7b288675e,bf9f74f1-2ae0-4391-ac8a-f4b2bbd87038 | ,, | https://web.fulcrumapp.com/photos/view?photos=63fe1308-0fbf-41d4-b434-a4000de15c05%2Cf94db4a4-9483-4b92-8a1d-aff7b288675e%2Cbf9f74f1-2ae0-4391-ac8a-f4b2bbd87038 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
d2361917-708e-4504-b0cd-c13a8f153db6 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 20 | -20.3742 | 118.6339 | POINT (118.6339079 -20.374213) | 2025-07-25 02:50:17 AEST | 2025-07-28 23:59:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 552 | 5 o'clock |  |  | Conveyor and walkway steel support | [37 empty] | Localized corrosion at lower portion of support with loss of section up to 1mm. Loss of protection coating on the walkway support member. | [18 empty] | Bogdan Stanca |  | Post corrosion at the lower part due to water stagnation. Base plate and anchors covered in thick deposits and not inspected. The corrosion protection coating is failing on walkway members exposing the bear metal to the corrosion environment. |  |  |  | no |  | 6af3adbc-2397-46a7-a39c-534b0306b8e1,23c7623e-97b4-4d65-bc7d-f5b6b23551aa,d2bdcf70-e3ca-46d9-a63a-62dfca171745,6f73a543-af14-44b0-a472-3de008d3bcf0 | ,,, | https://web.fulcrumapp.com/photos/view?photos=6af3adbc-2397-46a7-a39c-534b0306b8e1%2C23c7623e-97b4-4d65-bc7d-f5b6b23551aa%2Cd2bdcf70-e3ca-46d9-a63a-62dfca171745%2C6f73a543-af14-44b0-a472-3de008d3bcf0 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface
a9df6469-319f-4d72-b5e7-5b885641b3db | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 22 | -20.3742 | 118.6339 | POINT (118.6338819 -20.3741741) | 2025-07-24 19:00:19 AEST | 2025-07-29 00:16:40 AEST | 30011704-user5@smec.com | james.stone@smec.com | 561 | 10 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drumminess on the patch repair along the circumferential joint | [5 empty] | 4667f383-d751-4408-8688-aaf16ba17db8 |  | https://web.fulcrumapp.com/photos/view?photos=4667f383-d751-4408-8688-aaf16ba17db8 | Concrete | Circular Connection,Circular Joint | Drummy
adeeeedc-e5fd-4c38-acdd-ae04cd432062 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 22 | -20.3742 | 118.6338 | POINT (118.6338234 -20.3741574) | 2025-07-24 19:02:45 AEST | 2025-07-29 00:08:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 560 | 11 |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Drumminess on the patch repair along the radial joint | [5 empty] | 6e72ca5d-57ca-4209-87ab-833f835eab9f |  | https://web.fulcrumapp.com/photos/view?photos=6e72ca5d-57ca-4209-87ab-833f835eab9f | Concrete | Radial Joint | Drummy
9b3446be-7199-4d4f-8bfd-74ab48ecb12b | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 22 |  |  |  | 2025-07-24 19:04:40 AEST | 2025-07-29 00:08:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 559 | 11 |  | Grout Injection Hole | [57 empty] | KP |  | Signs of inactive leak of water from the grout injection hole | [5 empty] | fdc55f4b-c742-4bc1-ba19-377c1f28871f |  | https://web.fulcrumapp.com/photos/view?photos=fdc55f4b-c742-4bc1-ba19-377c1f28871f | Concrete | Grout Hole | Leaks
fe52db5b-32ee-41d0-9d8e-4c77da219ab4 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 23 | -20.3742 | 118.6339 | POINT (118.6338835 -20.3741735) | 2025-07-24 19:00:04 AEST | 2025-07-29 00:16:54 AEST | 30011704-user5@smec.com | james.stone@smec.com | 564 | 9 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Grout Delamination / Drummy Concrete over an area of 150mm x 400mm. | [5 empty] | 5974cd4c-51fe-44ff-86f7-3829f3c40068 |  | https://web.fulcrumapp.com/photos/view?photos=5974cd4c-51fe-44ff-86f7-3829f3c40068 | Concrete | Circular Joint | Drummy
a10b46dc-6493-430d-8f2d-0871b27efaf7 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 23 | -20.3742 | 118.6339 | POINT (118.6338853 -20.3741581) | 2025-07-24 19:03:31 AEST | 2025-07-29 00:09:44 AEST | 30011704-user5@smec.com | james.stone@smec.com | 563 | 10 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Grout delamination / Drummy concrete over an area of 200mm x 500mm. | [5 empty] | deaf34b9-45a5-4822-a98b-c5bf69f8764a |  | https://web.fulcrumapp.com/photos/view?photos=deaf34b9-45a5-4822-a98b-c5bf69f8764a | Concrete | Circular Joint | Drummy
1011b971-f17d-456c-a31f-06b4e8d805af | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 21 |  |  |  | 2025-07-25 06:01:34 AEST | 2025-07-29 00:09:39 AEST | 30011704-user5@smec.com | james.stone@smec.com | 554 | 2 O'Clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | Dr |  | Drumminess on the patch repair along the circumferential joint | [5 empty] | 30c08779-f9c3-4b08-8fd2-b4ad9154b58f |  | https://web.fulcrumapp.com/photos/view?photos=30c08779-f9c3-4b08-8fd2-b4ad9154b58f | Concrete | Circular Connection,Circular Joint | Drummy
d1e944b6-1c7c-4450-bd0c-62036f9f14e5 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 21 |  |  |  | 2025-07-25 06:09:11 AEST | 2025-07-29 00:17:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 551 | 11 O' Clock |  | Hydrophilic Joint Seal (Radial Joint) | [16 empty] | Leak through grout injection hole | 3 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 | [12 empty] | Water leak through joint, leading to accelerated concrete damage (locally). | [16 empty] | Dr |  | Minor water leak through patchwork on the radial joint. |  | yes |  |  |  | 8f8f964c-71a9-453d-bc14-077d1668cfcc |  | https://web.fulcrumapp.com/photos/view?photos=8f8f964c-71a9-453d-bc14-077d1668cfcc | Concrete | Radial Joint | Leaks |  | Not grout hole
56380e3b-098d-4041-bb60-51436a933bb5 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 15 | -20.3741 | 118.6338 | POINT (118.6338241 -20.3741443) | 2025-07-27 10:09:20 AEST | 2025-07-29 00:17:57 AEST | 30011704-user5@smec.com | james.stone@smec.com | 560 | 5 o’clock | [59 empty] | KP |  | The steel support to the walkway are heavily corroded, Priority High |  | yes |  |  |  | 50c17c3d-e134-4774-a4c8-1526e2daef5c,7130fac0-4e61-4996-8996-87665214170d | , | https://web.fulcrumapp.com/photos/view?photos=50c17c3d-e134-4774-a4c8-1526e2daef5c%2C7130fac0-4e61-4996-8996-87665214170d | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support
6c9b3b96-b945-4a43-b79f-a3cf66241abc | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 15 |  |  |  | 2025-07-27 10:13:03 AEST | 2025-07-29 09:49:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | 560 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base slab looks to be in fair condition, but the base plate and bolts are heavily corroded, priority High |  | yes |  |  |  | e4074d64-a1f3-40d3-b444-e76e6ae2e36f,477cdcad-b925-4f69-b36e-bc64189b9d1f | , | https://web.fulcrumapp.com/photos/view?photos=e4074d64-a1f3-40d3-b444-e76e6ae2e36f%2C477cdcad-b925-4f69-b36e-bc64189b9d1f | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface |  | Centre Support not Channel Bracket
6f7a7abd-081f-4a40-81de-e653832ac427 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 15 | -20.3742 | 118.6338 | POINT (118.6338248 -20.3741509) | 2025-07-27 10:24:54 AEST | 2025-07-29 00:10:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 560 | 7 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The steel supporting channels and bolted are heavily corroded. Priority High |  | yes |  |  |  | d3194627-1d03-4df5-aba1-f62ae186f990,f6782a17-956f-4552-8e29-910443ccfc3b | , | https://web.fulcrumapp.com/photos/view?photos=d3194627-1d03-4df5-aba1-f62ae186f990%2Cf6782a17-956f-4552-8e29-910443ccfc3b | Steel | Conveyor Support,Conveyor Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support and Bolt. Not Channel Bracket or Channel Bracket Bolt
ac6474b8-33cd-4566-80fb-633b919b5479 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 15 |  |  |  | 2025-07-27 10:35:58 AEST | 2025-07-29 09:49:15 AEST | 30011704-user5@smec.com | james.stone@smec.com | 564 | 5 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The supporting steel channel is heavily corroded. Priority High |  | yes |  |  |  | 8fedc362-9a7c-4fef-9a97-233c320663e2,1e655f2f-8441-47a8-bd79-a4bd8ac00f5f | , | https://web.fulcrumapp.com/photos/view?photos=8fedc362-9a7c-4fef-9a97-233c320663e2%2C1e655f2f-8441-47a8-bd79-a4bd8ac00f5f | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway Support. Not channel bracket
ff5cfdc6-f276-4e44-8374-41fb27e63ae0 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 15 |  |  |  | 2025-07-27 10:37:30 AEST | 2025-07-29 09:49:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 564 | 6 o’clock |  | Steel Channel Bracket | [57 empty] | KP |  | The base slab is in fair condition during the inspection, but base plate, bolts and footing are heavily corroded. High priority. |  | yes |  |  |  | 084549bf-ca23-4bf6-8fa1-78a57723aa54,5b6d9f06-0b3a-48fc-8aa7-f12d4560cb04 | , | https://web.fulcrumapp.com/photos/view?photos=084549bf-ca23-4bf6-8fa1-78a57723aa54%2C5b6d9f06-0b3a-48fc-8aa7-f12d4560cb04 | Steel | Centre Support,Centre Support-Bolt | Corrosion-Heavy,Corrosion-Surface |  | Centre Support and bolt not channel bracket
0e11396c-4368-4fea-a4ec-8379da626d13 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 16 | -20.3742 | 118.6339 | POINT (118.6339009 -20.3741978) | 2025-07-27 10:44:39 AEST | 2025-07-29 00:06:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 564 | 7 O'Clock |  |  | Conveyor steel support | [56 empty] | RT |  | Structural footing severely rusted. Likely to fail may result in failure of structure. Medium priority | [5 empty] | 96c3ca53-9af3-4b8b-9e33-a1d25f4b6779 |  | https://web.fulcrumapp.com/photos/view?photos=96c3ca53-9af3-4b8b-9e33-a1d25f4b6779 | Steel | Conveyor Support
5c5cf7e7-64fa-4859-b8fd-67b801f220e0 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 16 | -20.3217 | 118.5853 | POINT (118.585315 -20.321695) | 2025-07-27 11:04:24 AEST | 2025-07-29 00:13:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 568 | 7 |  |  | Steel Support Structure | [56 empty] | RT |  | Corroded footing with active ongoing rust , 1x bolt has failed due to corrosion. Need corrosion protection to prolong service life. Medium priority | [5 empty] | 1453f825-2915-43b4-a807-2ba9c8bf27f7 |  | https://web.fulcrumapp.com/photos/view?photos=1453f825-2915-43b4-a807-2ba9c8bf27f7 | Steel | Conveyor Support | Corrosion-Heavy,Corrosion-Surface |  | Conveyor Support not centre
b2a9753c-2298-4910-8c15-f18113abc29b | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 16 | -20.3742 | 118.6338 | POINT (118.6338474 -20.3741587) | 2025-07-27 11:13:59 AEST | 2025-07-29 00:18:11 AEST | 30011704-user5@smec.com | james.stone@smec.com | 569 | 7 O'Clock |  | Hydrophilic Joint Seal (Radial Joint) | [57 empty] | RT |  | Drummy concrete patches on radial joint over areas 250x250 and 200x250mm. Low priority | [5 empty] | 62cf1db6-0d21-4048-87e2-882c90c1b514 |  | https://web.fulcrumapp.com/photos/view?photos=62cf1db6-0d21-4048-87e2-882c90c1b514 | Concrete | Radial Joint | Drummy
08bd11a4-8900-4579-920f-f0beea2030d7 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 16 | -20.3742 | 118.6339 | POINT (118.6339013 -20.3742027) | 2025-07-27 13:28:06 AEST | 2025-07-29 00:13:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | 562 | 4 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Grout delamination /Drummy Concrete at radial joint over an area of 200mmx200mm. Priority medium | [5 empty] | a55ba710-5829-48c5-9c17-fe4b9d421bd6 |  | https://web.fulcrumapp.com/photos/view?photos=a55ba710-5829-48c5-9c17-fe4b9d421bd6 | Concrete | Circular Joint | Drummy |  | Circular Joint not radial
2f9a1930-b24c-48b3-b53d-e5a0eac429c5 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 16 | -20.3742 | 118.6339 | POINT (118.633918 -20.3741906) | 2025-07-27 13:37:48 AEST | 2025-07-29 00:18:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 563 | 4 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | RT |  | Grout delamination / drummy concrete over an area of 150mmx200mm. | [5 empty] | a644ee16-6290-4515-bd1f-31e3aae009a6 |  | https://web.fulcrumapp.com/photos/view?photos=a644ee16-6290-4515-bd1f-31e3aae009a6 | Concrete | Circular Joint | Drummy
a8f8e1f3-d81d-4992-8773-0059e3a00ec7 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 3715d8ac-7b3e-45dd-b748-751acb45cdf8 | 16 |  |  |  | 2025-07-27 13:57:55 AEST | 2025-07-29 00:13:35 AEST | 30011704-user5@smec.com | james.stone@smec.com | 563 | 2 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | 5mm offset in between rings 564 and 563. | [5 empty] | 0663eabe-e252-4c03-b7cc-42df7d62bdeb |  | https://web.fulcrumapp.com/photos/view?photos=0663eabe-e252-4c03-b7cc-42df7d62bdeb | Concrete | Circular Connection,Circular Joint | Displacement |  | Circular Joint and Circular Connection
cc8fc972-3a81-4612-9eb7-c1dbedda0772 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3741 | 118.6347 | POINT (118.6346801 -20.3740767) | 2025-05-27 20:13:18 AEST | 2025-07-24 15:53:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 572 | 11 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 101803 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 45553.6269 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 572, 11 O'clock, Segmented Bolted Joint (Radial Joint) |  |  |  | 0.4mm crack at radial segment bolted joint grout. |  | 0.4mm crack at radial segment bolted joint grout. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Same as 0.4mm crack along the radial joint | no |  |  |  |  | 1241ed4c-3182-46f0-8449-62a6007a9c54 |  | https://web.fulcrumapp.com/photos/view?photos=1241ed4c-3182-46f0-8449-62a6007a9c54 | Concrete | Radial Joint | Crack
81e58fcc-fec6-4896-9268-104362f86d7d | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:48:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 572 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84103 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.528 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 572, 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 corrosion . |  | Channel anchor bolts have Level 2 corrosion . | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Steel channel as well as anchor bolt is several corroded | yes |  |  |  |  | 458f1a4e-c25b-46d5-a87c-00719eb00fee |  | https://web.fulcrumapp.com/photos/view?photos=458f1a4e-c25b-46d5-a87c-00719eb00fee | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
4cb7ab3e-4dc2-4621-b484-787d170ad284 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:50:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 572 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 36789 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7333 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 572, 4 o'clock. Concrete Shell Segment Segment bolted joint (radial joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still drummy grout | yes |  |  |  |  | e6e3f089-4258-4c22-849e-b62a835b218a |  | https://web.fulcrumapp.com/photos/view?photos=e6e3f089-4258-4c22-849e-b62a835b218a | Concrete | Circular Joint | Drummy |  | Only Circular
c7980a72-4513-4a61-a8c0-03b2f0ed3eeb | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3179 | 118.5773 | POINT (118.5773419 -20.3179366) | 2025-05-27 20:13:18 AEST | 2025-07-27 13:51:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 574 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 69390 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44552.3952 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 574, 10, 11 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have level 2 corrosion. Steel channel support bracket has Level 2 corrosion. |  | Channel anchor bolts have level 2 corrosion. Steel channel support bracket has Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition | no |  |  |  |  | db4f44af-ee19-4c7f-ab4c-ba00c85d380c |  | https://web.fulcrumapp.com/photos/view?photos=db4f44af-ee19-4c7f-ab4c-ba00c85d380c | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
02d38ea2-b241-4557-a62d-df679f3c27e9 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:35:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 574 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27007 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 574, 2 & 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support anchor bolts have Level 2 corrosion. Steel channel is detached from the wall at 2 O'clock. |  | Steel channel support anchor bolts have Level 2 corrosion. Steel channel is detached from the wall at 2 O'clock. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | The steel channel and anchor bolts are severely corroded | no |  |  |  |  | bade3fef-bda3-4c02-9c2a-a0388d214c6b,38258960-375e-4e16-a0c7-d24ced180ffc | , | https://web.fulcrumapp.com/photos/view?photos=bade3fef-bda3-4c02-9c2a-a0388d214c6b%2C38258960-375e-4e16-a0c7-d24ced180ffc | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
67d26dba-c3ff-478b-9ac2-7fd8a2ccd7ac | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:41:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 574 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27008 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 574, 1 O'Clock, Concrete Shell Segment |  |  |  | Concrete shell segment has cracking of size 0.1mm. |  | Concrete shell segment has cracking of size 0.1mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition of the crack , appears to be about 0.2mm | no |  |  |  |  | 58b530ef-6d5d-4824-a35d-f37dcbf74a6b |  | https://web.fulcrumapp.com/photos/view?photos=58b530ef-6d5d-4824-a35d-f37dcbf74a6b | Concrete | Middle of Panel | Crack |  | Middle of Panel
2f1425cc-f1cd-45d5-b25a-755071fbc5da | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 15:44:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 574 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27004 |  | 6512 | UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 574, 2,3 & 12 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support anchor bolts have Level 4 - Medium High Corrosion. |  | Steel channel support anchor bolts have Level 4 - Medium High Corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services | Priority: P3 |  |  |  | a) replace damaged bolts one at a time as per original design specification; or, b) replace channels per original design specification; | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | KP |  | Condition unchanged, steel channel as well as bolts getting rusted. CS | no |  |  |  |  | c6c08784-c544-4404-a992-b7782a35af75,a9bab6cb-4730-4fa9-8234-199eba8b2979 | , | https://web.fulcrumapp.com/photos/view?photos=c6c08784-c544-4404-a992-b7782a35af75%2Ca9bab6cb-4730-4fa9-8234-199eba8b2979 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
49ce0456-4557-4153-9355-6f28b6a3b174 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:39:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 574 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69379 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Missing Components |  | Missing Components | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 574, 5 o'clock. Concrete Shell Segment Circle Joint Connection. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 200mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition, grout delimitation/ drummy | no |  |  |  |  | 9bdfa084-0161-4b45-92de-0d9c16d159a3,c1584d3d-935b-47e2-ac82-b2d36b73260e | , | https://web.fulcrumapp.com/photos/view?photos=9bdfa084-0161-4b45-92de-0d9c16d159a3%2Cc1584d3d-935b-47e2-ac82-b2d36b73260e | Concrete | Radial Joint | Drummy,Missing |  | Radial Joint
864dcbb0-dc76-40ba-a762-aa486da2b5aa | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:29:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 576 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84104 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.5297 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 576, 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 1 Low Corrosion . Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. |  | Channel anchor bolts have Level 1 Low Corrosion . Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | The channel as well as anchor bolt is severely corroded | yes |  |  |  |  | a5e169a8-e4a8-4bc3-952e-a5eac5f45596 |  | https://web.fulcrumapp.com/photos/view?photos=a5e169a8-e4a8-4bc3-952e-a5eac5f45596 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
a74939fd-e5be-4e1c-9c57-ca1a5e2d4faf | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 08:17:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 577 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93658 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 577, 7 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | b7661871-2528-41e1-a73a-c657e67606b8 |  | https://web.fulcrumapp.com/photos/view?photos=b7661871-2528-41e1-a73a-c657e67606b8 | Concrete | Radial Joint | Drummy
9b07ee82-a55c-4340-a037-074d91d1e649 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3782 | 118.6321 | POINT (118.6320877 -20.3781908) | 2025-05-27 20:13:18 AEST | 2025-07-24 15:22:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 578 | 10 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 36791 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 578, 10 o'clock, Segment bolted joint (circle joint) | Failure to seal joint | Failure to seal joint |  | Grout Delamination / debonding at circle segment bolted joints of size 300mm x 300mm. |  | Grout Delamination / debonding at circle segment bolted joints of size 300mm x 300mm. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Component should be "Segmented Bolted Joint (Circle Joint)". Adopted default consequence Financial - Level 3. | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | The patch repair along the radial joint is drummy as well as there is an active leak along the joint | yes |  |  |  |  | bb834cbe-fce0-4d1f-8ff9-75d869ac999a |  | https://web.fulcrumapp.com/photos/view?photos=bb834cbe-fce0-4d1f-8ff9-75d869ac999a | Concrete | Circular Joint,Radial Joint | Drummy,Leaks |  | Not Reinforcement
f5b0830d-6a0a-4c41-8957-f97898488514 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:16:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 578 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27009 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 578, 2,3 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 corrosion. One anchor bolt is missing at 2 O'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket anchor bolts have Level 2 corrosion. One anchor bolt is missing at 2 O'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition unchanged rusty blots and steel channel | no |  |  |  |  | 5b2f8fe8-429f-488f-ba2d-efe660133c72,8f5fe382-0708-4712-8a67-e8e7a93db4e7 | , | https://web.fulcrumapp.com/photos/view?photos=5b2f8fe8-429f-488f-ba2d-efe660133c72%2C8f5fe382-0708-4712-8a67-e8e7a93db4e7 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
d905066a-adf0-4046-b48a-326d00d82b83 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:18:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 578 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84105 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.5309 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 578, 3 o'Clock, Steel Channel Bracket |  |  |  | Missing channel anchor bolts at two locations. Steel channel support bracket has Level 1 Surface Corrosion up to 25% coverage. |  | Missing channel anchor bolts at two locations. Steel channel support bracket has Level 1 Surface Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition, still missing the bolt and steel channel has surface corrosion | no |  |  |  |  | bb4b51ab-6376-4817-bdbf-24d9de016c56 |  | https://web.fulcrumapp.com/photos/view?photos=bb4b51ab-6376-4817-bdbf-24d9de016c56 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
1afe3d0d-7237-46cf-a2ef-dab824e4e6ba | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:20:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 578 | 4 | Grout Injection Hole | Grout Injection Hole |  | 69396 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 22/12/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 578, 4 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Inactive at time of inspection |  | Grout injection hole has Leak Inactive at time of inspection | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | KP |  | Delimitation and drummy concrete 100x200 mm | yes |  |  |  |  | 732c2815-ee12-432c-b281-67a4a8fdad1a |  | https://web.fulcrumapp.com/photos/view?photos=732c2815-ee12-432c-b281-67a4a8fdad1a | Concrete | Grout Hole | Drummy,Leaks |  | Not Reinforcement
30a393fa-0459-4d62-8940-e8f110725c5f | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 17:12:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 578 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93659 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 578, 7 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 150mm x 300mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 150mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition, delaminated / drummy grout. | no |  |  |  |  | 6544d15c-5919-4912-a051-19b074b7c11a |  | https://web.fulcrumapp.com/photos/view?photos=6544d15c-5919-4912-a051-19b074b7c11a | Concrete | Circular Joint | Drummy
625ad822-77ef-458f-867e-879dc8f8dbb0 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:09:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 579 | 5 | Grout Injection Hole | Grout Injection Hole |  | 36792 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 2 | Condition Rating 2 | Condition Rating 2 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 579, 4 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Supervisor | KP |  | Still in the same condition as observed last time | no |  |  |  |  | 3f7672fd-b38b-42ec-a395-67b43fc5c0c3 |  | https://web.fulcrumapp.com/photos/view?photos=3f7672fd-b38b-42ec-a395-67b43fc5c0c3 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
826b2864-e795-41e1-885e-781e173763c9 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 15:04:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 580 | 12 | Grout Injection Hole | Grout Injection Hole |  | 36793 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 580, 12 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No leaks or signs of leaks observed at 12 o’clock clock position.But, found to have leak at 1 o clock | [5 empty] | e05bb20b-2e4f-46c4-ab25-c1df3b28fa93,ed47cc42-b7f8-496e-81d3-8821ed3cb755 | , | https://web.fulcrumapp.com/photos/view?photos=e05bb20b-2e4f-46c4-ab25-c1df3b28fa93%2Ced47cc42-b7f8-496e-81d3-8821ed3cb755 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
4c71b42f-6d51-4a11-8119-841abeb5b49e | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 13:00:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 580 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93661 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 580, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Radial joint has grout delimitation/ drummy grout on both sides of steel walkway support. | yes |  |  |  |  | 1e82ba65-5d9e-40a8-b26d-7b334a7038b0,0775a1fb-40a4-4d9c-b059-15fe5cd4d26c | , | https://web.fulcrumapp.com/photos/view?photos=1e82ba65-5d9e-40a8-b26d-7b334a7038b0%2C0775a1fb-40a4-4d9c-b059-15fe5cd4d26c | Concrete,Steel | Radial Joint,Walkway Support | Drummy
fe6d1f07-9e7c-421b-9c72-da952d060884 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:36:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 581 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84106 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 581, 7 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | On-Line | No | - | - | Condition Monitoring Competent Supervisor | KP |  | Delaminated/ drummy grout still present | no |  |  |  |  | a3c6762f-6c33-49c9-accb-d06a99889672 |  | https://web.fulcrumapp.com/photos/view?photos=a3c6762f-6c33-49c9-accb-d06a99889672 | Concrete | Radial Joint | Drummy
dd765371-9930-4e13-bdcd-e2befce02991 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:50:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 582 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27010 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 582, 1, 2, 3, 11 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 1 corrosion. One anchor bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3 |  | Steel channel support bracket anchor bolts have Level 1 corrosion. One anchor bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3 | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition | no |  |  |  |  | df32f536-aa27-4716-9292-5b1438201d53,89399b64-d6ef-410d-a8f7-6a6b7d69debb | , | https://web.fulcrumapp.com/photos/view?photos=df32f536-aa27-4716-9292-5b1438201d53%2C89399b64-d6ef-410d-a8f7-6a6b7d69debb | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
41a08858-d97f-45bc-a214-5376b736f080 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 14:56:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 582 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27550 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 582, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Channel anchor bolts have Level 2 corrosion. Channel anchor bolts are missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Channel anchor bolts have Level 2 corrosion. Channel anchor bolts are missing at some locations. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Steel channel bolts are corroded and one of the bolt is missing. Condition unchanged | no |  |  |  |  | 0863e833-afe0-4f72-bc28-40ba81ee597e,33c14c55-db1c-48ba-af99-661a1e65d785 | , | https://web.fulcrumapp.com/photos/view?photos=0863e833-afe0-4f72-bc28-40ba81ee597e%2C33c14c55-db1c-48ba-af99-661a1e65d785 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing,Corrosion-Surface |  | Surface Corrosion
5bce6bf9-447b-45f4-8a86-0dbaa91c6f1a | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:41:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 583 | 1 | Grout Injection Hole | Grout Injection Hole |  | 84107 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 583, 1 o'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | KP |  | Grout injection hole is still actively leaking | no |  |  |  |  | fd999a40-409f-4dae-844c-43cb3e341c20,7baeb5ef-a03a-485d-ac90-5f5b9800d55d | , | https://web.fulcrumapp.com/photos/view?photos=fd999a40-409f-4dae-844c-43cb3e341c20%2C7baeb5ef-a03a-485d-ac90-5f5b9800d55d | Concrete | Grout Hole | Leaks
dfc8b89a-adf1-4f03-a9dc-e0d91bbe3a61 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:41:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 583 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93663 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 583, 7 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. |  | Radial joint has grout Delamination / Drummy Grout over two areas of the same size around 200mm x 200mm each. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Delaminated/drummy grout still present | no |  |  |  |  | aad6c520-06fa-447c-9ef9-1e9f66dc61d2,cd1e031c-cd80-49ce-b734-1cf98118c21d | , | https://web.fulcrumapp.com/photos/view?photos=aad6c520-06fa-447c-9ef9-1e9f66dc61d2%2Ccd1e031c-cd80-49ce-b734-1cf98118c21d | Concrete | Radial Joint | Drummy
bb61034e-8b9d-4af1-a802-a8c6446788b7 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:35:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 584 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101782 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 584, 5 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout delimitation/ drummy concrete is still there. | no |  |  |  |  | cf695096-57b0-41f6-96dc-3e5e7c0f1178 |  | https://web.fulcrumapp.com/photos/view?photos=cf695096-57b0-41f6-96dc-3e5e7c0f1178 | Concrete | Circular Joint | Drummy
4556a4b2-f19e-4218-bf05-ad4048f1aadf | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:38:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 584 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93662 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 584, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over two areas of 200mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over two areas of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | Grout delimitation/ drummy patch repair is still there. | no |  |  |  |  | ef860512-228d-4ce4-945b-d3b6879be7cf |  | https://web.fulcrumapp.com/photos/view?photos=ef860512-228d-4ce4-945b-d3b6879be7cf | Concrete | Circular Joint | Drummy
3da67e51-11d3-486c-8829-cc6bd0ed2c0b | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3782 | 118.6321 | POINT (118.632083 -20.3781692) | 2025-05-27 20:13:18 AEST | 2025-07-30 11:24:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 585 | 11 | Grout Injection Hole | Grout Injection Hole |  | 36796 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 585, 11 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | KP |  | Chlorine induces and inactivate at the time of inspection | no |  |  |  |  | 03d79c51-4eab-46c4-acde-94b95f75555f,b8ae38a8-d78f-4ec4-8c20-a2d24a8c5a28 | , | https://web.fulcrumapp.com/photos/view?photos=03d79c51-4eab-46c4-acde-94b95f75555f%2Cb8ae38a8-d78f-4ec4-8c20-a2d24a8c5a28 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
042dd38a-2222-4ec8-9b9e-89cd2c09ae53 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 08:26:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 585 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84108 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 585, 7 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Inaccessible dur to pipeline being in the way. | [8 empty] | Concrete | Radial Joint | Drummy
c985dfd3-223b-4899-9209-0b304a2ad908 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 14:53:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 585 | 8 | Grout Injection Hole | Grout Injection Hole |  | 36795 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 585, 8 o'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Condition improved no sign of water ingress. | [5 empty] | d5eb8d17-fbb1-4a4a-87ef-7d99ea2149a0 |  | https://web.fulcrumapp.com/photos/view?photos=d5eb8d17-fbb1-4a4a-87ef-7d99ea2149a0 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
2f7bd1fc-b33c-45d4-9238-75501dd596c2 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 12:30:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 586 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27011 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 586, 10 & 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 25% coverage. Channel anchor bolts have level 2 corrosion. Channel anchor bolts are missing at 11 o'clock. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket has Level 2 Corrosion up to 25% coverage. Channel anchor bolts have level 2 corrosion. Channel anchor bolts are missing at 11 o'clock. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. 24/09/2024 AIE comments: Bolt is missing at 11 o'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Loss of services. |  | Loss of services. |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Condition same as the past. | no |  |  |  |  | f0cc8b81-d89a-42d4-bee1-3d46aeaefdd8,2be00642-d054-4f68-bce1-1e8d40f2490f,8220d5c7-a3f3-4859-b1f4-b970253283be | ,, | https://web.fulcrumapp.com/photos/view?photos=f0cc8b81-d89a-42d4-bee1-3d46aeaefdd8%2C2be00642-d054-4f68-bce1-1e8d40f2490f%2C8220d5c7-a3f3-4859-b1f4-b970253283be | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
20af4032-6e38-40b5-a685-e82f99001f3d | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:31:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 586 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27623 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 586, 2,3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 1 corrosion at 25% coverage. Steel channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket anchor bolts have Level 1 corrosion at 25% coverage. Steel channel anchor bolts have Level 2 corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | No change in the condition | no |  |  |  |  | a9156d30-d905-47e5-9f4f-631d85f49610,21ddeb89-b9b0-44ed-a679-f4d3a5bada7a | , | https://web.fulcrumapp.com/photos/view?photos=a9156d30-d905-47e5-9f4f-631d85f49610%2C21ddeb89-b9b0-44ed-a679-f4d3a5bada7a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
212d68ca-6291-4fcb-8430-ef612a8ed4ca | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:28:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 586 | 5 o’clock | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 69398 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 586, 5 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints at two locations of size 200mm x 200mm. |  | Grout Delamination / debonding at circle segment bolted joints at two locations of size 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition, drummy grout/ grout delimitation | no |  |  |  |  | bf89464b-53dd-4342-afd7-9e73d3678f75 |  | https://web.fulcrumapp.com/photos/view?photos=bf89464b-53dd-4342-afd7-9e73d3678f75 | Concrete | Circular Joint | Drummy
ed1f9d51-5b6d-4ab2-a9e6-0aee25bdf948 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3781 | 118.6318 | POINT (118.6317971 -20.3781026) | 2025-05-27 20:13:18 AEST | 2025-07-30 11:24:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 586 | 9 | Grout Injection Hole | Grout Injection Hole |  | 36797 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 586, 9 O'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition Unchanged, condition 3 | [5 empty] | 0d336e74-9921-430b-bf62-9374459e387d |  | https://web.fulcrumapp.com/photos/view?photos=0d336e74-9921-430b-bf62-9374459e387d | Concrete | Grout Hole | Leaks |  | Not Reinforcement
196fa392-a586-4afb-a2f0-e532719790ec | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 08:24:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 587 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93664 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 587, 7 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over two areas of 200mm x 150mm and 150mm x 400mm. |  | Radial joint has grout Delamination / Drummy Grout over two areas of 200mm x 150mm and 150mm x 400mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Inaccessible due to the pipeline being in the way. | [8 empty] | Concrete | Radial Joint | Drummy
433f5ad8-d956-4c31-b6cd-2a9e5a4f367c | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:17:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 588 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36798 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 588, 1 o'clock, Segment Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 300 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300 mm x 300 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition at the time of inspection | no |  |  |  |  | ce83c599-9c7a-4daf-8b4a-6bd3292fa9f2 |  | https://web.fulcrumapp.com/photos/view?photos=ce83c599-9c7a-4daf-8b4a-6bd3292fa9f2 | Concrete | Circular Joint,Reinforcement | Drummy
34b1521b-edcc-4dcb-8118-53323cbf56be | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 12:22:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 588 | 11 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 101805 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 45553.6291 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 588, 11 O'clock, Segmented Bolted Joint (Radial Joint) |  |  |  | 0.3mm crack at radial segment bolted joint grout. |  | 0.3mm crack at radial segment bolted joint grout. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | As per the previous observation, conditions unchanged | no |  |  |  |  | e0021b49-f8d0-4574-8c3b-24b143d76b4d,09998de0-0346-4391-938a-c8b7bb4c972a | , | https://web.fulcrumapp.com/photos/view?photos=e0021b49-f8d0-4574-8c3b-24b143d76b4d%2C09998de0-0346-4391-938a-c8b7bb4c972a | Concrete | Radial Joint | Crack
da3a341b-84ae-4d34-a8b2-ac6f03f1753e | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:47:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 588 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84109 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.5374 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 588, 3 o'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Corrosion. |  | Channel anchor bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | Steel channel and anchor bolt is severely corroded | no |  |  |  |  | 6ca51f3f-74b2-4c3c-9d0b-e15925863a6d |  | https://web.fulcrumapp.com/photos/view?photos=6ca51f3f-74b2-4c3c-9d0b-e15925863a6d | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface |  | Only Corrosion Surface
bfabc013-ffc2-436d-8022-9d50a8b3c782 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:18:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 588 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84110 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 588, 4 o'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition at the time of inspection | no |  |  |  |  | 94b8eae2-f0a6-4831-8779-5ee10c36c2b0 |  | https://web.fulcrumapp.com/photos/view?photos=94b8eae2-f0a6-4831-8779-5ee10c36c2b0 | Concrete | Circular Joint,Radial Joint | Drummy |  | Radial And circular Joint
d0262073-d2ed-4b31-a8cb-4234ea29519e | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:46:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 588 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27336 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 588, 2, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Missing bolt at 3 O'clock. Level 2 to Level 4 corrosion at anchor bolts of steel bracket. |  | Missing bolt at 3 O'clock. Level 2 to Level 4 corrosion at anchor bolts of steel bracket. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Double up , as its the part of same structure | no |  |  |  |  | e269ae78-76e3-4e4e-92de-572d692d277f,f43ed47d-3358-421f-ab1a-974418939688 | , | https://web.fulcrumapp.com/photos/view?photos=e269ae78-76e3-4e4e-92de-572d692d277f%2Cf43ed47d-3358-421f-ab1a-974418939688 | Steel | Channel Bracket-Bolt | Missing
ac304390-b33b-467a-aec6-37b27c620b64 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 12:14:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 589 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27347 |  | 6512 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 17/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 589, 2 o'clock, Concrete Shell Segment | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete |  | Concrete shell segment has drummy concrete | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of production and services | Priority: P3 |  |  |  | Remediate concrete as per BHP Standards and specifications | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | Scaffolding | Working at Heights, Hot Work | Engineering Repair Methodology Required Competent Supervisor | KP |  | No change in the condition | no |  |  |  |  | cdfdc305-ab6b-4ede-868a-60aad435d9af |  | https://web.fulcrumapp.com/photos/view?photos=cdfdc305-ab6b-4ede-868a-60aad435d9af | Concrete | Circular Joint | Drummy |  | Not reinforcement. Circular Joint
c3de52b5-f41a-4ba1-8dc5-6a2d3b4a135a | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 13:50:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 589 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93665 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 589, 7 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | No change in the condition, drummy grout still present | no |  |  |  |  | 6bf9dd38-e953-416b-a46d-b250c4412aeb |  | https://web.fulcrumapp.com/photos/view?photos=6bf9dd38-e953-416b-a46d-b250c4412aeb | Concrete | Radial Joint | Drummy
ef7b56ab-441d-4c35-b2c6-93a38ff00ca5 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3741 | 118.6347 | POINT (118.6346772 -20.3740512) | 2025-05-27 20:13:18 AEST | 2025-07-24 12:13:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 590 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27013 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 590, 2,3 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion. Channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 2 corrosion. Channel anchor bolts have Level 2 corrosion. | Loss of services. |  | Loss of services. |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Conditions unchanged. | no |  |  |  |  | 82b81e2a-313b-4374-a51a-3dc30e2cdb86,34c37c2a-d332-4b03-92dd-a7b60ae4aa00 | , | https://web.fulcrumapp.com/photos/view?photos=82b81e2a-313b-4374-a51a-3dc30e2cdb86%2C34c37c2a-d332-4b03-92dd-a7b60ae4aa00 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface |  | No Heavy Corrosion
b58701a0-bfe2-40a7-9ce1-f2b3d8df02e0 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-28 16:33:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 590 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93667 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Assessed | 16/08/2023 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 6 | Condition Rating 6 | Condition Rating 6 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 4. >= US$250 million, < US$2 billion |  | Severity Level 4. >= US$250 million, < US$2 billion | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 590, 5 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over two areas of 100mm x 100mm and 200mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over two areas of 100mm x 100mm and 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Safety | 26/02/2025 AC: As per agreed with GTS Structural Engineer (KM), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition | no |  |  |  |  | 1df3f388-4fe2-43b1-8891-7440c9142ba9 |  | https://web.fulcrumapp.com/photos/view?photos=1df3f388-4fe2-43b1-8891-7440c9142ba9 | Concrete | Circular Joint,Radial Joint | Drummy
170ef0b3-9f95-44ea-939b-d9eec1a76700 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 12:35:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 590 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101806 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 590, 9 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | [5 empty] | d2536ef8-c62c-4d4c-b80f-bfc49b44a200 |  | https://web.fulcrumapp.com/photos/view?photos=d2536ef8-c62c-4d4c-b80f-bfc49b44a200 | Concrete | Circular Joint | Drummy
7ba00802-131b-4cb7-b2e6-1621e217c3d7 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 12:28:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 591 | 8 | Grout Injection Hole | Grout Injection Hole |  | 36799 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 591, 8 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Active at time of inspection. |  | Grout injection hole has Leak - Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | RT |  | Leakage has not stopped and sipping salt noted on surface. Condition 4 | [5 empty] | d9664945-a32d-41fd-92bb-d304114c5f3f |  | https://web.fulcrumapp.com/photos/view?photos=d9664945-a32d-41fd-92bb-d304114c5f3f | Concrete | Grout Hole | Leaks |  | Not Reinforcement
d604d122-6f9c-48fc-aec6-c9abd59862d6 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 11:49:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 592 | 5 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 93668 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 45154.8401 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Almost Certain (Failure within 1 year) |  | Almost Certain (Failure within 1 year) | Ring 592, 5 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 3 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | 2x drummy grout patch repair on 200x200mm on both sides of steel supporting of walkway on radial joint | yes |  |  |  |  | f4fc0363-5266-44a6-ab1f-3192ed0da3f4,41d8abde-c00b-4fd3-80e3-8df605995c2c | , | https://web.fulcrumapp.com/photos/view?photos=f4fc0363-5266-44a6-ab1f-3192ed0da3f4%2C41d8abde-c00b-4fd3-80e3-8df605995c2c | Steel | Radial Joint | Drummy
20fe83fd-a86f-459b-bc95-54c4fd1576d5 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3782 | 118.6321 | POINT (118.6320933 -20.3781767) | 2025-05-27 20:13:18 AEST | 2025-07-30 11:23:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 593 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 93666 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 593, 9 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Patch repair failure cause localised spalling over an area of 150mm x 150mm. |  | Patch repair failure cause localised spalling over an area of 150mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Condition unchanged | no |  |  |  |  | a203e157-ba6b-4d45-afed-8f14638059a8 |  | https://web.fulcrumapp.com/photos/view?photos=a203e157-ba6b-4d45-afed-8f14638059a8 | Concrete | Circular Joint | Surface Damage |  | Circula joint
5fb55725-b73c-4c1f-803f-6899bbbdfbd1 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 11:21:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 594 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27014 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 594, 2,3 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion. Steel channel support bracket anchor bolts have Level 2 Corrosion at 2 O'clock. One anchor bolt missing at 11 O'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. |  | Steel channel support bracket has Level 2 corrosion. Steel channel support bracket anchor bolts have Level 2 Corrosion at 2 O'clock. One anchor bolt missing at 11 O'clock. One bolt is required per group of three bolt holes as per 117-C-00241/3. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Conditions unchanged Cs:-2 | [5 empty] | 7f58d205-8155-42e0-a0e9-bced75cbb57c,810fcf5b-e3b2-427a-83d1-9a6e6dc7c8a4 | , | https://web.fulcrumapp.com/photos/view?photos=7f58d205-8155-42e0-a0e9-bced75cbb57c%2C810fcf5b-e3b2-427a-83d1-9a6e6dc7c8a4 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
a7e987f7-ef8a-4a67-8349-b2e75c9fce50 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 11:30:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 594 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36800 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Assessed | 23/06/2023 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 6 | Condition Rating 6 | Condition Rating 6 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring: 594, 5 O'clock: Segment Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at segment bolted joints at two locations of sizes 200mm x 200mm each. |  | Grout Delamination / debonding at segment bolted joints at two locations of sizes 200mm x 200mm each. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 26/02/2025 AC: As per agreed with GTS Structural Engineer (KM), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition, drummy patch repair | no |  |  |  |  | fcb7b200-5ca1-4e7c-965c-b82900c378e8 |  | https://web.fulcrumapp.com/photos/view?photos=fcb7b200-5ca1-4e7c-965c-b82900c378e8 | Concrete | Radial Joint | Drummy |  | Not Reinforcement
7eb865c3-c3b3-4e37-a0be-61d7165f6e6d | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-30 05:39:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 595 | 7 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93669 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 595, 7 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over two areas of the same size around 200mm x 300mm each. |  | Radial joint has grout Delamination / Drummy Grout over two areas of the same size around 200mm x 300mm each. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Unable to access defect. Filled with mud. | [8 empty] | Concrete | Radial Joint | Drummy
a0226956-b9d7-41ae-87f4-2acd763c9ca7 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 11:07:33 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 596 | 4 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84112 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.5416 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 596,4 o'Clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is loose. |  | One channel anchor bolt is loose. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line |  |  |  |  | KP |  | On charges in the condition during the inspection | no |  |  |  |  | 19234e67-ca54-4bec-84b8-992c21be6737 |  | https://web.fulcrumapp.com/photos/view?photos=19234e67-ca54-4bec-84b8-992c21be6737 | Steel | Channel Bracket-Bolt | Loose
e7214366-f9c7-4643-a0a9-0456dfaa5f38 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 11:12:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 596 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36801 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Assessed | 23/06/2023 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 6 | Condition Rating 6 | Condition Rating 6 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring: 596, 5 O'clock: Segment Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at segment bolted joints at two locations at the sizes of 200mm x 200mm. |  | Grout Delamination / debonding at segment bolted joints at two locations at the sizes of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 26/02/2025 AC: As per agreed with GTS Structural Engineer (KM), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | Drummy patch repair, no charge in condition | no |  |  |  |  | 68575715-87c2-4638-a83d-8b52e2e392e8 |  | https://web.fulcrumapp.com/photos/view?photos=68575715-87c2-4638-a83d-8b52e2e392e8 | Concrete | Radial Joint | Drummy |  | Not Reinforcement
c636ad8c-815a-405d-ac69-b117b6695f8a | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 11:04:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 597 | 5 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93670 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 16/08/2023 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 597, 5 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | KP |  | The drummy concrete patch still in the same condition , no change | no |  |  |  |  | 01c48002-5407-45aa-9d7a-f4c63fd22f57 |  | https://web.fulcrumapp.com/photos/view?photos=01c48002-5407-45aa-9d7a-f4c63fd22f57 | Concrete | Circular Joint | Drummy
9d3eb7d8-49bc-48dc-a9a1-74667031e387 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 11:36:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 598 | 11 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36803 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 598, 11 o'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200 mm x 200 mm each |  | Radial joint has Grout Delamination / Drummy Grout over two areas of the same size around 200 mm x 200 mm each | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), revised recommended action and included repair methodology provided by GTS. 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Local structural failure. | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor | Kp |  | Unchanged, still drummy grout. | [5 empty] | dcc69880-59c4-4f7f-90d1-aade24fe7618,69c6fa1a-609b-4b5a-86b9-88025c5ab2f4 | , | https://web.fulcrumapp.com/photos/view?photos=dcc69880-59c4-4f7f-90d1-aade24fe7618%2C69c6fa1a-609b-4b5a-86b9-88025c5ab2f4 | Concrete | Radial Joint | Drummy |  | Not Reinforcement
13d46a51-56e0-4544-bc8a-d918d2ab5050 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-24 11:30:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 598 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 27016 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 598, 2,3 & 11, 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 1 corrosion. One bolt missing at 3 o'clock. |  | Steel channel support bracket anchor bolts have Level 1 corrosion. One bolt missing at 3 o'clock. | Loss of services. |  | Loss of services. |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | KP |  | Unchanged in condition | [5 empty] | 87fb85e0-0e1f-4dd2-ba8a-4d62eb58efbf,ab3ec79d-1889-4ee2-936b-7c1f49a20bad,80df491c-045d-4835-8e32-1275e30e7b43 | ,, | https://web.fulcrumapp.com/photos/view?photos=87fb85e0-0e1f-4dd2-ba8a-4d62eb58efbf%2Cab3ec79d-1889-4ee2-936b-7c1f49a20bad%2C80df491c-045d-4835-8e32-1275e30e7b43 | Steel | Channel Bracket-Bolt | Missing |  | Only bolt
cecd4967-4f0b-4be7-8d8a-3dd99b106849 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3782 | 118.6321 | POINT (118.6320676 -20.3781853) | 2025-05-27 20:13:18 AEST | 2025-07-30 11:22:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 598 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93672 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 598, 8 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Grout Delamination / debonding at segment bolted joints at two locations of sizes 200mm x 200mm. |  | Grout Delamination / debonding at segment bolted joints at two locations of sizes 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | RT |  | Some repair work done, drumminess in patch repair. | [5 empty] | 17cfc940-468c-462d-83e6-228782fc60e9 |  | https://web.fulcrumapp.com/photos/view?photos=17cfc940-468c-462d-83e6-228782fc60e9 | Concrete | Circular Joint,Radial Joint | Drummy |  | Radial Joint and Circular Joint
c36474b3-74ed-4961-8978-0e85f66f5d39 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-27 11:02:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 598 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36802 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Assessed | 23/06/2023 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 6 | Condition Rating 6 | Condition Rating 6 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring: 598, 5 O'clock: Segment Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at segment bolted joints over two areas of sizes 200mm x 200mm. |  | Grout Delamination / debonding at segment bolted joints over two areas of sizes 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 26/02/2025 AC: As per agreed with GTS Structural Engineer (KM), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. 04/10/2023 AC: As per agreed with GTS Structural Engineers (Avinash Gehlot), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | The radial joint patch repair is still drummy, no change | no |  |  |  |  | d60b99bb-010b-468c-af02-ab7dea3bed49 |  | https://web.fulcrumapp.com/photos/view?photos=d60b99bb-010b-468c-af02-ab7dea3bed49 | Concrete | Radial Joint | Drummy |  | Not Reinforcement
0ac2795c-bef5-4033-a8ce-31897779ccc5 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3217 | 118.5853 | POINT (118.5852578 -20.3216681) | 2025-05-27 20:13:18 AEST | 2025-07-28 15:44:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 600 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27634 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 600, 1, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1 to Level 2) and lower bolt (Level 4 to Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1 to Level 2) and lower bolt (Level 4 to Level 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | Bolts are rusted on steel channel at 1 o’clock, 3 o’clock. But to water logging at the bottom 7 o’clock and 4 o’clock (o’clock) was not being inspected | no |  |  |  |  | 178cf53a-ceca-43db-99fc-6cc2ad790e64,b8d17aa8-3508-49c3-830e-b1a88ef222a5,ef87e3fd-88e6-4bed-b200-7c1d873705b3,dc495d34-b6de-439e-9394-6c915f209cfd | ,,, | https://web.fulcrumapp.com/photos/view?photos=178cf53a-ceca-43db-99fc-6cc2ad790e64%2Cb8d17aa8-3508-49c3-830e-b1a88ef222a5%2Cef87e3fd-88e6-4bed-b200-7c1d873705b3%2Cdc495d34-b6de-439e-9394-6c915f209cfd | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
63c75adf-57df-4485-9fee-d3fd238b28d8 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 24 | -20.3741 | 118.6347 | POINT (118.6346753 -20.3740649) | 2025-05-27 20:13:18 AEST | 2025-07-28 15:55:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 600 | 5 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36804 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Assessed | 23/06/2023 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 6 | Condition Rating 6 | Condition Rating 6 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring: 600, 5 O'clock: Segment Bolted Joint (Radial Joint). | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at segment bolted joints at two locatrions of sizes 200mm x 200mm. |  | Grout Delamination / debonding at segment bolted joints at two locatrions of sizes 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 26/02/2025 AC: As per agreed with GTS Structural Engineer (KM), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of production and services | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | No change in the condition, drummy concrete at the time of inspection | no |  |  |  |  | 7da88185-7904-46e6-9ca3-48bbc27ea1cf |  | https://web.fulcrumapp.com/photos/view?photos=7da88185-7904-46e6-9ca3-48bbc27ea1cf | Concrete | Radial Joint | Drummy |  | Not Reinforcement
e54b2887-37ab-42bd-b7f4-fbe2ae48585d | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 19 | -20.3175 | 118.5798 | POINT (118.5797673 -20.3174842) | 2025-06-01 09:58:25 AEST | 2025-07-24 17:09:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 600 | 7 |  |  | Column footing | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [7 empty] | Corrosion | [31 empty] | KP |  | Severely corroded steel column,MIC | [5 empty] | 6ef900a3-0137-4071-9ed2-7a6fc92257cb,b99602c2-62ec-4f5a-bf2b-1b5418e0c4b2,4eeba9ab-e05a-42d4-9abc-f476a92350cf | ,, | https://web.fulcrumapp.com/photos/view?photos=6ef900a3-0137-4071-9ed2-7a6fc92257cb%2Cb99602c2-62ec-4f5a-bf2b-1b5418e0c4b2%2C4eeba9ab-e05a-42d4-9abc-f476a92350cf | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface
ee852736-3036-42ce-a665-06f48a530fd1 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 16 |  |  |  | 2025-07-24 12:24:32 AEST | 2025-07-28 08:38:12 AEST | 30011704-user5@smec.com | james.stone@smec.com | 587 | 11 |  | Grout Injection Hole | [57 empty] | KP |  | Presence of Chlorine leaks buildups | [5 empty] | 5174eef2-0dc2-4c92-a308-9ec66a9d7d4b |  | https://web.fulcrumapp.com/photos/view?photos=5174eef2-0dc2-4c92-a308-9ec66a9d7d4b | Concrete | Grout Hole | Leaks
aca39d10-ddd1-4446-8e1d-dcf2bac412b4 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 16 |  |  |  | 2025-07-24 15:08:32 AEST | 2025-07-24 15:09:44 AEST | 30011704-user5@smec.com | james.stone@smec.com | 579 | 12 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy concrete along the patch repair section. CS:- 1 | [5 empty] | 52c1b06f-50f2-4f4b-9d56-1bc6e8f2d467 |  | https://web.fulcrumapp.com/photos/view?photos=52c1b06f-50f2-4f4b-9d56-1bc6e8f2d467 | Concrete | Circular Joint | Drummy
2112fdc6-a0b3-48ab-9ec1-4433ae653b1e | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 16 |  |  |  | 2025-07-24 15:09:50 AEST | 2025-07-24 15:10:40 AEST | 30011704-user5@smec.com | james.stone@smec.com | 579 | 11 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy patch repair section. | [5 empty] | 00df35d7-52d3-4b46-a320-cf121ff51c0a |  | https://web.fulcrumapp.com/photos/view?photos=00df35d7-52d3-4b46-a320-cf121ff51c0a | Concrete | Circular Joint | Drummy
def40372-3d1b-4fda-b221-141136fef22e | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 16 |  |  |  | 2025-07-24 15:15:41 AEST | 2025-07-24 15:17:54 AEST | 30011704-user5@smec.com | james.stone@smec.com | 578 | 12 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy patch repair work | [5 empty] | bac7e518-1760-403b-9171-5c880077dae7,e3868547-08d6-4e51-b943-4f854136d9b7 | , | https://web.fulcrumapp.com/photos/view?photos=bac7e518-1760-403b-9171-5c880077dae7%2Ce3868547-08d6-4e51-b943-4f854136d9b7 | Concrete | Circular Joint | Drummy
7aa709dd-9eca-4cfd-a4cc-4934a06f6ecd | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 16 |  |  |  | 2025-07-24 15:17:58 AEST | 2025-07-24 15:28:10 AEST | 30011704-user5@smec.com | james.stone@smec.com | 578 | 12 |  | Segment Bolted Joint (Radial Joint) | [57 empty] | KP |  | Drummy patch repair work along the radial joint CS:- 3 | [5 empty] | 7407302f-28b5-41ab-85f0-c5223e65e3d7 |  | https://web.fulcrumapp.com/photos/view?photos=7407302f-28b5-41ab-85f0-c5223e65e3d7 | Concrete | Radial Joint | Drummy
08a02340-dbca-4a42-93fa-0067fc52b5cd | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 16 |  |  |  | 2025-07-24 15:35:15 AEST | 2025-07-24 15:36:57 AEST | 30011704-user5@smec.com | james.stone@smec.com | 576 | 12 |  | Segment Bolted Joint (Circle Joint) | [17 empty] | 1 | [39 empty] | KP |  | Drummy patch repair along the circumferential joint 30x30 CS:- 1 | [5 empty] | 9c3006dc-cbf9-455f-910e-b8ad360a6af4 |  | https://web.fulcrumapp.com/photos/view?photos=9c3006dc-cbf9-455f-910e-b8ad360a6af4 | Concrete | Circular Connection,Circular Joint | Drummy
9eacaaa5-d2ea-473a-ab14-248d497252b0 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 16 |  |  |  | 2025-07-24 15:48:40 AEST | 2025-07-24 15:49:35 AEST | 30011704-user5@smec.com | james.stone@smec.com | 574 | 12 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummer patch repair work along the circumferential joint | [5 empty] | f98add25-9fbd-403d-90fa-6cc8d0a78031 |  | https://web.fulcrumapp.com/photos/view?photos=f98add25-9fbd-403d-90fa-6cc8d0a78031 | Concrete | Circular Connection,Circular Joint
6a525d27-ca0c-4c03-8724-01473bb34daa | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 16 | -20.3782 | 118.6321 | POINT (118.6320808 -20.3781817) | 2025-07-24 15:49:37 AEST | 2025-07-30 11:22:19 AEST | 30011704-user5@smec.com | james.stone@smec.com | 574 | 10 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy patch repair work along the circumferential joint. | [5 empty] | 4b36a334-4c0f-4a67-919f-c3b068d18684 |  | https://web.fulcrumapp.com/photos/view?photos=4b36a334-4c0f-4a67-919f-c3b068d18684 | Concrete | Circular Connection,Circular Joint | Drummy
0440da8e-bd1b-4817-9621-a2efeb222100 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 | -20.3178 | 118.5797 | POINT (118.5797172 -20.3178311) | 2025-07-24 10:53:45 AEST | 2025-07-24 17:09:27 AEST | 30011704-user5@smec.com | james.stone@smec.com | 599 | 8 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess in the concrete close to the circumferencial joint. 50x20mm, condition 3. | [5 empty] | 1361d6a4-75d7-406c-8149-59155f985e67 |  | https://web.fulcrumapp.com/photos/view?photos=1361d6a4-75d7-406c-8149-59155f985e67 | Concrete | Circular Joint | Drummy
ea0e1c3e-9eec-4702-8e18-65e5e1481e31 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 | -20.3782 | 118.6321 | POINT (118.6320833 -20.3781795) | 2025-07-24 11:07:27 AEST | 2025-07-24 11:48:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | 599 | 10 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Visible patch repair 40x30cm, condition 1 | [5 empty] | 96555880-14b3-4356-8711-ae1272e91bda |  | https://web.fulcrumapp.com/photos/view?photos=96555880-14b3-4356-8711-ae1272e91bda | Concrete | Circular Joint |  |  | Circular Joint
12985ac3-ab7d-411c-b0a6-5845a6628edb | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 |  |  |  | 2025-07-24 11:26:12 AEST | 2025-07-28 16:10:18 AEST | 30011704-user5@smec.com | james.stone@smec.com | 598 | 10 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess at patchwork 25x25cm, condition 2. | [5 empty] | e026c239-626a-4557-b0e4-80c38c6c4808 |  | https://web.fulcrumapp.com/photos/view?photos=e026c239-626a-4557-b0e4-80c38c6c4808 | Concrete |  | Drummy
8b733051-643c-420e-bf43-e98ecb8a6650 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 |  |  |  | 2025-07-24 11:28:00 AEST | 2025-07-24 11:48:44 AEST | 30011704-user5@smec.com | james.stone@smec.com | 599 | 8 |  | Hydrophilic Joint Seal (Radial Joint) | [57 empty] | RT |  | Patch work at radial joint 10x20cm, condition 2 | [5 empty] | 5e1d38ae-8c46-4d36-923b-8a457a1d6e49 |  | https://web.fulcrumapp.com/photos/view?photos=5e1d38ae-8c46-4d36-923b-8a457a1d6e49 | Concrete | Circular Joint,Radial Joint |  |  | Circular joint and radial joint
56b21b13-50f0-4dc8-a73a-4703c33d9d82 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 | -20.3742 | 118.6338 | POINT (118.6338198 -20.3741663) | 2025-07-24 11:50:25 AEST | 2025-07-24 20:52:31 AEST | 30011704-user5@smec.com | james.stone@smec.com | 596 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Patchwork noted without drumminess. | [5 empty] | 9b364e5f-90de-426e-9cf3-c4a5389e7235 |  | https://web.fulcrumapp.com/photos/view?photos=9b364e5f-90de-426e-9cf3-c4a5389e7235 | Concrete | Circular Joint,Radial Joint | Drummy |  | Circular and Radial Joint
f4cf4432-d8fa-4152-91d2-8720daa32a26 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 | -20.3782 | 118.6321 | POINT (118.6320869 -20.3781774) | 2025-07-24 11:55:19 AEST | 2025-07-24 11:58:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 596 | 8 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Patchwork without drumminess, 50x50cm. Condition 1 | [5 empty] | 587f9e68-6733-468a-9d81-05d53ba3c470,2dda40e8-f3b9-47e7-be04-2f45843fcbb1 | , | https://web.fulcrumapp.com/photos/view?photos=587f9e68-6733-468a-9d81-05d53ba3c470%2C2dda40e8-f3b9-47e7-be04-2f45843fcbb1 | Concrete | Radial Joint | Drummy |  | Radial Joint
457cba7f-9ae9-48f7-a7fe-f5b11962060a | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 |  |  |  | 2025-07-24 12:00:15 AEST | 2025-07-24 12:02:53 AEST | 30011704-user5@smec.com | james.stone@smec.com | 595 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Patchwork along circumferencial joint no drumminess. Condition 1 | [5 empty] | 3b46fe69-dde5-4bb5-9afa-33c47c886fa9 |  | https://web.fulcrumapp.com/photos/view?photos=3b46fe69-dde5-4bb5-9afa-33c47c886fa9 | Concrete | Circular Joint | Drummy
44c56f7f-22f4-4348-a456-bae05b714058 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 | -20.3741 | 118.6338 | POINT (118.6338182 -20.3741383) | 2025-07-24 12:08:31 AEST | 2025-07-24 20:52:12 AEST | 30011704-user5@smec.com | james.stone@smec.com | 594 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Drumminess in the patchwork 50mmx200 and 150x500mm, condition 2 | [5 empty] | 04919962-0b26-497b-8af6-2efe8503fa42 |  | https://web.fulcrumapp.com/photos/view?photos=04919962-0b26-497b-8af6-2efe8503fa42 | Concrete | Circular Joint | Drummy |  | Circular joint
1a2d2529-0e53-47c9-904a-fa0c3121f14b | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 | -20.318 | 118.5773 | POINT (118.5773095 -20.318019) | 2025-07-24 12:11:09 AEST | 2025-07-24 20:50:46 AEST | 30011704-user5@smec.com | james.stone@smec.com | 594 | 10 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Patchwork seen around circumferencial ring. | [5 empty] | 33162a55-69a1-4742-ab89-66353a8def82 |  | https://web.fulcrumapp.com/photos/view?photos=33162a55-69a1-4742-ab89-66353a8def82 | Concrete | Circular Connection |  |  | Circular connection
ac8af69d-1ef0-46a6-a937-90c2618ec822 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 18 | -20.318 | 118.5773 | POINT (118.5773157 -20.3180466) | 2025-07-24 12:28:58 AEST | 2025-07-24 12:30:00 AEST | 30011704-user5@smec.com | james.stone@smec.com | 591 | 8 |  | Segment Bolted Joint (Circle Joint) | [57 empty] | RT |  | Patchwork noted with no drumminess. Condition 1 | [5 empty] | fcbda50c-54ff-4108-a6e6-ef0b62432368 |  | https://web.fulcrumapp.com/photos/view?photos=fcbda50c-54ff-4108-a6e6-ef0b62432368 | Concrete | Circular Joint | Drummy
614a796c-1f5f-4b50-8bdc-86bdd3040c7b | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 17 | -20.3194 | 118.5815 | POINT (118.5814883 -20.3193676) | 2025-07-24 15:13:25 AEST | 2025-07-28 08:29:00 AEST | 30011704-user5@smec.com | james.stone@smec.com | 578 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Patch work delaminating with drummy concrete 200x500mm. Condition 3 | [5 empty] | 07961906-b0c9-4405-bd69-7cdeb7c2cbc1 |  | https://web.fulcrumapp.com/photos/view?photos=07961906-b0c9-4405-bd69-7cdeb7c2cbc1 | Concrete | Circular Joint | Drummy |  | Circular Joint
58bb20d2-1075-4877-8254-7d1538bd1fe1 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 17 | -20.3185 | 118.5804 | POINT (118.5803583 -20.318495) | 2025-07-24 15:17:54 AEST | 2025-07-28 08:29:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 578 | 10 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | RT |  | Patchwork delaminating & Drummy Concrete. 400x400mm. Condition 3 | [5 empty] | d9af44be-64f7-4ac4-8775-1b685a2d09dc |  | https://web.fulcrumapp.com/photos/view?photos=d9af44be-64f7-4ac4-8775-1b685a2d09dc | Concrete | Circular Joint | Drummy |  | Circular Joint
d5bc34c2-c850-42a0-98be-d3298f6279de | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 17 | -20.3202 | 118.5826 | POINT (118.5825578 -20.3202426) | 2025-07-24 16:01:51 AEST | 2025-07-24 20:48:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 587 | 6 |  |  | Steel support structure | [56 empty] | RT |  | Rusted I beam support structure with considerable loss of flange thickness. Condition 4 | [5 empty] | 8a758062-0919-46bc-9603-3be0c9d57d0c |  | https://web.fulcrumapp.com/photos/view?photos=8a758062-0919-46bc-9603-3be0c9d57d0c | Steel | Centre Support
2077836e-8d11-40b4-81b6-64de49fc00c8 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 17 | -20.318 | 118.5773 | POINT (118.5773217 -20.318046) | 2025-07-24 16:09:31 AEST | 2025-07-28 08:37:31 AEST | 30011704-user5@smec.com | james.stone@smec.com | 591 | 6 |  |  | Steel support structure | [56 empty] | RT |  | Rusted I Beam support structure with thickness loss. | [5 empty] | 96444c10-3016-4a3b-a596-283d2fc65fed |  | https://web.fulcrumapp.com/photos/view?photos=96444c10-3016-4a3b-a596-283d2fc65fed | Steel | Centre Support
b7311905-3cb3-4553-b2c2-c34cdd3f6aba | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 17 | -20.3199 | 118.5821 | POINT (118.5821393 -20.3199228) | 2025-07-24 16:18:45 AEST | 2025-07-24 17:10:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 591 | 7 |  | Steel Channel Bracket | [57 empty] | RT |  | Support Channel bolt rusted. Condition 3 | [5 empty] | 1fadecc0-b156-4286-b06d-0c5f515c4fc9 |  | https://web.fulcrumapp.com/photos/view?photos=1fadecc0-b156-4286-b06d-0c5f515c4fc9 | Steel | Conveyor Support |  |  | Conveyor Support not Channel Bracket
a3704b34-a85f-4212-adf6-c7e32fb0796b | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 12 |  |  |  | 2025-07-27 10:56:35 AEST | 2025-07-27 11:28:21 AEST | 30011704-user5@smec.com | james.stone@smec.com | 598 | 4 o’clock |  | Steel Channel Bracket | [32 empty] | Ring 598, 4 o’clock | [24 empty] | KP |  | The steel channel has missing bolts, with some surface corrosion | [5 empty] | d904c7e8-df78-47f1-8c21-6a2962c5991d |  | https://web.fulcrumapp.com/photos/view?photos=d904c7e8-df78-47f1-8c21-6a2962c5991d | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
5b22a394-459d-4b0f-b15a-d07473e305eb | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 12 |  |  |  | 2025-07-27 11:23:44 AEST | 2025-07-27 11:28:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 594 | 4 o clock | [34 empty] | Ring 594, 4 o’clock | [24 empty] | KP |  | The steel channel as well as the bolt has corroded | [5 empty] | 5f507048-b8df-438b-b1aa-c22df122965e |  | https://web.fulcrumapp.com/photos/view?photos=5f507048-b8df-438b-b1aa-c22df122965e | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface |  | Steel Channel
772d6736-c9d6-4d0b-ab09-9e21ea29198e | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 12 |  |  |  | 2025-07-27 12:10:30 AEST | 2025-07-27 12:11:57 AEST | 30011704-user5@smec.com | james.stone@smec.com | 590 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy concrete work along the circumferential joint | [5 empty] | 395eceab-08c5-4c2a-a7a1-7d4ba53832a9 |  | https://web.fulcrumapp.com/photos/view?photos=395eceab-08c5-4c2a-a7a1-7d4ba53832a9 | Concrete | Circular Connection,Circular Joint | Drummy
3de28ee1-4edb-4df6-b25d-3b3585f95ef2 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 12 |  |  |  | 2025-07-27 12:21:16 AEST | 2025-07-27 12:22:42 AEST | 30011704-user5@smec.com | james.stone@smec.com | 587 | 4 o’clock |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | KP |  | Drummy concrete 200x 200 mm | [5 empty] | 6de3eb58-be8e-444f-b010-df027731aeb0,80562c04-7f0e-4c61-9cec-4754c43434cb | , | https://web.fulcrumapp.com/photos/view?photos=6de3eb58-be8e-444f-b010-df027731aeb0%2C80562c04-7f0e-4c61-9cec-4754c43434cb | Concrete | Middle of Panel | Drummy |  | Middle of the Panel
a88e6ac4-38a6-4f1e-a144-6e2e25eb45ab | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 12 |  |  |  | 2025-07-27 12:45:17 AEST | 2025-07-27 12:47:05 AEST | 30011704-user5@smec.com | james.stone@smec.com | 583 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummer patch work 30x 200mm | [5 empty] | b1506aaf-5a4c-40cf-a6ff-1106da8d2c1b |  | https://web.fulcrumapp.com/photos/view?photos=b1506aaf-5a4c-40cf-a6ff-1106da8d2c1b | Concrete | Circular Joint
caa6ab08-aa1a-46aa-a582-6c1e78bc6a2a | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 12 |  |  |  | 2025-07-27 12:50:13 AEST | 2025-07-27 12:51:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 582 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [32 empty] | Ring 582 , 4 o’clock | [24 empty] | KP |  | Drummy / delimitated grouting along the circumferential joint | [5 empty] | f62cceb9-74f6-4441-80c1-507a7a09215f |  | https://web.fulcrumapp.com/photos/view?photos=f62cceb9-74f6-4441-80c1-507a7a09215f | Concrete | Circular Connection,Circular Joint | Drummy
d0e57aab-8669-4cf1-988e-0a1f53447fbb | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 12 |  |  |  | 2025-07-27 13:24:16 AEST | 2025-07-27 13:26:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | 577 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Grout Delimitation / drummy along the circumferential joint 100 x 100mm | [5 empty] | 8c4d23c2-da1b-4046-9e45-e0f1b6601d21 |  | https://web.fulcrumapp.com/photos/view?photos=8c4d23c2-da1b-4046-9e45-e0f1b6601d21 | Concrete | Circular Connection,Circular Joint | Drummy
46bea5e6-034f-4512-a78e-7bec63855350 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 12 |  |  |  | 2025-07-27 13:45:17 AEST | 2025-07-27 13:46:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 573 | 4 o’clock |  | Segment Bolted Joint (Circle Joint) | [57 empty] | KP |  | Drummy/ delimitated grout 100x100mm along the circumferential joint | [5 empty] | 34a33566-8ffd-4923-a7c4-51e130cdc1b1 |  | https://web.fulcrumapp.com/photos/view?photos=34a33566-8ffd-4923-a7c4-51e130cdc1b1 | Concrete | Circular Connection,Circular Joint | Drummy
0c52d9e6-ffd8-47a9-bf37-0d8821ee0d10 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | e5e55a2a-2e7b-480e-9988-a0a945287b37 | 13 |  |  |  | 2025-07-27 11:29:03 AEST | 2025-07-28 08:35:26 AEST | 30011704-user5@smec.com | james.stone@smec.com | 572 | 7 O'Clock |  |  | Structure footing | [56 empty] | RT |  | Corroded footing with active rust. Moderate Likelihood of failing. Priority medium | [5 empty] | 052f8cb4-6e42-43d6-a71d-d126d7f4e45b |  | https://web.fulcrumapp.com/photos/view?photos=052f8cb4-6e42-43d6-a71d-d126d7f4e45b | Steel | Conveyor Support | Corrosion-Surface |  | Conveyor Support
8bbc202b-4ad0-4e1b-be8e-31a958ee2c2e | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 20 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 08:19:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 602 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 84114 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 44859.5427 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 602, 1 o'clock, Concrete shell segment |  |  |  | Concrete shell segment has Cracking - Hair line crack extending 0.3m and 0.2mm in width. |  | Concrete shell segment has Cracking - Hair line crack extending 0.3m and 0.2mm in width. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [5 empty] | Condition similar | Crack did not extend from previous inspection. | no |  |  |  |  | ed519e0b-2eb0-4106-aa8c-270090a3ad29,ec7cad19-0f32-4fe4-8b7d-f4d66f781042 | , | https://web.fulcrumapp.com/photos/view?photos=ed519e0b-2eb0-4106-aa8c-270090a3ad29%2Cec7cad19-0f32-4fe4-8b7d-f4d66f781042 | Concrete | Radial Joint | Crack |  | Radial Joint
5e949161-11f7-46ff-a317-292269a00e64 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 21:57:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 602 | 12 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36805 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7462 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 602, 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe). |  | Loss of minor services (NOT water pipe). |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [5 empty] | Corrcondition advancing especially between 12 an 1 o'clock. | Corrosion has advanced. Corrosion protection required. | yes |  |  |  |  | d8e7ead3-9eef-47a2-bb14-44ebb19c54e3,accc3dee-8d1d-4cd8-81c8-392bb28dd1f4 | , | https://web.fulcrumapp.com/photos/view?photos=d8e7ead3-9eef-47a2-bb14-44ebb19c54e3%2Caccc3dee-8d1d-4cd8-81c8-392bb28dd1f4 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
a24cdae2-1cdb-41fa-a0b1-78cb3594f86e | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 21:58:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 602 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93671 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Assessed | 16/08/2023 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 602, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm x 2. |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm x 2. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 26/02/2025 AC: As per agreed with GTS Structural Engineer (KM), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Safety | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Not accessible | [8 empty] | Concrete | Radial Joint | Drummy
651efee5-547d-46a5-b378-893072e490d1 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 21:59:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 603 | 10 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 36807 |  | 8516 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Repair Verified | 23/06/2023 |  | 24/10/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 603, 10 o'clock. Concrete shell segment - Segment bolted joint (radial joint). | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Radial joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. Repair verified LC 10/10/24 | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor |  | Fair condition | Clear sign of previous water ingress. Dry at time of inspection with no signs of further deterioration from the last inspection. | no |  |  |  |  | 8a65b7c1-568d-4b62-9e34-b039fb76a9d5,34d4d50e-9eda-47a0-b969-f523b43cb6af,f9213b69-4112-401f-bd00-ba1656aaf420 | Bolt 10 o'clock ,Bolt 10 o'clock close-up ,concrete etching. | https://web.fulcrumapp.com/photos/view?photos=8a65b7c1-568d-4b62-9e34-b039fb76a9d5%2C34d4d50e-9eda-47a0-b969-f523b43cb6af%2Cf9213b69-4112-401f-bd00-ba1656aaf420 | Concrete | Grout Hole | Drummy |  | Not radial joint or reinforcement - Should be grout hole
344f33ed-3001-41c3-ba75-bc10a5b26a92 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 10:14:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 603 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93673 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 603, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 150mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 150mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  | Fair condition | Concrete delimitation is still present, with no modification from the last inspection. | no |  |  |  |  | 127d5d79-6192-45d3-896b-8cab11f48e8e |  | https://web.fulcrumapp.com/photos/view?photos=127d5d79-6192-45d3-896b-8cab11f48e8e | Concrete | Circular Joint | Drummy
29e7bab4-1b06-4b28-a57e-9956c43ef197 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 10:19:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 604 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36809 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7493 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 604, 1 &3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [5 empty] | Good condition | Steel bracket in good condition. Surface corrosion to anchor bolts nuts. | no |  |  |  |  | 5d43413a-9b5b-4fd8-8d40-d68e18099f7e,41f3a491-08f0-494e-8b67-477d72eda29b,8612daa6-c0f3-4c59-ba54-ec44c88e0959 | ,, | https://web.fulcrumapp.com/photos/view?photos=5d43413a-9b5b-4fd8-8d40-d68e18099f7e%2C41f3a491-08f0-494e-8b67-477d72eda29b%2C8612daa6-c0f3-4c59-ba54-ec44c88e0959 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
5159600c-0409-4f5a-bd09-2492a682934c | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:06:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 604 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27637 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 604, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Level 1 corrosion on supporting baseplates of conveyor supports. Repair on anchor bolts have already been carried out as per standard repair details. |  | Level 1 corrosion on supporting baseplates of conveyor supports. Repair on anchor bolts have already been carried out as per standard repair details. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not accessible | [8 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
0754a479-fff0-4bd7-80e3-93fb00d29643 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:08:06 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 604 | 4 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 36808 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7486 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Almost Certain (Failure within 1 year) |  | Almost Certain (Failure within 1 year) | Ring: 604, 4 O'clock: Segment Bolted Joint (Radial Joint). |  |  |  | Grout Delamination / debonding at segment bolted joints. |  | Grout Delamination / debonding at segment bolted joints. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 3 | [5 empty] | No | Off-Line | [5 empty] | Shallow delamination | No change in condition from last inspection | no |  |  |  |  | 354a5ff5-cc43-4fba-b351-f67f915ced2b |  | https://web.fulcrumapp.com/photos/view?photos=354a5ff5-cc43-4fba-b351-f67f915ced2b | Concrete | Radial Joint | Drummy
c7770f10-59e1-460b-a709-2ef9e5c1ebe1 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:11:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 604 | 4 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 36806 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7473 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Almost Certain (Failure within 1 year) |  | Almost Certain (Failure within 1 year) | Ring: 604, 4 O'clock: Segment Bolted Joint (Radial Joint). |  |  |  | Grout Delamination / debonding at segment bolted joints over an area of 200mm x 200mm. |  | Grout Delamination / debonding at segment bolted joints over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 3 | [5 empty] | Yes | Off-Line | [6 empty] | Should be on Ring 605. No changes from the last inspection | no |  |  |  |  | 29379316-4d1a-4a1b-8274-14c75ae2bdde |  | https://web.fulcrumapp.com/photos/view?photos=29379316-4d1a-4a1b-8274-14c75ae2bdde | Concrete | Radial Joint | Drummy
81421964-9d09-436c-b20d-64a88cb9b4fa | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 10:15:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 605 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101783 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 605, 3 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | No change noted from previous inspection | no |  |  |  |  | cf7a1fa1-3cd7-4305-bc1c-ff6a9be89b46 |  | https://web.fulcrumapp.com/photos/view?photos=cf7a1fa1-3cd7-4305-bc1c-ff6a9be89b46 | Concrete | Circular Joint | Drummy
7160e9c7-71f4-4c7f-9a27-6596bb752808 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:13:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 606 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84115 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 606, 1 o'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | No change in the defect | no |  |  |  |  | 57a78019-4fee-4118-86a7-b73bc557fcf9 |  | https://web.fulcrumapp.com/photos/view?photos=57a78019-4fee-4118-86a7-b73bc557fcf9 | Concrete | Channel Bracket | Leaks |  | Channel Bracket
6df932d4-6475-471b-853a-ddcc5c8240fb | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:17:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 606 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 27018 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 606, 3 & 10, 11, 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 corrosion. Bolt missing at 3 o'clock. Steel channel support bracket has Level 2 corrosion. |  | Steel channel support bracket anchor bolts have Level 2 corrosion. Bolt missing at 3 o'clock. Steel channel support bracket has Level 2 corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [5 empty] | Fair condition | No significant change is noted from the previous inspection. Light support bracket level 3 corrosion. | no |  |  |  |  | 9f27001c-0e8b-4429-94d8-e6bc182ec551,c507b4c8-e943-4438-a829-cc61a12f6a19,b1900b30-e3ef-41a0-92b2-6e8050d0a00a,57dd9887-46f3-41cd-b70a-6f542e28cebd | "Surface corrosion, especially at the holes location ",No corrosion noted,3 o'clock , | https://web.fulcrumapp.com/photos/view?photos=9f27001c-0e8b-4429-94d8-e6bc182ec551%2Cc507b4c8-e943-4438-a829-cc61a12f6a19%2Cb1900b30-e3ef-41a0-92b2-6e8050d0a00a%2C57dd9887-46f3-41cd-b70a-6f542e28cebd | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
b577dc83-880e-474e-ba90-164d6578ded7 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:15:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 606 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93674 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 16/08/2023 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 606, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Not accessible | [8 empty] | Concrete | Radial Joint | Drummy
5d05ca9e-4803-462c-9eb2-7ff5ba6be896 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:17:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 608 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27638 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 608, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. |  | Steel channel support bracket anchor bolts have Level 2 Corrosion. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [5 empty] | Fair condition | There is no significant change in defect condition . | no |  |  |  |  | b5fc4cb6-b0ff-42f9-936f-2910440acfb2,e32ec2ad-f5c8-43fc-b3d8-89d1cdb25e9a | , | https://web.fulcrumapp.com/photos/view?photos=b5fc4cb6-b0ff-42f9-936f-2910440acfb2%2Ce32ec2ad-f5c8-43fc-b3d8-89d1cdb25e9a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
8dcde143-7020-4459-b41a-544c113110fe | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:18:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 608 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36810 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7501 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 608, 1, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1) and lower bolt (Level 4 to Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1) and lower bolt (Level 4 to Level 5). | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | No significant change from previous inspection | no |  |  |  |  | 16e42f1c-fac9-4cb6-91e7-d4ae8fcf5e27 |  | https://web.fulcrumapp.com/photos/view?photos=16e42f1c-fac9-4cb6-91e7-d4ae8fcf5e27 | Steel | Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
48e505ed-8be0-4cee-bf74-66cb75d00a52 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:20:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 609 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84116 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 609, 11 o'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 200mm x 200mm and 300mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 200mm x 200mm and 300mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  | Fair condition | The defect is still present, and no further deterioration is noted to Ring 609. | no |  |  |  |  | 1492c916-d1ca-44d4-b434-04fdffa94fee |  | https://web.fulcrumapp.com/photos/view?photos=1492c916-d1ca-44d4-b434-04fdffa94fee | Concrete | Circular Joint | Drummy
d32c15bf-673c-4eb1-99f5-4ba02e82eaa3 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 10:40:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 610 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27021 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 610, 2,3 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Some anchor bolts loose. Steel channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 2 corrosion up to 25% coverage. Some anchor bolts loose. Steel channel anchor bolts have Level 2 corrosion. | Loss of services |  | Loss of services |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [5 empty] | Fair condition | No change from previous condition. Position 2, 3 and 12. Not 0 | no |  |  |  |  | 1f2183fd-3aa6-484a-8f58-ad15e00d9b9a,888eaa34-fab9-4164-81a6-43d95a6cf3f9 | 10-11 o'clock ,11-12 o'clock | https://web.fulcrumapp.com/photos/view?photos=1f2183fd-3aa6-484a-8f58-ad15e00d9b9a%2C888eaa34-fab9-4164-81a6-43d95a6cf3f9 | Steel | Channel Bracket,Channel Bracket-Bolt | Loose
5eca4c37-38e0-4d06-82ac-3ee58aa1f707 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:35:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 610 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 36811 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 610, 3 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200 mm x 200 mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Channel bolt nut not fully tighten. New nut noted on on bolt. Delamination is still present. There was no visible extension of damage from the last inspection. Previous repair has failed. | no |  |  |  |  | 30d38be0-94cf-45f7-9383-e80380a6aaa4,52a44e39-1ead-4115-bb95-9ee013ef672b,e3ee61ee-f5ce-40af-9ced-622114691a95,1be9e79c-341e-4350-be83-e8a1d34cee6f | Loose nut ,New nut ,Extension of damage from 610 to 609,failed patching repair | https://web.fulcrumapp.com/photos/view?photos=30d38be0-94cf-45f7-9383-e80380a6aaa4%2C52a44e39-1ead-4115-bb95-9ee013ef672b%2Ce3ee61ee-f5ce-40af-9ced-622114691a95%2C1be9e79c-341e-4350-be83-e8a1d34cee6f | Concrete | Channel Bracket-Bolt,Circular Joint,Reinforcement | Drummy,Loose |  | Loose
83f79575-c835-4af6-b7f0-725c1e483c46 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 10:49:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 610 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 93675 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 610, 8 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Patch repair | yes |  |  |  |  | 68f9a97d-d11d-448f-8041-a5fb540b0a44,1f6eae88-2a32-42bb-84cb-9b8463cfeadb | , | https://web.fulcrumapp.com/photos/view?photos=68f9a97d-d11d-448f-8041-a5fb540b0a44%2C1f6eae88-2a32-42bb-84cb-9b8463cfeadb | Concrete | Circular Joint | Drummy
93f4f5a5-b0ee-4a6f-bb6e-5f095ce39ea7 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:35:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 611 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 101807 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 611, 12 O'clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  | Remains the same | No change | no |  |  |  |  | 2a1bca95-30c8-4f43-b522-50e2293a9991,9af837f5-2844-4780-a4b1-9d730d66dd94 | , | https://web.fulcrumapp.com/photos/view?photos=2a1bca95-30c8-4f43-b522-50e2293a9991%2C9af837f5-2844-4780-a4b1-9d730d66dd94 | Concrete | Circular Joint | Drummy |  | Circular Joint not Radial
1bb58b15-c900-4cda-a13d-46fa091d07a8 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 06:00:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 612 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 101784 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 18/09/2024 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 612, 3 O'clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt Not Specified |  | Shear failure of bolt Not Specified | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Circle joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for | - |  | Priority: P3 | 80dbd20b-d251-4ea5-b669-1b098286b517 |  | https://web.fulcrumapp.com/photos/view?photos=80dbd20b-d251-4ea5-b669-1b098286b517 | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  | No change | [9 empty] | Concrete | Circular Joint | Drummy
b0f2f7c3-04db-47c2-b566-62ba89ecf28e | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 06:02:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 612 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84117 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 44859.5463 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 612, 3 o'Clock, Channel Anchor Bolts |  |  |  | One channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). |  | One channel anchor bolt is missing. 07/09/2023 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Not a reportable defect, delete this in the next inspection. 24/09/2024 AIE comments: 117-E-00184/1 indicates that holes to be surveyed and drilled according to blind holes on concrete segments (different to the bracket at 12 o'clock). Bolt is missing at this location as the blind hole is visible from the photo. This is a typical defect as per UHT SIM Inspection Procedure 0142588 (Section 5.10). | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line | [5 empty] | No change | [6 empty] | 0fbf815a-bc28-4b22-ac61-68a977abd063,3d9cbfcd-cd3e-4fa7-be26-40c8e58adbd0 | , | https://web.fulcrumapp.com/photos/view?photos=0fbf815a-bc28-4b22-ac61-68a977abd063%2C3d9cbfcd-cd3e-4fa7-be26-40c8e58adbd0 | Concrete | Channel Bracket-Bolt | Missing
39b860ee-a038-405e-91e6-3a0cb9badd37 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 06:05:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 612 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 93676 |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 16/08/2023 |  | No | No | No | Concrete Damage due to Cast- In | Concrete Damage due to Cast- In |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Atmospheric Corrosion of Cast-In | Atmospheric Corrosion of Cast-In |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 612, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Radial joint has grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Damage mechanism is a result of corrosion of embedded bolts at grout pockets likely due to chloride induced and not atmospheric exposure. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  | No change | [6 empty] | 0dd78d5d-4b97-4e0d-a8fe-b825e728467f |  | https://web.fulcrumapp.com/photos/view?photos=0dd78d5d-4b97-4e0d-a8fe-b825e728467f | Concrete | Radial Joint | Drummy
757ed1bb-0b91-4adb-a65a-7ff5630daf7e | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 22:07:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 612 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27341 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 612, 2, 3, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Missing nuts at 2 & 3 O'clock. Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1 & Level 2) and lower bolt (Level 5). |  | Missing nuts at 2 & 3 O'clock. Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 1 & Level 2) and lower bolt (Level 5). | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [7 empty] | no |  |  |  |  | 25da8be3-bac9-42cb-8d16-f15e17ee9718,286377e6-0dec-4ea6-b617-558e430312ff | , | https://web.fulcrumapp.com/photos/view?photos=25da8be3-bac9-42cb-8d16-f15e17ee9718%2C286377e6-0dec-4ea6-b617-558e430312ff | Steel | Channel Bracket-Bolt | Missing
830842bd-d241-4041-a901-fc9da48110c4 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 06:16:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 613 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36812 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7516 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 613, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket anchor bolts have Level 2 - Medium Low Corrosion. |  | Steel channel support bracket anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | SS | [5 empty] | 07510cf1-e7c6-44ef-859e-d1f370768b30 |  | https://web.fulcrumapp.com/photos/view?photos=07510cf1-e7c6-44ef-859e-d1f370768b30 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
f5b4e56e-6575-41aa-8cb3-590930713fe5 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 614 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 84578 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 44872.7435 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 614, 2 & 3 o'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings |  |  |  | Embedded steel lugs have Level 2 Minor Corrosion |  | Embedded steel lugs have Level 2 Minor Corrosion | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line | [15 empty] | Concrete,Steel |  | Corrosion-Surface
1412a8d4-10f2-4462-ad5f-63364283d97d | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 614 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36814 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7531 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 614, 2,3 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 1 corrosion up to 5% coverage. Steel channel support bracket anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion up to 5% coverage. Steel channel support bracket anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [15 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
b15f0b0f-4061-42c6-bd22-644d0798c304 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 22:19:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 614 | 0 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 36813 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7523 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 614, 2,3 & 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has level 3 corrosion up to 5% coverage. Steel channel support bracket anchor bolts have Level 3 - Medium corrosion. |  | Steel channel support bracket has level 3 corrosion up to 5% coverage. Steel channel support bracket anchor bolts have Level 3 - Medium corrosion. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | This appears to be available double entrance. This entrance may relate to Posiion 10, where channel corrosion Level 3 is noted and on connecting bolts. | no |  |  |  |  | a1909ea9-94d2-40f3-a188-bc34e776857e,a6213ed0-3917-416a-af7d-70ee2f1c99b3,0396f47a-d680-44d0-a659-738ee913f5ea | Channel and bolt corrosion ,Steel loss of section up to 2mm either side of flange ,Bolt head corrosion and localised corrosion to channel web | https://web.fulcrumapp.com/photos/view?photos=a1909ea9-94d2-40f3-a188-bc34e776857e%2Ca6213ed0-3917-416a-af7d-70ee2f1c99b3%2C0396f47a-d680-44d0-a659-738ee913f5ea | Steel | Channel Bracket,Radial Joint | Corrosion-Heavy,Corrosion-Surface
da30f9dc-6498-4149-8bef-4fd46ce34b6d | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:42:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 615 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 36815 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 43901.7537 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring: 615, 2, 4 & 7 O'clock: Steel Anchor Bolts. |  |  |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 3 & Level 4) and lower bolt (Level 5). |  | Corrosion of anchor bolt of walkway and conveyor supports: upper bolt (Level 3 & Level 4) and lower bolt (Level 5). | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | 2 o'clock damage noted visible, 4 o'clock not accessible, 7 o'clock not accessible. Left over bolt at 3 o'clock corrosion level 3. | [5 empty] | 39622cbb-c4c0-4dff-9c4c-acf90720076d,708e98e4-3e6e-4139-a148-c640f89f2596 | Corroded anchor ,1 an 2 o'clock Ring 615 areas | https://web.fulcrumapp.com/photos/view?photos=39622cbb-c4c0-4dff-9c4c-acf90720076d%2C708e98e4-3e6e-4139-a148-c640f89f2596 | Steel | Channel Bracket-Bolt,Conveyor Support-Bolt | Corrosion-Heavy,Corrosion-Surface
82f6f5e8-3154-41ee-81c3-e41eb8ebdfd2 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:44:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 616 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68667 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 616, 11 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | loss of service | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor |  |  | Condition unchanged | no |  |  |  |  | 0ae1710b-6ad2-4732-acd1-f32db759c57e |  | https://web.fulcrumapp.com/photos/view?photos=0ae1710b-6ad2-4732-acd1-f32db759c57e | Concrete | Grout Hole | Leaks |  | NOt reinforcement
13afa6b1-b4c8-4913-b806-9fac45eb23c1 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:50:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 616 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27349 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 616, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 - Major Corrosion. Two anchor bolts are missing. Cable tray has Level 3 - Medium Corrosion |  | Steel channel support bracket has Level 4 - Major Corrosion. Two anchor bolts are missing. Cable tray has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. Defect 27350 closed out and added to this as single repair. | Loss of services. | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all repair affected areas, corroded areas. 3. Replace missing anchor bolts as per original design. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0. Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. Electrical Crew. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor |  |  | Anchor bolts missing. Corrosion level unchanged, especially at lower end of channel. | no |  |  |  |  | ee3bd0ed-0540-4883-b6cb-660041d94e84,2c43690f-d5c5-41dc-968e-a8069743e8d2 | , | https://web.fulcrumapp.com/photos/view?photos=ee3bd0ed-0540-4883-b6cb-660041d94e84%2C2c43690f-d5c5-41dc-968e-a8069743e8d2 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing |  | not misc
a7ccfddc-2575-4cae-a56e-c717b8589638 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 11:20:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 616 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96827 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 616, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Patch repair | yes |  |  |  |  | 63f0fe2f-1ccc-4714-978d-46a13eb692b5 |  | https://web.fulcrumapp.com/photos/view?photos=63f0fe2f-1ccc-4714-978d-46a13eb692b5 | Concrete | Circular Joint | Drummy |  | Not Reinforcement
495b455f-85d2-420e-8c56-3d5e896a672a | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:51:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 616 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27644 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 616,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not accessible | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
41a141c3-61bb-4858-93eb-4fdd8b31deba | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:51:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 616 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27645 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 616,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not accessible | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
7766c1a1-be62-4150-bbbd-21e84e6db7db | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:52:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 617 | 11 | Grout Injection Hole | Grout Injection Hole |  | 96828 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 617, 11 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - Inactive at time of inspection. |  | Grout injection hole has leak - Inactive at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Impact to durability of other elements. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | No changes from the last inspection | no |  |  |  |  | 3b38ab0b-c825-4a53-bec0-586bbb0ca045 |  | https://web.fulcrumapp.com/photos/view?photos=3b38ab0b-c825-4a53-bec0-586bbb0ca045 | Concrete | Grout Hole | Leaks
6edf429f-ab29-4597-922e-460062d83016 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:54:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 617 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84580 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 7/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 617, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | No change from previous inspection | no |  |  |  |  | 1d6f2ca6-2c1a-4862-aaba-d02ae5e29a57 |  | https://web.fulcrumapp.com/photos/view?photos=1d6f2ca6-2c1a-4862-aaba-d02ae5e29a57 | Concrete | Circular Joint | Drummy
ae120129-31b8-41ae-8598-c8608a1bb48b | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:57:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 618 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 68668 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Carbonation Induced |  | Carbonation Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 618, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor |  |  | No change from previous inspection | no |  |  |  |  | a99bfe2d-d1d4-4272-ab81-c19f27ebdc25,5b32db1d-695c-4087-9feb-a515e0d85aa5,f3a92e69-74e2-4575-9927-e7f60751154e,035767f6-0260-46c7-a77f-df0d4e2d7896,08296fc4-0cfa-4ac3-ab4b-31b47406b780 | Defect general view. ,Close up at 10 o'clock , Close up at 11 o'clock ,, | https://web.fulcrumapp.com/photos/view?photos=a99bfe2d-d1d4-4272-ab81-c19f27ebdc25%2C5b32db1d-695c-4087-9feb-a515e0d85aa5%2Cf3a92e69-74e2-4575-9927-e7f60751154e%2C035767f6-0260-46c7-a77f-df0d4e2d7896%2C08296fc4-0cfa-4ac3-ab4b-31b47406b780 | Concrete |  | Leaks |  | Not Reinforcement
b47c19fa-fa04-4355-9908-49b7ab6a5cb1 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 22:58:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 618 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 68712 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44540.2354 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 618, 11 to 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 5% coverage. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 5% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | No change from previous inspection | no |  |  |  |  | 106ee7db-562f-4b7a-9f65-d5d550946e5d,6f73bb85-8e0e-478b-ba35-5a1d57d16b41 | , | https://web.fulcrumapp.com/photos/view?photos=106ee7db-562f-4b7a-9f65-d5d550946e5d%2C6f73bb85-8e0e-478b-ba35-5a1d57d16b41 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
20032703-276a-43df-b471-d73f5dbb412c | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 22:31:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 618 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84581 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 7/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 618, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | No change noted. The delamination appears to be contained and may be produced during bolt joint sealing. | no |  |  |  |  | cee25812-7f2f-4576-88b9-c55b3ec14ff3 |  | https://web.fulcrumapp.com/photos/view?photos=cee25812-7f2f-4576-88b9-c55b3ec14ff3 | Concrete | Circular Joint | Drummy
d53fb3be-b84b-4422-ba3b-651963718f2e | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 11:42:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 618 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96830 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 618, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Patch Repair previous inspection and Drummy concrete | yes |  |  |  |  | 49c1cd07-1e28-4c9a-8299-b2426ffad17a,6bc5f13a-ec50-4e95-91d8-137cdc591e67,84d01511-80fd-40e0-a76b-d301f147ffc3,a92ce984-8481-4170-9f48-96c6a537da26 | ,,, | https://web.fulcrumapp.com/photos/view?photos=49c1cd07-1e28-4c9a-8299-b2426ffad17a%2C6bc5f13a-ec50-4e95-91d8-137cdc591e67%2C84d01511-80fd-40e0-a76b-d301f147ffc3%2Ca92ce984-8481-4170-9f48-96c6a537da26 | Concrete | Circular Joint | Drummy |  | Not Reinforcement
ea226f83-a0a4-404a-ac18-9c84322dd113 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 23:01:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 619 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84582 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 7/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 619, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | 146dda34-4b2d-456e-866d-ad81b29bdf62 |  | https://web.fulcrumapp.com/photos/view?photos=146dda34-4b2d-456e-866d-ad81b29bdf62 | Concrete | Circular Joint | Drummy
b85a77fa-dced-4375-b74d-d29c86f90ed9 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 23:12:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 619 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84583 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 619, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination extended to Ring 618. Shallow Delamination. | yes |  |  |  |  | 6d6a3855-8b64-4216-a1e6-9203e6a12339,5ea3ca31-817e-4a63-ad47-40b6b4a2dbef | ,Delamination on Ring 618 | https://web.fulcrumapp.com/photos/view?photos=6d6a3855-8b64-4216-a1e6-9203e6a12339%2C5ea3ca31-817e-4a63-ad47-40b6b4a2dbef | Concrete | Circular Joint | Drummy
10c28c63-51d1-45c4-a4ab-c5a07780c2ca | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 11:47:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 619 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96831 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 619, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Patch repair | yes |  |  |  |  | 84878dcd-4da6-4c32-9f7f-63fa3d162e34,25d031fa-97b8-4094-a5b6-654901700ec6,6c24cf14-f44e-44c1-9a5a-a18903582abe | ,, | https://web.fulcrumapp.com/photos/view?photos=84878dcd-4da6-4c32-9f7f-63fa3d162e34%2C25d031fa-97b8-4094-a5b6-654901700ec6%2C6c24cf14-f44e-44c1-9a5a-a18903582abe | Concrete | Circular Joint | Drummy |  | Not Reinforcement
a8ca050a-dae4-46c2-a69a-bbae1bcec1f7 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 22:51:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 620 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68713 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 620, 11 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor |  |  | Same condition and situation as per previous inspection | no |  |  |  |  | 9adf7883-363f-4e31-b225-eb19ce9805f5,8d8f2605-7055-4aaa-baef-8eb13d4bec90 | , | https://web.fulcrumapp.com/photos/view?photos=9adf7883-363f-4e31-b225-eb19ce9805f5%2C8d8f2605-7055-4aaa-baef-8eb13d4bec90 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
b3c12141-dd32-4df2-9a93-20a8c4a58217 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 23:16:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 620 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84584 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 620, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | aff365eb-aeb7-4f88-af9c-ce8a52ec9911 |  | https://web.fulcrumapp.com/photos/view?photos=aff365eb-aeb7-4f88-af9c-ce8a52ec9911 | Concrete | Circular Joint | Drummy
7bda8a46-3d33-4125-ba44-ff0ce353b38d | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 23:29:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 620 | 4 | Steel Channel Bracket | Steel Channel Bracket |  | 27646 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 620,4 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not fully accessible. After removal of corrosion, the estimated section loss on structural plate up to 1mm. Anchor bolt heavily corroded past nut. Nut heavily corroded. | no |  |  |  |  | adf4d58d-23f1-42c7-a1aa-1c847ef041fe,de0886c0-5fa7-411b-acce-c0e704808dc3 | ,Bolt and nut connection | https://web.fulcrumapp.com/photos/view?photos=adf4d58d-23f1-42c7-a1aa-1c847ef041fe%2Cde0886c0-5fa7-411b-acce-c0e704808dc3 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
9867e5ea-4e9c-4824-a6f4-51779ce83035 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 23:33:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 621 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68714 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 621, 11 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor |  |  | Similar to previous condition | no |  |  |  |  | fe113a29-b3d5-410c-8121-d22e8274cc64,9a42bbda-eb60-4180-b016-422c80521a65,c880134c-ea8d-4d9d-ae34-31ae685e3b0a | ,, | https://web.fulcrumapp.com/photos/view?photos=fe113a29-b3d5-410c-8121-d22e8274cc64%2C9a42bbda-eb60-4180-b016-422c80521a65%2Cc880134c-ea8d-4d9d-ae34-31ae685e3b0a | Concrete | Grout Hole | Leaks |  | Not Reinforcement
34203d8a-9f93-4930-b1a1-2cd43acb7653 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 23:32:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 621 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84585 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 621, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | c9a388d6-e710-49e3-9b6d-e79b86b4f159 |  | https://web.fulcrumapp.com/photos/view?photos=c9a388d6-e710-49e3-9b6d-e79b86b4f159 | Concrete | Circular Joint | Drummy
a8ce7728-a561-4c75-a571-3787c4fb7643 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 22:55:03 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 622 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27022 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 5 | Level 5 | Level 5 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 622, 11 to 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. Two channel anchor bolts have Level 5 Corrosion. |  | Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. Two channel anchor bolts have Level 5 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Condition level updated to reflect bolt condition. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace severely corroded anchor bolts. Alternatively, repair anchor bolts as per BHP standard drawing 000-S-12598. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Bottom 2 abhor bolt heads missing. Sufficient bolts remain for safe connection. Channel corrosion level not change from previous inspection. | yes |  |  |  |  | 7d5fa0cc-27b8-4b6a-b5ac-81972e085f1a |  | https://web.fulcrumapp.com/photos/view?photos=7d5fa0cc-27b8-4b6a-b5ac-81972e085f1a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
5c1403e9-6738-4f83-993d-a03753dbf74c | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-29 23:42:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 622 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84586 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 622, 3 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | Three channel anchor bolts are missing. |  | Three channel anchor bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolt as per approved design drawing. | GTS Specification. Concrete remediation crew. | No | Off-Line | No | Walkway | - | Replace Component Competent Supervisor |  |  | One bolt is missing. 2 bolts supporting the channel. | no |  |  |  |  | 3cd6aeb1-bccb-4631-ae0a-b9afec211fc4,de0d21bc-bcde-4d6a-9925-41a7356065a7 | Missing bolt ,2 bolts still active | https://web.fulcrumapp.com/photos/view?photos=3cd6aeb1-bccb-4631-ae0a-b9afec211fc4%2Cde0d21bc-bcde-4d6a-9925-41a7356065a7 | Steel | Channel Bracket-Bolt | Missing
cf7bac49-8a01-4dd9-97dd-32a107dc4bfb | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:27:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 623 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68715 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 623, 11 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor |  |  | Similar condition at the time of current inspection as per previous inspection. Similar condition found at 3 o'clock generated fron injection hole. | no |  |  |  |  | 119dfdea-f3d1-4550-bff6-2b0f87aa5a2c,78aecfeb-53dc-4199-8a87-dbf03dad3921,301d04c5-9616-4810-9d2f-e211f79f8b06,0f93d86b-abeb-435a-8661-4af67593ee15,0da33e2f-2d9c-477c-8f8d-746f6be74e09 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=119dfdea-f3d1-4550-bff6-2b0f87aa5a2c%2C78aecfeb-53dc-4199-8a87-dbf03dad3921%2C301d04c5-9616-4810-9d2f-e211f79f8b06%2C0f93d86b-abeb-435a-8661-4af67593ee15%2C0da33e2f-2d9c-477c-8f8d-746f6be74e09 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
4d57a2e9-f204-4ba1-83c1-a44c0384c7b4 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:15:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 623 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84587 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 623, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination has extended to Ring 622. Surface delamination 75mm x 150mm. | yes |  |  |  |  | b09bae59-ce66-4683-aef1-d0d3d0926516,8c49431c-90af-4035-a2e7-375fc526e64f | ,Delaminated concrete at joint. | https://web.fulcrumapp.com/photos/view?photos=b09bae59-ce66-4683-aef1-d0d3d0926516%2C8c49431c-90af-4035-a2e7-375fc526e64f | Concrete | Circular Joint | Drummy
558c94c2-7f3a-4e5e-bab6-c130e94b2f96 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:29:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 624 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68716 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 624, 11 o'clock. Concrete Shell Segment - Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor |  |  | No changes from previous inspection | no |  |  |  |  | d590adac-42bb-45e0-9cd9-e8ed604024c4,e259ca82-a9eb-426c-aa67-d39a167e61db | , | https://web.fulcrumapp.com/photos/view?photos=d590adac-42bb-45e0-9cd9-e8ed604024c4%2Ce259ca82-a9eb-426c-aa67-d39a167e61db | Concrete | Grout Hole | Leaks |  | Not Reinforcement
02ac7a2b-0083-4ad9-9eba-f129bb76f7fe | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:31:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 624 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84588 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 624, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | No change from previous inspection | no |  |  |  |  | 2f42e4af-4d3c-430f-aee9-c6d0fbafb9f5 |  | https://web.fulcrumapp.com/photos/view?photos=2f42e4af-4d3c-430f-aee9-c6d0fbafb9f5 | Concrete | Circular Joint | Drummy
c1f33c0e-be1b-41d7-a60d-5cca9e3ffec4 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:31:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 624 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27648 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 624,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not accessible | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
f002241d-48fe-4e5e-99ef-072af99531c6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:32:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 624 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27647 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 624,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not accessible | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
4f5a9774-da3b-4080-b52b-97d71a638d4f | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:33:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 625 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84594 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 625, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | 25451b11-683b-4eec-ba34-2288bbcfadba |  | https://web.fulcrumapp.com/photos/view?photos=25451b11-683b-4eec-ba34-2288bbcfadba | Concrete | Radial Joint | Drummy
9a5b9cea-b043-4c13-9216-66946d7a9f71 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:34:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 625 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84589 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 625, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | a0404162-1ed8-4685-ae0a-6ab3d38e9658 |  | https://web.fulcrumapp.com/photos/view?photos=a0404162-1ed8-4685-ae0a-6ab3d38e9658 | Concrete | Circular Joint | Drummy
eb628722-a85f-46c5-8694-1fce9bac858f | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 01:56:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 626 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27023 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 2 | Level 2 | Level 2 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 626, 1 & 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 2 Minor Corrosion 3 anchor bolts missing at 3 O'clock. |  | Steel channel support bracket has Level 2 Minor Corrosion 3 anchor bolts missing at 3 O'clock. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 BHP Comments: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-E-00184/1. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Monitor for further deterioration. Consider widescale coating / corrosion remediation project. Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor |  |  | Steel condition is similar to previous inspection. One bolt is missing at 3 o'clock. 2 bolts supporting the channel at 3 o'clock. | no |  |  |  |  | 0ca1afd0-ba29-4773-814c-78c4003bda4f,44c472bb-d81b-4ff5-825e-c639f448fc7f,acabec2c-c5e3-440e-a669-2daeb088d41a,eac17cae-1675-46a2-8f1f-a8f8c79020e3 | Channel at 1 o'clock ,Missing bolt at 3 o'clock ,Exiting bolt at 3 o'clock ,Channel at 3 o'clock | https://web.fulcrumapp.com/photos/view?photos=0ca1afd0-ba29-4773-814c-78c4003bda4f%2C44c472bb-d81b-4ff5-825e-c639f448fc7f%2Cacabec2c-c5e3-440e-a669-2daeb088d41a%2Ceac17cae-1675-46a2-8f1f-a8f8c79020e3 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
addbcd57-6f7d-4ea0-a33d-f24232c26cc4 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 02:05:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 626 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 68717 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 2 | Level 2 | Level 2 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 626, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Two (2) bolts missing or with Level 2 corrosion |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Two (2) bolts missing or with Level 2 corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Alternatively, repair anchor bolts as per BHP standard drawing 000-S-12598. | AIMS Inspector | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor |  |  |  | no |  |  |  |  | d4d5e6a6-fd61-4430-9e71-b19cc244e45c |  | https://web.fulcrumapp.com/photos/view?photos=d4d5e6a6-fd61-4430-9e71-b19cc244e45c | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
50c5471e-47c4-4832-93fd-dfd34df259de | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 13:50:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 626 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96832 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 626, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | No change | no |  |  |  |  | 3a7c567a-6888-443c-9deb-1d49a2c25080,86290822-4100-4e2c-9fda-6d61f426bfd5,25ef8950-f57a-4cf3-a36f-6e40b3798b7b | ,, | https://web.fulcrumapp.com/photos/view?photos=3a7c567a-6888-443c-9deb-1d49a2c25080%2C86290822-4100-4e2c-9fda-6d61f426bfd5%2C25ef8950-f57a-4cf3-a36f-6e40b3798b7b | Concrete | Circular Joint | Drummy |  | Not Reinforcement
412d5672-850a-443e-b089-ae792b2a6857 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 02:18:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 628 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 84595 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44873.2809 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 628, 3 O'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 3 Medium Corrosion Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. |  | Channel anchor bolts have Level 3 Medium Corrosion Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line | [6 empty] | Single bolt connection for channel. Nut not tighten. Advanced corrosion around the bolts area. | yes |  |  |  |  | 16bf86e1-4a00-4e94-ac63-262178f5ba9a |  | https://web.fulcrumapp.com/photos/view?photos=16bf86e1-4a00-4e94-ac63-262178f5ba9a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
454a5c60-8fcc-4215-ad00-30ed9267fd8e | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 02:16:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 628 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27650 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 628,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not accessible | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
45063b6b-e5d3-4147-b623-40865d6706d9 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 02:19:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 628 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27649 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 628,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not accessible | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
4d3ca882-8d8e-4cea-af3b-798b61630554 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 02:29:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 629 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84596 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 629, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | 6b83cba7-7a88-4eac-94c8-139f9aa0b028 |  | https://web.fulcrumapp.com/photos/view?photos=6b83cba7-7a88-4eac-94c8-139f9aa0b028 | Concrete | Radial Joint | Drummy
0ab9fe00-ce45-408a-9830-7c76742a0aed | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 630 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27651 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Financial | Financial |  | Missing Component | Missing Component |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 630, 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts have Level 2 Medium Low Corrosion. One channel anchor bolt is missing. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. One channel anchor bolt is missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace missing anchor bolt as per original design. | AIMS Inspector | No | Off-Line | Yes | Scaffolding | - | Replace Component Competent Supervisor | [11 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
3fbb6f92-2118-4143-be8f-18f075b858ce | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 02:32:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 630 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27353 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Financial | Financial |  | Missing Component | Missing Component |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 630, 1, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. Bolt is missing. |  | Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. Bolt is missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor |  |  | Two bolts connect the channel. One bolt is missing. | no |  |  |  |  | c49d7795-be25-4e8e-ac3b-c2d5a65b43b2,e9bf3868-7493-4d25-84b8-52e31f0b0dbf,4c86b789-b496-45e5-a69f-014c19fc951e,82d980f2-aefc-4448-971c-f86c3cf6cd7a | ,,, | https://web.fulcrumapp.com/photos/view?photos=c49d7795-be25-4e8e-ac3b-c2d5a65b43b2%2Ce9bf3868-7493-4d25-84b8-52e31f0b0dbf%2C4c86b789-b496-45e5-a69f-014c19fc951e%2C82d980f2-aefc-4448-971c-f86c3cf6cd7a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
05e4ecfe-0c60-453c-a426-76d8940fd294 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 19 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 23:27:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 630 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27025 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 630, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of services and production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor |  |  | It is not clear how this damage has been assessed previously. The concrete around the steel channel appears deteriorated due to the extensive corrosion. There are no clear signs that the concrete ring reinforcement has been affected. However, the corrosion of steel channel is due to water ingress. At the time of inspection, the area is dry with no signs of water. | [5 empty] | 0314fe54-1b89-4a86-8b13-5c3df489d058,4fcc1fb0-0c50-4c65-a62a-ea8066df1153,d43bfc27-4188-4182-8710-ca61f5712961,372e0e0b-2fc9-4c5a-88db-d2eb602a48a5,96ead5f4-be99-4bb8-b36d-80c20f8c4b4a,f2321116-9ecb-4348-8783-75b94c66d1f6 | Concrete surrounding the steel channel and water damage ,,,,, | https://web.fulcrumapp.com/photos/view?photos=0314fe54-1b89-4a86-8b13-5c3df489d058%2C4fcc1fb0-0c50-4c65-a62a-ea8066df1153%2Cd43bfc27-4188-4182-8710-ca61f5712961%2C372e0e0b-2fc9-4c5a-88db-d2eb602a48a5%2C96ead5f4-be99-4bb8-b36d-80c20f8c4b4a%2Cf2321116-9ecb-4348-8783-75b94c66d1f6 | Concrete,Steel | Channel Bracket | Leaks |  | Channel Bracket
d7a5e590-2598-468a-a272-07899a5e3d75 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 02:35:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 630 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27024 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 630, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 4 - Major Corrosion |  | Steel channel support bracket has Level 4 - Major Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Advanced corrosion noted to the steel channel and bolts. | no |  |  |  |  | 0f5314af-72c2-42e7-ac24-4e022c617f16 |  | https://web.fulcrumapp.com/photos/view?photos=0f5314af-72c2-42e7-ac24-4e022c617f16 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
05db7e3b-51bc-48c8-a552-78215809a0f0 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 23:17:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 630 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27652 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 5 | Level 5 | Level 5 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 630, 11 to 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 5 - Major Corrosion Several fasteners have Level 5 Corrosion |  | Steel channel support bracket has Level 5 - Major Corrosion Several fasteners have Level 5 Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | 1. Replace severely corroded anchor bolts. Alternatively, repair anchor bolts as per BHP standard drawing 000-S-12598. 2. Apply protective coating to extend at least 150mm past all repair affected areas, corroded areas. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | The Level 5 corrosion is localised between 10 and 11 o'clock. 2 Bolt heads in this area corroded to the condition that is not considered serviceable. Estimated loss of section between 2 and 3mm. | no |  |  |  |  | 82bad91c-9c10-4096-95d5-efc9f08804ae,8b7e7f1a-ac28-4dc6-b18f-ff58909787b8,f0991b60-28d0-44c8-a8cf-ebfc8aadff57,5b795736-9d7c-4e73-ae7e-ff50285ac056 | ,,, | https://web.fulcrumapp.com/photos/view?photos=82bad91c-9c10-4096-95d5-efc9f08804ae%2C8b7e7f1a-ac28-4dc6-b18f-ff58909787b8%2Cf0991b60-28d0-44c8-a8cf-ebfc8aadff57%2C5b795736-9d7c-4e73-ae7e-ff50285ac056 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
9af6f3c9-93fc-42f5-b5c7-03882313c42f | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 02:38:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 630 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84590 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 630, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | 3a088623-79e3-4fa7-9cc9-5222421259ed |  | https://web.fulcrumapp.com/photos/view?photos=3a088623-79e3-4fa7-9cc9-5222421259ed | Concrete | Circular Joint | Drummy
7663111b-1af8-4a85-bc78-8fe6930cc360 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 11 |  |  |  | 2025-05-29 06:17:29 AEST | 2025-05-30 22:00:31 AEST | 30011704-user5@smec.com | james.stone@smec.com | 613 | 1 |  |  |  | Ring-613-01 | [5 empty] | Ring 613 top conveyor roller brackets | [24 empty] | Ring 613 top conveyor roller brackets |  |  |  | Roller brackets on both sides are corroding, coatings failing. Section loss is currently not advanced, but should be treated. Caused by proximity to the water spray system. | [20 empty] | SS | [7 empty] | fc04f194-9539-4f4b-a59b-6a8bfcfab5b5,57ab63df-e580-4bc3-a20a-ceab6a712a81,212a192c-ec0c-4017-ba4d-5a03b6060c9c,7699f5f3-0525-436b-ace8-2683656acd30 | ,,, | https://web.fulcrumapp.com/photos/view?photos=fc04f194-9539-4f4b-a59b-6a8bfcfab5b5%2C57ab63df-e580-4bc3-a20a-ceab6a712a81%2C212a192c-ec0c-4017-ba4d-5a03b6060c9c%2C7699f5f3-0525-436b-ace8-2683656acd30 | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
72a0a338-7d9d-461e-84fa-98e8ff13c143 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 11 |  |  |  | 2025-05-29 06:28:46 AEST | 2025-05-30 22:00:10 AEST | 30011704-user5@smec.com | james.stone@smec.com | 614 | 2 |  |  |  | Ring-614-02 | [30 empty] | Ring 614 top conveyor roller brackets |  |  |  | Roller brackets on both sides are corroding, coatings failing. Section loss is currently not advanced, but should be treated. Caused by proximity to the water spray system. | [9 empty] | 23492d72-6c74-466c-9895-50d3f7913ff5,f2b02e96-7a74-4e5c-89d2-1c8f8710c3c1 | , | https://web.fulcrumapp.com/photos/view?photos=23492d72-6c74-466c-9895-50d3f7913ff5%2Cf2b02e96-7a74-4e5c-89d2-1c8f8710c3c1 | [8 empty] | SS | [10 empty] | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
0ac373bf-210b-4a65-931f-8cbc4448e93a | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 17 | -20.3739 | 118.6343 | POINT (118.6342586 -20.3738759) | 2025-05-29 06:27:04 AEST | 2025-05-30 21:59:34 AEST | 30011704-user5@smec.com | james.stone@smec.com | 614 | 12 |  |  |  | 614 - 01 |  |  |  | Ring 614 |  | Ring 614 - 3 o' clock | [24 empty] | 614 - 01 |  |  |  | Channel supporting red pipe is heavily corroded. Paint flaking. |  | Channel supporting red pipe is heavily corroded. Paint flaking. | [6 empty] | Priority 3 | [11 empty] | SS | [7 empty] | 24223265-3b72-42bb-9d2e-3dacd85bb796,6e77775a-15ff-4e6f-afd9-5d6f947eb61e | , | https://web.fulcrumapp.com/photos/view?photos=24223265-3b72-42bb-9d2e-3dacd85bb796%2C6e77775a-15ff-4e6f-afd9-5d6f947eb61e | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Surface Damage
5de4b50e-9a75-4d90-8b1c-324b3cf2140b | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 | -20.2993 | 118.5651 | POINT (118.5650633 -20.2992811) | 2025-05-29 02:33:26 AEST | 2025-05-29 04:29:02 AEST | 30011704-user5@smec.com | james.stone@smec.com |  |  | Steel tray bracket anchor |  | Steel tray bracket anchor | Ring 604, 12 o'clock service channel bracket bolt faild. | [30 empty] | Ring 604, 12 o'clock |  |  |  | One of 2 anchor bolts supporting the service tray has failed. |  | One of 2 anchor bolts supporting the service tray has failed. | [11 empty] | Yes |  | Yes. Near water sprinkler | Yes | Yes | No | Reinstate the bolt. |  | Bolt epoxy fixing failure | One of the two bolts supporting the water sprinkler main has failed. | [5 empty] | faa3211d-1795-4953-a88e-190cf1fa4e9e | Failed anchor | https://web.fulcrumapp.com/photos/view?photos=faa3211d-1795-4953-a88e-190cf1fa4e9e | Steel | Channel Bracket | Coating Failure |  | Coating Failure
f8e9fc1e-fa52-4061-ac50-ee2272a33581 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 | -20.2993 | 118.5651 | POINT (118.5650642 -20.2992843) | 2025-05-29 02:58:43 AEST | 2025-05-30 21:56:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | 607 | 11 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | BS Ring 607 Segment Bolted Joint (Circle Joint), 11 o'clock |  |  |  | Segment Bolted Joint (Circle Joint | [51 empty] | BS | Concrete delamination | Small delamination 100mmx100mm at Ring 607, 11 o'clock | [5 empty] | db556a98-9664-4347-8547-39f8f6c8d99e |  | https://web.fulcrumapp.com/photos/view?photos=db556a98-9664-4347-8547-39f8f6c8d99e | Concrete | Grout Hole | Drummy |  | Grout Hole
57119147-4398-4740-84db-0de0c034faee | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 11 |  |  |  | 2025-05-29 23:33:48 AEST | 2025-05-29 23:38:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 621 | 1 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Leak | [15 empty] | Ring 621, 1 o'clock | [24 empty] | BS |  | Defect previously marked, but no record found. Damage noted extended from previous marking. | [5 empty] | 96557a55-e562-4b92-ae2e-947858d9ae7f |  | https://web.fulcrumapp.com/photos/view?photos=96557a55-e562-4b92-ae2e-947858d9ae7f | Concrete | Grout Hole | Leaks |  | Grout Hole
8110959a-1aef-425f-a529-713c1133f3b1 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 | -20.2993 | 118.5651 | POINT (118.5650655 -20.2992869) | 2025-05-29 03:08:28 AEST | 2025-06-01 10:35:07 AEST | 30011704-user5@smec.com | james.stone@smec.com | 608 | 10 |  | Segment Bolted Joint (Radial Joint) |  | BS Ring 608 11 o'clock | [55 empty] | BS | Fair | Small delamination 70mm x 150mm at joint with Ring 609. | [5 empty] | 0531e342-4237-4842-85af-723f71ff46cd |  | https://web.fulcrumapp.com/photos/view?photos=0531e342-4237-4842-85af-723f71ff46cd | Concrete | Circular Joint | Drummy |  | Circular joint not radial
c12f7df3-772c-4485-9f32-1b07ee010e65 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 18 | -20.2993 | 118.5651 | POINT (118.5650541 -20.299285) | 2025-05-29 03:57:07 AEST | 2025-05-30 21:58:50 AEST | 30011704-user5@smec.com | james.stone@smec.com | 608 | 2 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | BS Ring 608 2 o'clock | [55 empty] | BS |  | Hairline crack, previously marked, extending from joint for 300mm. | [5 empty] | 674d8933-b953-4a51-bb3b-c4dffea3a653,22ffc832-5d87-4f17-81a5-a18c4c7faaa1 | , | https://web.fulcrumapp.com/photos/view?photos=674d8933-b953-4a51-bb3b-c4dffea3a653%2C22ffc832-5d87-4f17-81a5-a18c4c7faaa1 | Concrete | Circular Joint | Crack |  | Circular
2aa1f7c8-e53f-4440-803a-3c38c21fca8b | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7 |  |  |  | 2025-05-30 01:35:57 AEST | 2025-05-30 01:40:45 AEST | 30011704-user5@smec.com | james.stone@smec.com | 624 | 1 |  | Grout Injection Hole | [32 empty] | Leaching from injection hole. |  |  |  |  | Grout injection hole has Leak - Inactive at time of inspection. | [19 empty] | BS | [7 empty] | 231555c6-7141-456f-9670-556120d1435b,9b502ec7-03ad-45b1-86d0-6340d82b3364 | previous inspections shows an extension of surface concrete damage due to water ingress and extending along the wall.,previou marking at 1 o'clock between Ring 624 and 625. clause not assessable | https://web.fulcrumapp.com/photos/view?photos=231555c6-7141-456f-9670-556120d1435b%2C9b502ec7-03ad-45b1-86d0-6340d82b3364 | Concrete | Grout Hole | Leaks
2b6cace4-bbe7-4d82-badf-6648f2c08908 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7 |  |  |  | 2025-05-30 01:43:08 AEST | 2025-05-30 01:51:16 AEST | 30011704-user5@smec.com | james.stone@smec.com | 625 | 3 |  | Grout Injection Hole | [32 empty] | 3 o'clock grout injection hole |  |  |  |  | Grout injection hole has Leak - Inactive at time of inspection. | [19 empty] | BS |  | Concrete etching from grout injection hole. There was no significant change from the previous inspection . | [5 empty] | f4c27cc7-0f3e-4438-a929-719cb86aea62,092a1240-c13e-4087-838d-bb1364f9d326 | , | https://web.fulcrumapp.com/photos/view?photos=f4c27cc7-0f3e-4438-a929-719cb86aea62%2C092a1240-c13e-4087-838d-bb1364f9d326 | Concrete | Grout Hole | Leaks
f2731a26-551e-4a80-9915-81acd6a751ec | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 8 |  |  |  | 2025-05-30 02:12:26 AEST | 2025-05-30 02:15:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 627 | 3 |  | Segment Bolted Joint (Radial Joint) | [32 empty] | 3 o'clock at joint with Ring 626 |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | Drummy concrete at Ring bolt connection | [5 empty] | 4aec5e72-a34f-413f-8a1d-a0284df8909a |  | https://web.fulcrumapp.com/photos/view?photos=4aec5e72-a34f-413f-8a1d-a0284df8909a | Concrete | Circular Joint | Drummy |  | Not radial Joint
df7a9338-055e-4c79-9aaf-8c893a41c5f6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7 |  |  |  | 2025-05-30 02:22:40 AEST | 2025-05-30 02:27:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 628 | 2 |  | Segment Bolted Joint (Circle Joint) | [38 empty] | Horizontal cracks into the mortar, protecting the ring bolt. 0.2mm wide | [18 empty] | BS |  | Fine cracks in mortar | [5 empty] | 1debec16-00e9-41c4-a584-5f9575806315,0aec273b-a228-4757-b495-ad96b235efc1 | "Old crack, previously marked ",New crack not noted previously | https://web.fulcrumapp.com/photos/view?photos=1debec16-00e9-41c4-a584-5f9575806315%2C0aec273b-a228-4757-b495-ad96b235efc1 | Concrete | Circular Joint,Mortar | Crack
9d428238-8387-4e23-8b56-12aaee3ff12a | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 6 |  |  |  | 2025-05-30 22:02:40 AEST | 2025-05-30 22:06:15 AEST | 30011704-user5@smec.com | james.stone@smec.com | 612 | 11 |  | Grout Injection Hole | [57 empty] | BS |  | Signs of leaking at grot hole. Not active at the time of inspection. Not advanced from last marking. | [5 empty] | 268cb2e0-80e1-4235-b340-86028dac819f |  | https://web.fulcrumapp.com/photos/view?photos=268cb2e0-80e1-4235-b340-86028dac819f | Concrete | Grout Hole | Leaks
d455defc-995a-416f-8f45-adfb5585adb6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7 |  |  |  | 2025-05-30 22:37:27 AEST | 2025-05-30 22:42:27 AEST | 30011704-user5@smec.com | james.stone@smec.com | 619 | 11 |  | Segment Bolted Joint (Radial Joint) | [16 empty] | Construction | 3 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  |  | Not assessable | Ring joint between 618 and 619 at 11 o'clock |  | Shear failure of bolt |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | Mortar at bolt cover is possible due to poor workmanship. Damage effect on bolt not assessable. | [5 empty] | 6217cda1-a106-441b-802c-b9c66904bd85 |  | https://web.fulcrumapp.com/photos/view?photos=6217cda1-a106-441b-802c-b9c66904bd85 | Concrete | Mortar,Circular Joint | Drummy |  | Not radial, circular joint
c71d9606-8007-4f54-82f8-7995471a14d9 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 6 |  |  |  | 2025-05-30 22:56:32 AEST | 2025-05-30 22:59:55 AEST | 30011704-user5@smec.com | james.stone@smec.com | 629 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84596 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 629, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | New defect by SMEC. BHP number to be removed. Defect located at interface between Ring 628 and 629. | yes |  |  |  |  | d3f790b4-91b5-49ad-bd75-787bc2d9016b |  | https://web.fulcrumapp.com/photos/view?photos=d3f790b4-91b5-49ad-bd75-787bc2d9016b | Concrete | Circular Joint,Radial Joint | Drummy
b1f8792f-4bd6-43c0-a6a5-277ad39be4a1 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 5 |  |  |  | 2025-06-01 11:02:20 AEST | 2025-06-01 11:09:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 614 | 9 |  |  | Roller Belt Support Structure | [14 empty] | Corrosion - Structure Member/Platework |  | 4 | [39 empty] | KP |  | Steel Roller supports are Heavily corroded and delimitation of coating | [5 empty] | a8163864-3bbe-4baa-b2f0-a207eaeb91eb,420d46f6-6c3b-4930-b752-7cc383bfee78,4745e79f-d9fd-44f6-8f8f-2076a2e85d45,a4eedd26-fb6c-4909-bd0b-4f630d87a4a0,4f086f3b-14e8-4ea2-844a-d64d0701546a | ,,,, | https://web.fulcrumapp.com/photos/view?photos=a8163864-3bbe-4baa-b2f0-a207eaeb91eb%2C420d46f6-6c3b-4930-b752-7cc383bfee78%2C4745e79f-d9fd-44f6-8f8f-2076a2e85d45%2Ca4eedd26-fb6c-4909-bd0b-4f630d87a4a0%2C4f086f3b-14e8-4ea2-844a-d64d0701546a | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
348b26f1-3e9d-41b5-949d-8068e68ebb5c | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 5 |  |  |  | 2025-06-01 11:20:33 AEST | 2025-06-01 11:24:26 AEST | 30011704-user5@smec.com | james.stone@smec.com | 616 | 9 |  |  | Steel Roller Supporting Beam | [14 empty] | Corrosion - Structure Member/Platework |  | 5 | [39 empty] | KP |  | Heavily corroded and damaged/ failed | [5 empty] | de6162b0-4912-473f-9c25-ae4db206370c,77df4f26-5584-450b-9fdf-e791f3109888,a92da92e-fd40-4602-9cd6-adbdda0bf117 | ,, | https://web.fulcrumapp.com/photos/view?photos=de6162b0-4912-473f-9c25-ae4db206370c%2C77df4f26-5584-450b-9fdf-e791f3109888%2Ca92da92e-fd40-4602-9cd6-adbdda0bf117 | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
c6d668d9-28a3-44f6-b0f5-d5c32b704031 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 5 |  |  |  | 2025-06-01 13:39:32 AEST | 2025-06-01 13:41:02 AEST | 30011704-user5@smec.com | james.stone@smec.com | 624 | 8 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | Kp |  | Drummy Grout concrete closer to circular ring | [5 empty] | 2c698a95-4119-4b78-a227-c0f8f593ca68,3befeffd-8f46-461b-887f-f1c588902788 | , | https://web.fulcrumapp.com/photos/view?photos=2c698a95-4119-4b78-a227-c0f8f593ca68%2C3befeffd-8f46-461b-887f-f1c588902788 | Concrete | Circular Joint | Drummy |  | Circular Joint
9ffe6cbf-4e02-4d72-9325-b973432cfbfa | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-07-08 13:41:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 631 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96833 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 631, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | ac07b4cc-7ccd-44b3-9ae2-03f290d03c61 |  | https://web.fulcrumapp.com/photos/view?photos=ac07b4cc-7ccd-44b3-9ae2-03f290d03c61 | Concrete | Circular Joint | Drummy |  | Not Reinforcement
7177f8f1-3165-4344-bfdc-071cc253ebf8 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 | -20.2993 | 118.565 | POINT (118.5650371 -20.2993007) | 2025-05-27 20:13:18 AEST | 2025-05-31 00:35:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 632 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84597 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 632, 11 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 500mm x 600mm around grout injection hole. |  | Concrete shell segment has drummy concrete over an area of 500mm x 600mm around grout injection hole. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), downgraded to P3 and monitor | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Exiting drummy area remains unchanged. New drummy area identified 200mmx300mm. 0.3mm crack at the bottom corner of the segment extending 200mm. Area around the crack is drummy, indicating concrete failure. Urgent attention is required. | yes |  |  |  |  | 586db30e-dfe5-42da-9da0-cf71a6fe6393,84f7dbd4-5417-4f0a-851e-c74b46569040,63300b89-1fc9-4a51-a8f7-91208d098e14,ae9c59a8-084c-4ba7-9263-bd4333be3063,e93a4eb3-cf18-42ed-a4fe-4cb700ca92de | ,,,New drummy area ,Vertical crack at segment corner. | https://web.fulcrumapp.com/photos/view?photos=586db30e-dfe5-42da-9da0-cf71a6fe6393%2C84f7dbd4-5417-4f0a-851e-c74b46569040%2C63300b89-1fc9-4a51-a8f7-91208d098e14%2Cae9c59a8-084c-4ba7-9263-bd4333be3063%2Ce93a4eb3-cf18-42ed-a4fe-4cb700ca92de | Concrete | Corner,Grout Hole | Crack,Drummy
00c16da1-17fd-4129-a9d2-d9852b4dbe21 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 03:01:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 632 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27653 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 632, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion |  | Steel channel support bracket has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Surface corrosion to nuts and bolts. Chanel covered in dust at lower level | no |  |  |  |  | 5c386a49-e4eb-4922-befd-f55915af8a10,26446099-e623-45b4-8bfc-88adaee0fd28 | , | https://web.fulcrumapp.com/photos/view?photos=5c386a49-e4eb-4922-befd-f55915af8a10%2C26446099-e623-45b4-8bfc-88adaee0fd28 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
4dfc917b-54ae-4408-a3d3-8525fe90f0be | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 632 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27654 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 632,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [15 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
f5caeda6-da9e-4a0c-8c50-399d7c04439b | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 23 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 03:02:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 632 | 7 | Steel Channel Bracket | Steel Channel Bracket |  | 27655 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 632,7 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 3 - Medium corrosion | Class 3 - Medium corrosion |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Not accessible | [8 empty] | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
5d634ed4-4f8b-4a2b-8d0c-b44622378145 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 01:41:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 634 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27026 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 5 | Level 5 | Level 5 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 634, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 2 - Minor Corrosion. Up to 25% coverage. Level 5 Corrosion to 2 bolts. |  | Steel channel support bracket has Level 2 - Minor Corrosion. Up to 25% coverage. Level 5 Corrosion to 2 bolts. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace severely corroded anchor bolts. Alternatively, repair anchor bolts as per BHP standard drawing 000-S-12598. | Replace the missing anchor bolts as per approved drawing. Monitor for further deterioration. Consider widescale coating / corrosion remediation project. Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | Walkway | Working at Heights | Standard Repair Detail Competent Supervisor |  |  | Bottom two bolts have failed. Chanel is supported by multiple bolts in good condition. | yes |  |  |  |  | 3678ecd0-820e-42fd-91fe-928445c47fd9,ae292e5c-a675-4817-a290-5f0ca499021b,f8b6aa3e-c21c-48fd-a75b-4c80824bb799,0e1f7d8f-8b9d-43be-955c-30dfa206185a,9f92ed85-3286-48e6-ac7f-898bbbc5a115,9e8f6345-507c-4ec1-910b-394632555b27,c1621355-4537-4941-9f94-f287bca01b14,1d05eb0a-2fad-4265-95d9-1c362e80dbcf | ,,,,,Failed bottom bolt ,Failed second bolt ,Multiple bolts in place | https://web.fulcrumapp.com/photos/view?photos=3678ecd0-820e-42fd-91fe-928445c47fd9%2Cae292e5c-a675-4817-a290-5f0ca499021b%2Cf8b6aa3e-c21c-48fd-a75b-4c80824bb799%2C0e1f7d8f-8b9d-43be-955c-30dfa206185a%2C9f92ed85-3286-48e6-ac7f-898bbbc5a115%2C9e8f6345-507c-4ec1-910b-394632555b27%2Cc1621355-4537-4941-9f94-f287bca01b14%2C1d05eb0a-2fad-4265-95d9-1c362e80dbcf | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
7ce623ee-7de1-477f-9b56-58bfa8927e2a | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 03:06:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 634 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96834 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 634, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | 811cd346-4055-4705-adf2-c1fcad411029 |  | https://web.fulcrumapp.com/photos/view?photos=811cd346-4055-4705-adf2-c1fcad411029 | Concrete | Circular Joint | Drummy |  | Not Reinforcement
34d92aa4-374d-41fe-bd99-49505afd0a62 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 03:42:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 635 | 1 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84598 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 635, 1 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | The delamination has extended upwards for an area of 200mm x 400mm. The delamination appears to be generated from the radial joint between Ring 635 and 636. | yes |  |  |  |  | 2885fa2a-1f67-400f-b05f-770a7380bdeb | Pink marking is the new delaminatiled area | https://web.fulcrumapp.com/photos/view?photos=2885fa2a-1f67-400f-b05f-770a7380bdeb | Concrete | Circular Joint | Drummy |  | Circular joint not radial
46f6aee5-f057-4839-bbf5-0f765e2f330a | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 03:44:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 635 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96835 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 635, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | The delamination did not extend beyond the initial marking. The area appears to have been previously patched, and the repair has failed. The repair may have happened at the tunnel construction | no |  |  |  |  | 17f9c226-521b-4ea5-a115-6804015b81b3 |  | https://web.fulcrumapp.com/photos/view?photos=17f9c226-521b-4ea5-a115-6804015b81b3 | Concrete | Circular Joint | Drummy |  | Not Reinforcement
b1ccc334-2058-4a0e-b891-f89e7d2c31cd | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 05:47:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 636 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27029 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 31/01/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 636, 1 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout Injection Hole has Leak - Active at time of inspection. |  | Grout Injection Hole has Leak - Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer |  |  | The injection hole is dry, and there is no further deterioration | yes |  |  |  |  | f511670f-296e-42e6-b3f8-6ea7c75f3331 |  | https://web.fulcrumapp.com/photos/view?photos=f511670f-296e-42e6-b3f8-6ea7c75f3331 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
86ac1fd7-fb7c-4e17-8c86-564ac89a5054 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 03:50:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 636 | 1 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84599 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 636, 1 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination has extended beyond original marking. | yes |  |  |  |  | 9595b70f-9f62-4030-8679-e7bd2775c30a |  | https://web.fulcrumapp.com/photos/view?photos=9595b70f-9f62-4030-8679-e7bd2775c30a | Concrete | Radial Joint | Drummy
4052d83f-2c3e-4911-9519-7888e87fc699 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-30 05:49:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 636 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84591 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 636, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Further deterioration of joint is noted. | yes |  |  |  |  | c072960c-d5b6-4946-b2fc-121f22331bf1 |  | https://web.fulcrumapp.com/photos/view?photos=c072960c-d5b6-4946-b2fc-121f22331bf1 | Concrete | Circular Joint | Drummy
417eb6c1-affc-4c4d-974e-02d142160794 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 05:51:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 638 | 1 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84601 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 638, 1 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | The Drummy area did not change. The affected area is only the grout infill. However, the gap appears to be larger. | yes |  |  |  |  | 7749cf9c-64fc-49ad-ae67-63ebb3ad832a,9580c2dc-2ee0-445e-8f63-5b1d7d714827 | , | https://web.fulcrumapp.com/photos/view?photos=7749cf9c-64fc-49ad-ae67-63ebb3ad832a%2C9580c2dc-2ee0-445e-8f63-5b1d7d714827 | Concrete | Circular Joint | Drummy |  | Circular joint not radial
5c7047b7-3f51-4f4d-af76-4a275af1e914 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 | -20.2994 | 118.565 | POINT (118.5650409 -20.2993691) | 2025-05-27 20:13:18 AEST | 2025-05-31 01:48:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 638 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84600 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 638, 11 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 200mm x 600mm adjacent to steel channel bracket. |  | Concrete shell segment has drummy concrete over an area of 200mm x 600mm adjacent to steel channel bracket. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Review and assess condition at the next inspection. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | No change from previous inspection | no |  |  |  |  | 73135197-b654-4f83-baad-85335f8fcbc1 |  | https://web.fulcrumapp.com/photos/view?photos=73135197-b654-4f83-baad-85335f8fcbc1 | Concrete,Steel | Radial Joint | Drummy |  | Radial Joint
ceca9f38-f69a-4a42-b4ec-bed876ee0b54 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 01:47:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 638 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27030 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 638, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [7 empty] | no |  |  |  |  | e2ff24a2-0e9e-40fe-b355-e9a5478bd2d4,e9b9d867-3e86-434b-a289-13e2835fae03 | , | https://web.fulcrumapp.com/photos/view?photos=e2ff24a2-0e9e-40fe-b355-e9a5478bd2d4%2Ce9b9d867-3e86-434b-a289-13e2835fae03 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
2f954711-6701-4c46-857f-aca5fe013e1d | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 05:52:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 638 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84602 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 2 | Level 2 | Level 2 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 638, 2 & 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt one is loose at 2 O'Clock and another is missing at 3 O'Clock. Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. |  | Channel anchor bolt one is loose at 2 O'Clock and another is missing at 3 O'Clock. Steel channel support bracket has Level 2 Minor Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Tighten loose anchor bolt nut. | AIMS structural inspector | No | On-Line | No | Walkway | - | Scheduled Maintenance Competent Supervisor |  |  |  | no |  |  |  |  | 94311554-e09c-4b69-b399-6b59a6ae41cc,e01eead3-e47f-41ad-9f06-3e98c95c614b,18f6854b-d520-44f2-9ca2-9f9be3c80c90 | ,, | https://web.fulcrumapp.com/photos/view?photos=94311554-e09c-4b69-b399-6b59a6ae41cc%2Ce01eead3-e47f-41ad-9f06-3e98c95c614b%2C18f6854b-d520-44f2-9ca2-9f9be3c80c90 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Loose,Missing
1b0fca60-79a7-4d72-aa5d-e803742fcad2 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 05:55:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 638 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84592 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 638, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Break out grout locally, abrasive blast steelwork, and inspect by competent engineer to develop repair detail. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | The delamination has extended to adjacent ring 637. However, area delaminated appear to be fill mortar not ring concrete. | yes |  |  |  |  | fcab454e-1574-49dd-8bcd-18b3b10afd90,6437e800-69d9-4830-bbb7-7bcda09a71a9 | , | https://web.fulcrumapp.com/photos/view?photos=fcab454e-1574-49dd-8bcd-18b3b10afd90%2C6437e800-69d9-4830-bbb7-7bcda09a71a9 | Concrete | Circular Joint,Mortar | Drummy
8b7d9c1a-9231-4801-beed-3f8b48536f33 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 02:11:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 640 | 10 | Grout Injection Hole | Grout Injection Hole |  | 68718 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 640, 10 o'clock. Concrete Shell Segment - Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor |  |  | The delaminated area did not extend past existing marking. Leaking thru the concrete segment active at time of inspection. Crack injection may be required. There are no leaks at the injection hole at the time of inspection. | no |  |  |  |  | 8fa10c08-5cec-4b2a-a1c9-9ac8d38e915e,b81d0515-cd90-476e-bc1f-5fa418dda15a,97433ec2-c2e6-4d5a-a627-d4e767b2458a | ,, | https://web.fulcrumapp.com/photos/view?photos=8fa10c08-5cec-4b2a-a1c9-9ac8d38e915e%2Cb81d0515-cd90-476e-bc1f-5fa418dda15a%2C97433ec2-c2e6-4d5a-a627-d4e767b2458a | Concrete | Grout Hole,Reinforcement | Crack,Drummy,Leaks
c82fe2ac-4065-4df2-bbb1-17be640a6584 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 02:07:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 640 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84604 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 640, 12 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 900mm x 600mm adjacent to pipe support. |  | Concrete shell segment has drummy concrete over an area of 900mm x 600mm adjacent to pipe support. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), downgraded to P3 and monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | The delamination area did not extend past existing marking. Leaking active at the time of inspection. | no |  |  |  |  | 36bfbdd4-6f77-4efd-9866-496891588c62 |  | https://web.fulcrumapp.com/photos/view?photos=36bfbdd4-6f77-4efd-9866-496891588c62 | Concrete | Misc (Pipes/Cable Tray/etc) | Drummy,Leaks
69f56e1a-d5b0-4ad0-a98d-e7fc39b27160 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 02:04:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 640 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27656 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 640, 12 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | Pipe bracket support is no longer in service. Supported pipe fully corroded no longer serviceable. Concrete damage has not extended beyond previous marking. Water ingress is still active. Concrete injection may be required to seal the crack. No maintenance work noted. | yes |  |  |  |  | 2662ad0b-a9b6-49f5-af01-ac30a83076b5,f3c0e72e-c29a-4a11-a79c-d3f65e4d3f37,ced6ea17-7084-4ee6-980c-77a4f128e49d,2a0576e1-61d8-4dab-9b2d-fe39b8ad333d | ,,, | https://web.fulcrumapp.com/photos/view?photos=2662ad0b-a9b6-49f5-af01-ac30a83076b5%2Cf3c0e72e-c29a-4a11-a79c-d3f65e4d3f37%2Cced6ea17-7084-4ee6-980c-77a4f128e49d%2C2a0576e1-61d8-4dab-9b2d-fe39b8ad333d | Concrete | Misc (Pipes/Cable Tray/etc),Reinforcement | Crack,Leaks,Corrosion-Heavy |  | Corrosion Heavy
0744abeb-9e4e-4dd7-be3a-ef416428680e | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 06:32:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 640 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 86560 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 24/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 640, 2 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 250mm x 1200mm. |  | Concrete shell segment has drummy concrete over an area of 250mm x 1200mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), downgraded to P3 and monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | Excavation | Condition Monitoring Competent Supervisor |  |  | The Drummy area did not extend past the previous marked area. Possible the damage to be a combination of poor workmanship for the segment, water leaking from grout hole at 2 o'clock, and the corrosion of steel bracket. | no |  |  |  |  | 6ba5a92f-7abc-4442-95c6-453c3117a936,ea297ca1-404a-4ea7-ae1b-3f23b990db00,009befbe-a8bc-4911-92fd-f9a7b327d26b,9efcf4ac-9f06-47ac-a669-009ef0d4ad58 | ,,, | https://web.fulcrumapp.com/photos/view?photos=6ba5a92f-7abc-4442-95c6-453c3117a936%2Cea297ca1-404a-4ea7-ae1b-3f23b990db00%2C009befbe-a8bc-4911-92fd-f9a7b327d26b%2C9efcf4ac-9f06-47ac-a669-009ef0d4ad58 | Concrete,Steel | Middle of Panel | Drummy,Leaks |  | Middle of panel
3eb9106a-9c6c-4011-9c3a-e2f68c8128c0 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 06:16:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 640 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84593 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 640, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | The Drummy area did not advanced | no |  |  |  |  | c587d1ec-0844-4b42-8629-1b85b452dab0 |  | https://web.fulcrumapp.com/photos/view?photos=c587d1ec-0844-4b42-8629-1b85b452dab0 | Concrete | Circular Joint | Drummy
33ad858b-cff8-42b6-a291-2281abfcd8ae | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 06:18:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 640 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27031 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 640, 4 o'clock. Concrete Shell Segment. - Hydrophyllic Joint Seal - Radial Joint | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Radial joint) has Leak - Active at time of inspection. |  | Joint seal (Radial joint) has Leak - Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | The damage does not appear to have been extended. Same condition as per previous inspection. | no |  |  |  |  | 19ff894e-4a1b-42cb-83c1-2bc9e1195704,68551406-1031-4918-a1af-db0f9e5d71a2 | , | https://web.fulcrumapp.com/photos/view?photos=19ff894e-4a1b-42cb-83c1-2bc9e1195704%2C68551406-1031-4918-a1af-db0f9e5d71a2 | Concrete | Radial Joint,Reinforcement | Leaks
6ca052e5-83ce-4c34-8e3d-cad50dd9e670 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 02:12:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 640 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84603 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 640, 9 to 10 O'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 600mm x 1600mm. |  | Concrete shell segment has drummy concrete over an area of 600mm x 1600mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), downgraded to P3 and monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | The delamination did not extend past the existing marking. | no |  |  |  |  | ce55c7bd-c474-402d-a77c-87cd232aba6b |  | https://web.fulcrumapp.com/photos/view?photos=ce55c7bd-c474-402d-a77c-87cd232aba6b | Concrete | Middle of Panel | Drummy |  | Middle of panel
cd9e5275-e717-494a-b517-af4a18c23938 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 06:40:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 641 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84605 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 8/11/2022 |  | 31/01/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 641, 2 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 300mm x 300mm adjacent to pipe support. |  | Concrete shell segment has drummy concrete over an area of 300mm x 300mm adjacent to pipe support. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | Break out loose and damaged concrete. Engineer to assess damage to reinforcement and remediation required. All areas of damaged concrete shall be replaced with high strength concrete patch repairs including embedment of galvanic Cathodic Protection (CP) anodes. Corroded reinforcement that has not been removed shall be thoroughly cleaned of all corroded material. Where corroded reinforcement has been removed it should be replaced by welding a new length of N grade reinforcement of the same diameter to the remaining undamaged reinforcing bar. Or replacing the damaged bar with a new N grade bar of the same diameter as the removed bar. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Defect not found | yes |  |  |  |  | 27e89de8-141c-4f8e-8289-a5711735d7cd |  | https://web.fulcrumapp.com/photos/view?photos=27e89de8-141c-4f8e-8289-a5711735d7cd | Concrete | Misc (Pipes/Cable Tray/etc) | Drummy
bb54d459-5989-47c5-a37e-d4a69e1fbe98 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 06:47:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 642 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84606 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 642, 2 to 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolts have Level 4 Medium High Corrosion. Steel channel support bracket has Level 5 High Corrosion up to 100% coverage. Nut is missing at 3 o'clock. |  | Channel anchor bolts have Level 4 Medium High Corrosion. Steel channel support bracket has Level 5 High Corrosion up to 100% coverage. Nut is missing at 3 o'clock. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace severely corroded channel support and anchor bolts. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor |  |  | Possible incorrect reference. Bracket from 12’O clock to 1’ O clock, advanced corrosion to the nut to the point that is no longer serviceable. | yes |  |  |  |  | 1f38d2de-1889-4795-b70a-f7d807c9cb63 |  | https://web.fulcrumapp.com/photos/view?photos=1f38d2de-1889-4795-b70a-f7d807c9cb63 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Missing
b8d8fb32-b481-4657-87aa-ec48db9d68e7 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 06:48:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 642 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 96836 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | No Selection Applicable - Refer to Detailed Defect Description |  | No Selection Applicable - Refer to Detailed Defect Description | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 642, 3 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | One nut is missing from channel anchor bolt. |  | One nut is missing from channel anchor bolt. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Steelwork Remediation Crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Still present, no change. | no |  |  |  |  | 60f574a1-1532-40ab-98d3-3a481902293e |  | https://web.fulcrumapp.com/photos/view?photos=60f574a1-1532-40ab-98d3-3a481902293e | Steel | Channel Bracket-Bolt | Missing
18b9ec19-0674-49a8-8b75-17d7b07f81fe | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 23:36:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 646 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 68719 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 2 | Level 2 | Level 2 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 646, 11 to 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts have level 2 corrosion. Two anchor bolts are missing. |  | Channel anchor bolts have level 2 corrosion. Two anchor bolts are missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts. Alternatively, repair anchor bolts as per BHP standard drawing 000-S-12598. | AIMS Inspector | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor |  |  | No changes from previous inspection | no |  |  |  |  | e1ea8e97-b2e2-47aa-b5be-c0f48ac3dc80,c65aa594-4b66-48de-9beb-b032a2e72e45,97300625-af8e-4053-b497-cf0f5f8ea478,0d06b3e0-12f1-4f0e-9799-a2d75f872f18,2ec1ba13-e957-470b-b3fc-31c8ed67d4fa | ,,,, | https://web.fulcrumapp.com/photos/view?photos=e1ea8e97-b2e2-47aa-b5be-c0f48ac3dc80%2Cc65aa594-4b66-48de-9beb-b032a2e72e45%2C97300625-af8e-4053-b497-cf0f5f8ea478%2C0d06b3e0-12f1-4f0e-9799-a2d75f872f18%2C2ec1ba13-e957-470b-b3fc-31c8ed67d4fa | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
9be50af3-acb1-43e7-8640-de0626038058 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 23:34:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 646 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84610 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 646, 3 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | Missing nut on channel andchor bolt. |  | Missing nut on channel andchor bolt. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | GTS Specification. Remediation crew. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Missing bolt | no |  |  |  |  | 390b9616-931e-4ad3-bf55-3c699cd68ff7 |  | https://web.fulcrumapp.com/photos/view?photos=390b9616-931e-4ad3-bf55-3c699cd68ff7 | Steel | Channel Bracket-Bolt | Missing
daf5bafd-3b0e-4446-bbd7-fa962e5c3a07 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 23:40:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 648 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27658 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 648, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 2 - Medium Low Corrosion. |  | Channel anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [7 empty] | no |  |  |  |  | 86e6d1fe-ebd1-4e24-a8c0-486cb496b7f6,10664822-3edf-44eb-9f78-4650668672bc,a6b83df2-204f-4ebc-a007-b0563c5ce166,b7f7c91d-4358-44e6-a74d-b7af90e34902 | ,,, | https://web.fulcrumapp.com/photos/view?photos=86e6d1fe-ebd1-4e24-a8c0-486cb496b7f6%2C10664822-3edf-44eb-9f78-4650668672bc%2Ca6b83df2-204f-4ebc-a007-b0563c5ce166%2Cb7f7c91d-4358-44e6-a74d-b7af90e34902 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
0a1d0613-d69a-4af8-9d5a-879a46371b63 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 649 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84611 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 649, 7 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Break out grout locally, abrasive blast steelwork, and inspect by competent engineer to develop repair detail. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Engineering Repair Methodology Required Competent Engineer | [11 empty] | Concrete | Circular Joint | Drummy
ed658007-8d0b-4828-9a91-8c7544098c8c | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 03:03:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 650 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27032 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 1 | Level 1 | Level 1 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 650, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts have level 2 corrosion. Missing one anchor bolt at 11 O'Clock. |  | Channel anchor bolts have level 2 corrosion. Missing one anchor bolt at 11 O'Clock. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace missing anchor bolt as per approved design drawing. Monitor for further deterioration. Consider widescale coating / corrosion remediation project. | Monitor for further deterioration. Consider widescale coating / corrosion remediation project. Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor |  |  | The second bolt is missing. The remaining bolts have surface corrosion. | no |  |  |  |  | 5226ca41-51a0-4ea6-9e82-1c3f5c31d60b,5dfb6bcf-e9e4-420e-a0fc-1a2835dcb5b7 | , | https://web.fulcrumapp.com/photos/view?photos=5226ca41-51a0-4ea6-9e82-1c3f5c31d60b%2C5dfb6bcf-e9e4-420e-a0fc-1a2835dcb5b7 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface,Missing
3a847b67-d97d-4509-aa47-f97b935f4dfb | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 23:54:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 650 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84612 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 650, 3 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | GTS Specification. Remediation crew. | Yes | On-Line | No | Walkway | - | Replace Component Competent Supervisor |  |  |  | no |  |  |  |  | 1f8a2fe6-d39b-4a14-a4f6-9c516c077517 |  | https://web.fulcrumapp.com/photos/view?photos=1f8a2fe6-d39b-4a14-a4f6-9c516c077517 | Steel | Channel Bracket-Bolt | Missing
a1c5ca29-5642-4444-82fc-451d831c9265 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 06:25:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 652 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68720 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint (Radial Joint) - Ring 652, 4 o'clock. Concrete Shell Segment. Identified in 2019. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | Previously listed under AIMS defect 30745 under incorrect AIMS quadrant. 30745 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | loss of services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Grout has failed, and joint steel plates are exposed. Surface corrosion noted with no significant section loss at the time of inspection. Repair priority needs to be elevated. | yes |  |  |  |  | 635eb6d5-2e90-4d75-a2fc-b9c756cae4c3,6633c26c-eb34-4281-bd61-4496a503b49e | , | https://web.fulcrumapp.com/photos/view?photos=635eb6d5-2e90-4d75-a2fc-b9c756cae4c3%2C6633c26c-eb34-4281-bd61-4496a503b49e | Concrete,Steel | Radial Joint | Corrosion-Heavy,Corrosion-Surface,Drummy
c6ca4a59-6dcb-4445-90be-0e38e62ddf58 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 01:43:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 652 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84613 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 652, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | The drummy area did not extend past the previous marking. | no |  |  |  |  | 849a3818-a815-4767-94d5-ab81269d0d66 |  | https://web.fulcrumapp.com/photos/view?photos=849a3818-a815-4767-94d5-ab81269d0d66 | Concrete | Circular Connection | Drummy |  | Circular Connection
5d53fee6-dac7-421b-98ad-4554ee5c71fe | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 01:44:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 652 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27659 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 652, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 2 - Medium Low Corrosion. |  | Channel anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [7 empty] | no |  |  |  |  | 12116eb4-4e5d-4c91-aacc-60ed34d78bfc,9b15bc25-7bfe-4430-96d8-9b510c46e688,a0148cca-cfc1-4a78-906a-72a1cdc26abd | ,, | https://web.fulcrumapp.com/photos/view?photos=12116eb4-4e5d-4c91-aacc-60ed34d78bfc%2C9b15bc25-7bfe-4430-96d8-9b510c46e688%2Ca0148cca-cfc1-4a78-906a-72a1cdc26abd | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
cf54959e-7f6d-440d-962b-0bf08a507690 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 01:45:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 652 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84614 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 652, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | f0bec7f5-9f0d-40fa-b8cb-99d66fee2cab |  | https://web.fulcrumapp.com/photos/view?photos=f0bec7f5-9f0d-40fa-b8cb-99d66fee2cab | Concrete | Radial Joint | Drummy
0635c432-0ead-4631-998f-cc19ad911ea1 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 01:52:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 653 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84616 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 653, 1 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm across both ring 652 and 653. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm across both ring 652 and 653. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Further deterioration of joint noted, especially on Ring 652 side. | yes |  |  |  |  | 965caa8c-2f59-46ca-993b-02595304fc56,a92d2034-618d-4740-9000-107582b67c39 | , | https://web.fulcrumapp.com/photos/view?photos=965caa8c-2f59-46ca-993b-02595304fc56%2Ca92d2034-618d-4740-9000-107582b67c39 | Concrete | Circular Joint | Drummy
c6fb8b7b-122f-4e37-98f2-42dc956a6c06 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 01:53:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 653 | 2 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84615 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 653, 2 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Further deterioration of joint noted | yes |  |  |  |  | 5a22b1c1-dbb7-4564-9597-5f53cc0d0656 |  | https://web.fulcrumapp.com/photos/view?photos=5a22b1c1-dbb7-4564-9597-5f53cc0d0656 | Concrete | Circular Joint | Drummy
216ab5a5-da3c-41b9-ad9e-d3605d049ed7 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:00:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 654 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27033 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 654, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 Corrosion |  | Steel channel support bracket has Level 2 Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Level 3 corrosion on bracket connection to tunnel light. | yes |  |  |  |  | 3b170f8a-a795-4316-9e81-c503b74b5650,a3028f2e-5e42-48a0-8503-4f7ac74c2a62 | , | https://web.fulcrumapp.com/photos/view?photos=3b170f8a-a795-4316-9e81-c503b74b5650%2Ca3028f2e-5e42-48a0-8503-4f7ac74c2a62 | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
745f82af-76e5-447b-b84c-237616114a65 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 03:10:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 654 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 96837 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 45267.4684 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Ring 654, 11 to 1 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion |  | Steel channel support bracket has Level 2 Minor Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [7 empty] | no |  |  |  |  | d04271ce-c403-48d9-a571-1f01f866044c,091d1622-a563-42c5-8913-e9302e07f4c3,d69748ee-dc04-4e28-aac4-c2439b3b4d51 | ,, | https://web.fulcrumapp.com/photos/view?photos=d04271ce-c403-48d9-a571-1f01f866044c%2C091d1622-a563-42c5-8913-e9302e07f4c3%2Cd69748ee-dc04-4e28-aac4-c2439b3b4d51 | Steel | Channel Bracket | Corrosion-Surface
484fc95c-b476-41a1-bdb9-8a9595fee3c7 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:01:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 654 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84617 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Repair Verified | 8/11/2022 |  | 31/01/2024 | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 654, 3 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | Missing nut on channel andchor bolt. |  | Missing nut on channel andchor bolt. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing nut as per approved design drawing. | GTS Specification. Remediation crew. | No | On-Line | No | Walkway | - | Replace Component Competent Supervisor |  |  | Corrosion to the bolt making the bolt unserviceable. | no |  |  |  |  | cf8ce42a-9d11-4365-a94d-a83d6a8381f7 |  | https://web.fulcrumapp.com/photos/view?photos=cf8ce42a-9d11-4365-a94d-a83d6a8381f7 | Steel | Channel Bracket-Bolt | Missing
ee5e2330-df1b-4e10-8ae9-daac482ebdd9 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:02:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 654 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27356 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Financial | Financial |  | Missing Component | Missing Component |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 654, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolt is missing nut. |  | Channel anchor bolt is missing nut. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace missing anchor bolt nut. Alternatively, repair anchor bolts as per BHP standard drawing 000-S-12598. | Steelwork Remediation Crew. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor |  |  | Possible duplication | no | [7 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
3df40bdd-ebaf-4061-a602-b9f978b64504 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:08:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 655 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84620 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 655, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | The circular joint at 4 o'clock has been previously marked. The deterioration did not extend. Circular joint at 3 o'clock in good condition. | no |  |  |  |  | 3f92a6bc-3760-48d7-ae3b-aa6c6bf5d9fd,f71214da-bece-4237-a1c9-56f95d136f9d,de9a9cc7-abd6-4f59-afc0-1630a80ce2ef | Circular joint at 4 o'clock ,Circular joint 1 at 3 o'clock in good condition ,Circular joint 2 at 3 o'clock in good condition | https://web.fulcrumapp.com/photos/view?photos=3f92a6bc-3760-48d7-ae3b-aa6c6bf5d9fd%2Cf71214da-bece-4237-a1c9-56f95d136f9d%2Cde9a9cc7-abd6-4f59-afc0-1630a80ce2ef | Concrete | Circular Connection,Circular Joint | Drummy
995992ef-1ae8-4a34-bf5c-28d67817377c | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:09:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 655 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84621 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 8/11/2022 |  | 31/01/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 655, 9 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 500mm x 500mm adjacent to pipe support. |  | Concrete shell segment has drummy concrete over an area of 500mm x 500mm adjacent to pipe support. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P2 |  |  |  | Break out loose and damaged concrete. Engineer to assess damage to reinforcement and remediation required. All areas of damaged concrete shall be replaced with high strength concrete patch repairs including embedment of galvanic Cathodic Protection (CP) anodes. Corroded reinforcement that has not been removed shall be thoroughly cleaned of all corroded material. Where corroded reinforcement has been removed it should be replaced by welding a new length of N grade reinforcement of the same diameter to the remaining undamaged reinforcing bar. Or replacing the damaged bar with a new N grade bar of the same diameter as the removed bar. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | Walkway | - | Engineering Repair Methodology Required Competent Engineer |  |  | Not Accessible | [8 empty] | Concrete | Misc (Pipes/Cable Tray/etc) | Drummy
ada1ff5b-7897-4374-a5f9-7f70c8fd0d53 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:14:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 656 | 4 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 68721 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 44540.2564 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Bored Tunnel - Segment Bolted Joint Circle Joint) - Ring 656, 4 o'clock. Concrete Shell Segment. Identified in 2019. |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Not accessible. Confusing information provided. Circular and radial joints described. | [8 empty] | Concrete | Circular Joint,Radial Joint | Drummy
b7e8d263-415d-4431-a364-9efbeef6f7f3 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 17:30:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 657 | 8 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84624 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 657, 8 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Same as previously, no change in condition | no |  |  |  |  | 0cb19628-8bf7-4caa-b56b-06c0ab8209e2,6be3b728-82bd-426f-88a0-bdd7de3960ae,f9c70e6f-1bbf-4040-96be-0d734d5b9863,11654d0f-1174-4658-ae6d-06362e0648ae | ,,, | https://web.fulcrumapp.com/photos/view?photos=0cb19628-8bf7-4caa-b56b-06c0ab8209e2%2C6be3b728-82bd-426f-88a0-bdd7de3960ae%2Cf9c70e6f-1bbf-4040-96be-0d734d5b9863%2C11654d0f-1174-4658-ae6d-06362e0648ae | Concrete | Radial Joint | Drummy
41406e94-5c73-4eb3-a350-4e6896aa1e7e | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 17:47:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 657 | 8 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84622 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 657, 8 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 400mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Same as previously found, Drummy concrete | no |  |  |  |  | f7eb8ca4-f294-4cdb-a429-c0a6c2783b4d,257953d9-789a-4414-b795-b35f286f8d1c | , | https://web.fulcrumapp.com/photos/view?photos=f7eb8ca4-f294-4cdb-a429-c0a6c2783b4d%2C257953d9-789a-4414-b795-b35f286f8d1c | Concrete | Radial Joint | Drummy
a09d0f20-f40b-4e3e-a59f-3679a648fdc0 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:34:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 658 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27035 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 658, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Inactive at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | dca6c378-3241-4a15-99fe-cf0645955dd0 |  | https://web.fulcrumapp.com/photos/view?photos=dca6c378-3241-4a15-99fe-cf0645955dd0 | Concrete | Circular Joint | Leaks |  | Circular Joint not reinforcement
d323700f-fa41-4436-88c0-6f91d6e30650 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:36:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 658 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27660 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 658, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 20% coverage. Channel anchor bolts have Level 2 Medium Low Corrosion |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 20% coverage. Channel anchor bolts have Level 2 Medium Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | The corrosion has advanced, especially at bolts to Level 3 | yes |  |  |  |  | 1c07a692-9c4b-49c0-80ba-ff29de247a06 |  | https://web.fulcrumapp.com/photos/view?photos=1c07a692-9c4b-49c0-80ba-ff29de247a06 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
b3a1ec3f-0439-49e1-bff9-80126f5a600c | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-31 03:26:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 658 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27034 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 658, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | No change from previous inspection | no |  |  |  |  | 438241ce-6b97-47ce-9a53-00130a009ded,93b93b28-e8c3-495e-8fa8-4642ea7b914e,9e120fac-26b3-4459-aaa5-868e3924289f,7a919c6f-787c-4535-a8ff-6ca2be2d056f | ,,, | https://web.fulcrumapp.com/photos/view?photos=438241ce-6b97-47ce-9a53-00130a009ded%2C93b93b28-e8c3-495e-8fa8-4642ea7b914e%2C9e120fac-26b3-4459-aaa5-868e3924289f%2C7a919c6f-787c-4535-a8ff-6ca2be2d056f | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
859dd048-950e-4736-9854-b86be0461372 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:37:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 658 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84626 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 658, 3 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | Missing nut on channel anchor bolt. |  | Missing nut on channel anchor bolt. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | GTS Specification. Remediation crew. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | 6675b242-73ef-482d-9770-2ed1c4ff6f45 |  | https://web.fulcrumapp.com/photos/view?photos=6675b242-73ef-482d-9770-2ed1c4ff6f45 | Steel | Channel Bracket-Bolt | Missing
9e18cd66-0989-47ea-a92f-12e339ed31b4 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:38:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 658 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84627 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 658, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Not accessible | [8 empty] | Concrete | Circular Joint | Drummy
f83019bd-c84d-476a-895a-ecce8933d4a0 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:50:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 660 | 2 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84632 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 660, 2 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | fa12f96e-7008-4e0e-939f-da4a4339de32 |  | https://web.fulcrumapp.com/photos/view?photos=fa12f96e-7008-4e0e-939f-da4a4339de32 | Concrete | Circular Joint | Drummy
4a642c47-6e31-41c1-9e5e-99b85786ab43 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 24 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:51:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 660 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84631 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 660, 7 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Cathodic Protection continuity cable severed. |  | Cathodic Protection continuity cable severed. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | Renew Cathodic Protection Continuity Cable. | Cathodic Protection Technician | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor |  |  | Not accessible | [8 empty] | Concrete
28129da6-d0cf-44c1-a6fe-ad5c10af577c | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 20 |  |  |  | 2025-05-30 03:44:56 AEST | 2025-05-30 03:48:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 635 defect copy from 636 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27029 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 31/01/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 635, 1 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout Injection Hole has Leak - Active at time of inspection. |  | Grout Injection Hole has Leak - Not active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Engineer | BS |  | Injection hole has been filled with expanding foam. This foam appears that has stopped the leaking. However, it is deteriorating rapidly. | yes |  |  |  |  | e8a885cc-d1b1-444c-bd50-b5a18aacc241,c76967c7-be63-45cd-983c-d7df8d692c24 | , | https://web.fulcrumapp.com/photos/view?photos=e8a885cc-d1b1-444c-bd50-b5a18aacc241%2Cc76967c7-be63-45cd-983c-d7df8d692c24 | Concrete | Grout Hole | Leaks |  | Not Reinforcement
d67c2297-ba56-4126-93a0-25771b0cbf0d | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 18 | -20.2993 | 118.5651 | POINT (118.5650717 -20.299299) | 2025-05-30 23:46:47 AEST | 2025-05-31 00:34:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 634 | 11 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [15 empty] | Concrete Damage due to Cast- In |  | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  | Possible (Failure within 5 Years) |  | Bolt connection 1 between ring segments at 11 o'clock |  | Failure of shell segment in compression or tension leading to single ring failure. |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | [16 empty] | BS |  | Connection seal between adjacent segments of ring 644 is drummy, and 0.2mm wide crack is formed ar interface between segments indicating possible movement. | [5 empty] | 331e467e-3aeb-46da-99ef-bddb25d00fa2,ce77ff52-4c94-4caa-9476-2de58400db38,2590c2f5-804f-4ac1-805d-d0c180238278 | ,, | https://web.fulcrumapp.com/photos/view?photos=331e467e-3aeb-46da-99ef-bddb25d00fa2%2Cce77ff52-4c94-4caa-9476-2de58400db38%2C2590c2f5-804f-4ac1-805d-d0c180238278 | Concrete | Radial Joint | Crack,Drummy |  | Radial Joint no Circular Joint
4d124c62-2811-4843-a2b7-787e60c3e654 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 18 |  |  |  | 2025-05-31 02:20:37 AEST | 2025-05-31 02:29:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 643 | 10 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [17 empty] | 2 |  |  |  | Health & Safety |  |  |  | Concrete cracks |  | Severity Level 1 |  |  | Rare (Failure within 50 years) |  | Vertical crack 0.1mm wide extending for 500mm at 10 o'clock | [7 empty] | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | [16 empty] | BS |  | Vertical crack 0.1mm wide extending for 500mm. No leaks noted. | [5 empty] | 55214550-fdf0-4ee1-806d-157f54bb4c6a,d79d6876-352c-4405-9437-acce8af422f7,835fcdd5-7b3e-4a99-8766-4f21bcdfc75a,b481092d-5c2c-4122-aefa-4baef767a13c | Crack extension general view ,Crack close up ,Crack close up ,Crack close up | https://web.fulcrumapp.com/photos/view?photos=55214550-fdf0-4ee1-806d-157f54bb4c6a%2Cd79d6876-352c-4405-9437-acce8af422f7%2C835fcdd5-7b3e-4a99-8766-4f21bcdfc75a%2Cb481092d-5c2c-4122-aefa-4baef767a13c | Concrete | Middle of Panel | Crack,Leaks |  | Middle of Panel
117ce0e1-ffb0-488d-bedd-c89ebc60c0d2 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 18 |  |  |  | 2025-05-31 02:38:30 AEST | 2025-05-31 02:47:14 AEST | 30011704-user5@smec.com | james.stone@smec.com | 646 | 11 |  | Segment Bolted Joint (Radial Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  | Rare (Failure within 50 years) |  | Ring 646, 11 o'clock at interface with Ring 645 |  | Shear failure of bolt |  |  |  | Horizontal cracks 0.1mm in the bolt seal extending for 200mm. Previous marked and do not appear to have extended from last inspection. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | Previous mark crack | [5 empty] | 9914d90b-c7c8-4ed2-857c-50aa837a63d7,9a181a60-e6a9-4e4d-9cfd-4bd9d4ced454,2eb68ee2-a9f7-4f1c-83c8-88624b413b9f | General view ,Crack close up ,Crack close up | https://web.fulcrumapp.com/photos/view?photos=9914d90b-c7c8-4ed2-857c-50aa837a63d7%2C9a181a60-e6a9-4e4d-9cfd-4bd9d4ced454%2C2eb68ee2-a9f7-4f1c-83c8-88624b413b9f | Concrete | Radial Joint | Crack
2569dd93-b72f-4293-97e8-3f7a5202ea6e | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 18 |  |  |  | 2025-05-31 02:50:10 AEST | 2025-05-31 02:53:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 647 | 12 |  | Segment Bolted Joint (Circle Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  | Rare (Failure within 50 years) |  | Ring 467, 12 o'clock |  | Shear failure of bolt |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | Delamination at Ring section condition. | [5 empty] | b38b8d88-d754-44c2-902e-b0357a65b2e5,bab5658b-ed6f-4f14-ae27-a751ce77b1cd | General view of the delamination , | https://web.fulcrumapp.com/photos/view?photos=b38b8d88-d754-44c2-902e-b0357a65b2e5%2Cbab5658b-ed6f-4f14-ae27-a751ce77b1cd | Concrete | Circular Joint | Drummy
68c6436b-6d81-4aca-8424-55c4a65040ca | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 17 |  |  |  | 2025-05-31 05:56:24 AEST | 2025-05-31 06:02:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 638 | 2 |  | Segment Bolted Joint (Circle Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  | Possible (Failure within 5 Years) |  | Ring 638, 2 o'clock at interface to ring 637 |  | Shear failure of bolt |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | Ring 638, 2 o'clock ring connection grout is drummy for an area of 100x100mm. | [5 empty] | f1baa492-4ea9-4419-8c5e-f30e1791f3cd,4489f1b6-5e22-40c3-b5eb-80612282e961 | , | https://web.fulcrumapp.com/photos/view?photos=f1baa492-4ea9-4419-8c5e-f30e1791f3cd%2C4489f1b6-5e22-40c3-b5eb-80612282e961 | Concrete | Circular Joint | Drummy
3c27cbc4-6f30-4298-8f5b-16896851b338 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 17 |  |  |  | 2025-05-31 06:19:48 AEST | 2025-05-31 06:28:14 AEST | 30011704-user5@smec.com | james.stone@smec.com | 640 | 2 to 3 o'clock |  | Steel Channel Bracket | [15 empty] | Corrosion - Connection |  | 5 |  |  |  | Health & Safety |  |  |  | Induced corrosion due to 1 o'clock grout leaking over the steel bracket. |  | Severity Level 3 |  |  | Almost Certain (Failure within 1 Year) |  | Ring 640, between 2and 3 o'clock |  |  | Steel corrosion |  |  | Level 4 corrosion of steel channel due to water leaking from grout hole at o'clock |  | Loss of minor services (NOT water pipe) | [16 empty] | BS |  | Advanced corrosion on support channel. Leak from grout hole inactive at the time of inspection. | [5 empty] | 8f45766d-0592-4d04-99ce-0404f80a4c5d,227825db-0755-45cc-b01f-b2e983d4df47,2b4ebcd5-dc49-4e31-bc9b-81df3f7e523b,ebe9bc72-3118-461d-8a98-9a7587236293 | ,,, | https://web.fulcrumapp.com/photos/view?photos=8f45766d-0592-4d04-99ce-0404f80a4c5d%2C227825db-0755-45cc-b01f-b2e983d4df47%2C2b4ebcd5-dc49-4e31-bc9b-81df3f7e523b%2Cebe9bc72-3118-461d-8a98-9a7587236293 | Steel | Channel Bracket,Grout Hole | Corrosion-Heavy,Leaks
b2f2e6bb-64b1-42ee-b4ff-1d2eb19c77b4 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 15 |  |  |  | 2025-05-31 23:25:44 AEST | 2025-05-31 23:30:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 644 | 2 |  | Segment Bolted Joint (Circle Joint) | [15 empty] | Corrosion - Connection |  | 3 |  |  |  | Health & Safety |  |  | Atmospheric Corrosion of Cast-In |  |  | Severity Level 2 |  |  | Likely (Failure within 2 Years) |  | Ring 644, 2 o'clock at interface with Ring 643 |  | Shear failure of bolt |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | Drummy connection. Possible corrosion of cast in plates. | [5 empty] | 3f4824c6-9230-4ed1-bc5a-d7c112cd0266 |  | https://web.fulcrumapp.com/photos/view?photos=3f4824c6-9230-4ed1-bc5a-d7c112cd0266 | Concrete | Circular Joint | Drummy
affcbf83-6349-4a63-a400-1da16a0fd573 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 15 |  |  |  | 2025-05-31 23:45:01 AEST | 2025-05-31 23:50:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 648 | 2 |  | Segment Bolted Joint (Radial Joint) | [16 empty] | Plastic shrinkage | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  | Possible (Failure within 5 Years) |  | Ring 648, 2 o'clock radial joint |  | Failure to seal joint |  |  |  | Shrinkage crack 0.1mm |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | Shrinkage crack at joint connection that will allow chlorides to teach the cast in plates that will corroded and mortar to Spall. | [5 empty] | 3969d992-3ce9-42d0-a080-4d382c0edb53,c6d1f145-ef68-4560-9d54-5f2946d1a0c0 | , | https://web.fulcrumapp.com/photos/view?photos=3969d992-3ce9-42d0-a080-4d382c0edb53%2Cc6d1f145-ef68-4560-9d54-5f2946d1a0c0 | Concrete | Mortar,Radial Joint | Crack,Surface Damage
ec21752e-7fcc-4978-b73b-73ee2b5c06cc | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 15 |  |  |  | 2025-06-01 01:46:09 AEST | 2025-06-01 01:50:54 AEST | 30011704-user5@smec.com | james.stone@smec.com | 652 | 2 |  | Segment Bolted Joint (Radial Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 4 |  |  |  | Health & Safety |  |  | Atmospheric Corrosion of Cast-In |  |  | Severity Level 3 |  |  | Likely (Failure within 2 Years) |  | Ring 652, 2 o'clock radial joint |  | Shear failure of bolt |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | New defect with rapid deterioration. Both radial joints have horizontal cracks . | [5 empty] | 63b3581b-8a72-484e-822d-09b9d6fb594e,1fa1bf28-8cd2-4354-9739-cca39f0196d7,0e476b8b-37d4-4ec4-a7bb-1ace2fde4843 | ,, | https://web.fulcrumapp.com/photos/view?photos=63b3581b-8a72-484e-822d-09b9d6fb594e%2C1fa1bf28-8cd2-4354-9739-cca39f0196d7%2C0e476b8b-37d4-4ec4-a7bb-1ace2fde4843 | Concrete | Circular Joint,Radial Joint | Crack,Drummy
7babc946-84a2-4d52-9e26-592fa5a05a2b | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 15 |  |  |  | 2025-06-01 01:53:58 AEST | 2025-06-01 01:56:44 AEST | 30011704-user5@smec.com | james.stone@smec.com | 653 | 4 |  | Segment Bolted Joint (Circle Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 4 |  |  |  | Health & Safety |  |  | Atmospheric Corrosion of Cast-In |  |  | Severity Level 3 |  |  | Likely (Failure within 2 Years) |  | Ring 653, 4 o'clock |  | Shear failure of bolt |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | Area previously marked. The damage appears to get worse | [5 empty] | eb773e17-911d-4584-8246-2ea5e1bc165b |  | https://web.fulcrumapp.com/photos/view?photos=eb773e17-911d-4584-8246-2ea5e1bc165b | Concrete | Circular Joint | Drummy
f01ff7d0-1fd7-4e0f-ac0e-f5b28344f66e | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 14 |  |  |  | 2025-06-01 05:52:16 AEST | 2025-06-01 06:10:14 AEST | 30011704-user5@smec.com | james.stone@smec.com | 652 | 5 |  |  | Steel walkway braket | [14 empty] | Corrosion - Connection |  | 5 |  |  |  | Health & Safety |  |  | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Likely (Failure within 2 Years) |  | Ring 652, 5 o'clock under service path |  | Rupture |  |  | Class 3 - Medium corrosion |  |  |  | loss of access to tunnel | [15 empty] | BS |  | Steel bracket presents a level 3 corrosion with minor loss of section. Connection bolts have a level 3 corrosion with loss of threads and a total loss of nuts. | [5 empty] | 2431d9ea-48f2-4926-a84b-ba54407966ef,665854bd-d637-4cac-9d7f-18bd567c6810,6f9580b2-cb8f-4875-87bb-429bcd2f7d97,5f909a3e-b8ca-48dd-a0c0-1b04643d7acb,9f674743-be40-4d59-971a-dbab13785af0,67e79987-a808-43b7-ae6f-e52816ab2e75,d7953a5d-9ec3-41be-ba08-36eaf3ea1a02 | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=2431d9ea-48f2-4926-a84b-ba54407966ef%2C665854bd-d637-4cac-9d7f-18bd567c6810%2C6f9580b2-cb8f-4875-87bb-429bcd2f7d97%2C5f909a3e-b8ca-48dd-a0c0-1b04643d7acb%2C9f674743-be40-4d59-971a-dbab13785af0%2C67e79987-a808-43b7-ae6f-e52816ab2e75%2Cd7953a5d-9ec3-41be-ba08-36eaf3ea1a02 | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface |  | Walkway support not Misc
d99babde-dea4-4232-8fa3-95852748d506 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 14 |  |  |  | 2025-06-01 05:58:35 AEST | 2025-06-01 08:54:17 AEST | 30011704-user5@smec.com | james.stone@smec.com | 652 | 6 |  |  | Vertical steel post | [14 empty] | Corrosion - Structure Member/Platework |  | 3 |  |  |  | Financial |  |  | Localised Corrosion ATM |  |  | Severity Level 4 |  |  | Likely (Failure within 2 Years) |  | Ring 652, 6 o'clock |  | Shear failure of bolt |  |  | Class 3 - Medium corrosion |  |  |  | Loss of conveyor support | [15 empty] | BS |  | Base plate haa Level 3 corrosion with minor loss of section, steel column present Level 3 corrosion at bottom with minor loss of section. Anchor bolts have no threads, and nuts have corroded 90%. | [5 empty] | 1652b53d-0110-4a91-8be5-d5bcc96a4ea3,c0078331-382c-43d4-959d-e6b6702d5571,5060b444-cd6e-416a-8210-87d2069a1b9a,32c36be9-5453-41c9-a5c0-206306384531,c60ce316-0cc1-48fe-8e3d-6dd1386c6829,abb8f017-d9c2-4c4b-aa47-029875ea3b40,e936ed12-d40c-47f6-aada-c7471f381048,2875eb5b-4988-4b09-9e88-748f0250e326 | ,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=1652b53d-0110-4a91-8be5-d5bcc96a4ea3%2Cc0078331-382c-43d4-959d-e6b6702d5571%2C5060b444-cd6e-416a-8210-87d2069a1b9a%2C32c36be9-5453-41c9-a5c0-206306384531%2Cc60ce316-0cc1-48fe-8e3d-6dd1386c6829%2Cabb8f017-d9c2-4c4b-aa47-029875ea3b40%2Ce936ed12-d40c-47f6-aada-c7471f381048%2C2875eb5b-4988-4b09-9e88-748f0250e326 | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface
11edca30-07ec-4760-956c-58adeb236c25 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 14 | -20.2993 | 118.565 | POINT (118.5649895 -20.2992895) | 2025-06-01 06:26:12 AEST | 2025-06-01 08:23:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 656 | 5 |  |  | Service Parh steel support bracket | [14 empty] | Corrosion - Structure Member/Platework |  | 3 |  |  |  | Health & Safety |  |  | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Likely (Failure within 2 Years) |  | Level 3 corrosion to steel plates and Level 4 to bolts and nuts |  | Shear failure of bolt |  |  |  | The steel plates have Level 3 corrosion. However, the bolts and nuts are at Level 4 and 5. |  |  | Loss of access into the tunnel | [15 empty] | BS |  | Heavily corroded bolts connection. No threads are visible on bolts and 90% corrosion of nuts. | [5 empty] | a4172329-f8f9-49ef-a100-87418a8fd588,97dd5be6-6c59-4dfb-81c8-d0ac7e4c941d,3f3ed238-a869-4647-b595-38593bf55f06,cc402107-b61f-446f-9488-693a3d62de17,a5ec87ff-9289-41a7-874f-f45649dc3622,0688d8ad-3824-4b65-92d0-3c4b023a52df,1e4e1379-88cd-4e22-a403-8c9d0eb93a0f | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=a4172329-f8f9-49ef-a100-87418a8fd588%2C97dd5be6-6c59-4dfb-81c8-d0ac7e4c941d%2C3f3ed238-a869-4647-b595-38593bf55f06%2Ccc402107-b61f-446f-9488-693a3d62de17%2Ca5ec87ff-9289-41a7-874f-f45649dc3622%2C0688d8ad-3824-4b65-92d0-3c4b023a52df%2C1e4e1379-88cd-4e22-a403-8c9d0eb93a0f | Steel | Walkway Support | Corrosion-Heavy,Corrosion-Surface
b9801f60-9a78-417d-97ee-2cf4f50c2788 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 14 | -20.2993 | 118.565 | POINT (118.5650055 -20.2992682) | 2025-06-01 06:32:42 AEST | 2025-06-01 09:38:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 656 | 6 o'clock |  |  | Steel column supporting the walkway and conveyor | [14 empty] | Corrosion - Structure Member/Platework |  | 3 |  |  |  | Financial |  |  | Localised Corrosion ATM |  |  | Severity Level 3 |  |  | Likely (Failure within 2 Years) |  | Ring 656, 6 o'clock |  | Shear failure of bolt |  |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | [19 empty] | BS |  | Base plate has advanced corrosion, specifically at the location, which is subject to continuous water leaking from above water pipe. The base plate appears to have lost substantial strength from the bottom up. Hold down bolts are heavily corroded,l. Bolts are not protruding past nuts. Nuts lost 60 % of section. | [5 empty] | 8fc5f2a8-299f-4cec-bc0d-1d869342759e,3ce1e63e-5ee6-47b4-96d7-57fb0eac23f2,0e5aba7f-309d-43f7-98f5-6ea2b836753c,82e23794-7385-41c6-8ffc-e1b5c40c86f1,49ca2b7e-6e8d-41c4-a6c0-baca86fc2b83,5a5d1f4a-4278-4506-8f2f-8e1f679eb7a6 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=8fc5f2a8-299f-4cec-bc0d-1d869342759e%2C3ce1e63e-5ee6-47b4-96d7-57fb0eac23f2%2C0e5aba7f-309d-43f7-98f5-6ea2b836753c%2C82e23794-7385-41c6-8ffc-e1b5c40c86f1%2C49ca2b7e-6e8d-41c4-a6c0-baca86fc2b83%2C5a5d1f4a-4278-4506-8f2f-8e1f679eb7a6 | Steel | Misc (Pipes/Cable Tray/etc),Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Leaks,Missing
8a294687-5e73-433d-8fe9-182da8d22f4a | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 12 |  |  |  | 2025-06-01 09:38:30 AEST | 2025-06-01 19:58:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | 660 | 5-6 |  |  | Footing | [16 empty] | 3 | [14 empty] | Conveyor footing & walkway support bolts and nuts |  |  | Corrosion |  | Level 3 to Level 4 corrosion at anchor bolts of conveyor and walkway supports. | [19 empty] | BP |  | Base plate has advanced corrosion, active black iron oxide, subject to continuous water leaking from above water pipe. The base plate appears to have lost substantial strength from the bottom up. Hold down bolts/ bolts/ bolts are heavily corroded,l. are not | [5 empty] | b287f4a5-88be-4098-9db8-99a37bb1e537,92f9f040-d27d-476a-9c2a-539c1a50a8ef,0ee4790e-5803-4667-b83d-4f2ff2d98cee,0013464e-df19-4dfd-8ed6-6957ca31277d,6a742732-a112-4488-ac6c-482de8cfa667,4e77dcbe-1a30-42ed-8753-fdb599ba01fb | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=b287f4a5-88be-4098-9db8-99a37bb1e537%2C92f9f040-d27d-476a-9c2a-539c1a50a8ef%2C0ee4790e-5803-4667-b83d-4f2ff2d98cee%2C0013464e-df19-4dfd-8ed6-6957ca31277d%2C6a742732-a112-4488-ac6c-482de8cfa667%2C4e77dcbe-1a30-42ed-8753-fdb599ba01fb | Steel | Misc (Pipes/Cable Tray/etc),Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Leaks,Missing
43a2dd30-e170-4e63-8dc0-fe05c6cf91ad | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 12 |  |  |  | 2025-06-01 10:27:40 AEST | 2025-06-01 19:58:29 AEST | 30011704-user5@smec.com | james.stone@smec.com | 664 | 5-6 Conveyor footing & walkway support bolts and nuts |  |  | Footing and walkway support footing steel frame |  |  |  |  | Tunnel |  | Ring 664 |  | No for footing, old marking on walkway support frame | [5 empty] | Corrosion - Connection |  | 4 | [19 empty] | Class 3 - Medium corrosion | [19 empty] | BP |  | Base plate has advanced corrosion, active black iron oxide, subject to continuous water leaking from above water pipe. The base plate appears to have lost metal and substantial strength from the bottom up. Hold. down | [5 empty] | 13752ae5-2c20-4d44-9ea3-a32b601a4f6c,8db91802-bec7-4ac7-b29e-027528a981fb,46a975a8-3919-4aa3-9a92-8bd2baec76aa,9d9713dd-a8e0-4043-862f-3cc44ef3e57a,99cded1d-f73d-49c6-ad49-31fd4ed89bc7,096d578f-ece9-4d0b-9bfa-8d480a1f6ea2,59a1fb8a-c286-40df-9c42-bd3f0ddf0e9c | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=13752ae5-2c20-4d44-9ea3-a32b601a4f6c%2C8db91802-bec7-4ac7-b29e-027528a981fb%2C46a975a8-3919-4aa3-9a92-8bd2baec76aa%2C9d9713dd-a8e0-4043-862f-3cc44ef3e57a%2C99cded1d-f73d-49c6-ad49-31fd4ed89bc7%2C096d578f-ece9-4d0b-9bfa-8d480a1f6ea2%2C59a1fb8a-c286-40df-9c42-bd3f0ddf0e9c | Steel | Misc (Pipes/Cable Tray/etc),Walkway Support,Walkway Support-Bolt | Corrosion-Heavy,Leaks,Missing
22ac7328-0c26-4e79-b501-69148660679c | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 8 |  |  |  | 2025-06-01 14:16:41 AEST | 2025-06-01 14:19:03 AEST | 30011704-user5@smec.com | james.stone@smec.com | 633 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | Kp |  | Drummy grout concrete at 9 o’clock | [5 empty] | 8621aba3-c53d-4d7f-a98c-2820f00eb4c6,c6c0bf93-1dab-4ca7-a656-cdc898aa9388 | , | https://web.fulcrumapp.com/photos/view?photos=8621aba3-c53d-4d7f-a98c-2820f00eb4c6%2Cc6c0bf93-1dab-4ca7-a656-cdc898aa9388 | Concrete | Circular Joint | Drummy |  | Circular Joint
5cd5dad9-16a0-4437-877c-74c3722d2876 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 8 |  |  |  | 2025-06-01 14:41:23 AEST | 2025-06-01 14:47:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | 640 | 9 to 7 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | Kp |  | Drummy concrete with loose aggregate | [5 empty] | 65236db0-a619-4ca9-8029-fedf3cbf3436,daf107f1-892c-47cd-9c45-9374cbed018d,164a082c-8a96-498b-ba2d-84e7bef36e3a,6ef0af3f-3870-447b-bfed-617175ee7129,b769ed04-2ae6-48c4-922a-174430309e01,c7e19683-d0cd-41f6-8c90-50eb592f6fc0,b26aec26-d1c2-4f77-bbaf-fd702e839e18 | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=65236db0-a619-4ca9-8029-fedf3cbf3436%2Cdaf107f1-892c-47cd-9c45-9374cbed018d%2C164a082c-8a96-498b-ba2d-84e7bef36e3a%2C6ef0af3f-3870-447b-bfed-617175ee7129%2Cb769ed04-2ae6-48c4-922a-174430309e01%2Cc7e19683-d0cd-41f6-8c90-50eb592f6fc0%2Cb26aec26-d1c2-4f77-bbaf-fd702e839e18 | Concrete | Middle of Panel | Drummy,Loose |  | Middle of Panel
c1d74095-7ab6-4384-a77f-367550f1e3fe | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 8 |  |  |  | 2025-06-01 14:47:32 AEST | 2025-06-01 14:50:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 641 | 7 to 8 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | Kp |  | Buildup of Chlorine leaching and delimitation of concrete | [5 empty] | a088acd2-3106-41c7-9a5c-c724823f6ebf,599e98d4-0634-45b4-a685-04e908ad5375,a432c8b8-71ce-4cb2-83bf-ef1d0997008b,9711a4c3-92b3-4c38-b844-8071aac71273 | ,,, | https://web.fulcrumapp.com/photos/view?photos=a088acd2-3106-41c7-9a5c-c724823f6ebf%2C599e98d4-0634-45b4-a685-04e908ad5375%2Ca432c8b8-71ce-4cb2-83bf-ef1d0997008b%2C9711a4c3-92b3-4c38-b844-8071aac71273 | Concrete | Circular Joint |  |  | Circular Joint
279a4a4e-ad15-451d-943e-d1220ac1efbb | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 8 |  |  |  | 2025-06-01 15:07:21 AEST | 2025-06-01 15:08:55 AEST | 30011704-user5@smec.com | james.stone@smec.com | 646 | 8 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | Kp |  | Drummy concrete around edge of circumferential edge | [5 empty] | efed3714-485d-48cd-be95-3197697b4120,35324cf5-533b-45bc-8f75-2a497755f843,a91c2e89-2b7e-4794-bac3-0227d3fbe3ed | ,, | https://web.fulcrumapp.com/photos/view?photos=efed3714-485d-48cd-be95-3197697b4120%2C35324cf5-533b-45bc-8f75-2a497755f843%2Ca91c2e89-2b7e-4794-bac3-0227d3fbe3ed | Concrete | Circular Joint | Drummy |  | Circular Joint
b3a55e8a-29cf-4de1-8fc2-87a20ccd28e9 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 8 |  |  |  | 2025-06-01 15:15:54 AEST | 2025-06-01 15:18:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 650 | 7 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | Kp |  | Ground water ingress | [5 empty] | d9633829-d3c6-4e3c-8e97-d7676a9dcb70,78bfa973-8d02-4b81-933a-58938dda3be6 | , | https://web.fulcrumapp.com/photos/view?photos=d9633829-d3c6-4e3c-8e97-d7676a9dcb70%2C78bfa973-8d02-4b81-933a-58938dda3be6 | Concrete | Circular Joint |  |  | Circular Joint
8267061e-08c2-486f-8f1a-19f65e46fbb5 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 7 |  |  |  | 2025-06-01 17:22:09 AEST | 2025-06-01 17:24:10 AEST | 30011704-user5@smec.com | james.stone@smec.com | 656 | 9 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [57 empty] | Kp |  | Drummy concrete and loose aggregate | [5 empty] | 72578c1e-a434-42f1-8b9d-b06e82958686,4227011d-2bb2-4761-89a4-fa8d5f518090,37435227-00c6-4a5c-98d7-dca7b8abb833,54b92c2e-c89d-443f-9255-4ab0187c5ebb | ,,, | https://web.fulcrumapp.com/photos/view?photos=72578c1e-a434-42f1-8b9d-b06e82958686%2C4227011d-2bb2-4761-89a4-fa8d5f518090%2C37435227-00c6-4a5c-98d7-dca7b8abb833%2C54b92c2e-c89d-443f-9255-4ab0187c5ebb | Concrete | Circular Joint | Drummy,Loose |  | Circular Joint
1e8fba6c-a47d-4317-9581-c51218bd7576 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 7 |  |  |  | 2025-06-01 17:45:49 AEST | 2025-06-01 17:48:40 AEST | 30011704-user5@smec.com | james.stone@smec.com | 658 | 8 |  | Hydrophilic Joint Seal (Radial Joint) | [59 empty] | Radial joint has Grout delaminating/ Drummy concrete | [5 empty] | 78d7c3ab-77ee-4312-b9a1-6b3cf75691bc,14870f8c-bd17-4a13-abc2-58e9467f803b,2012d067-fa4d-4961-97b0-6efe0a78ed4f,d28b53c7-3923-44b2-8fde-30a37b2265cb | ,,, | https://web.fulcrumapp.com/photos/view?photos=78d7c3ab-77ee-4312-b9a1-6b3cf75691bc%2C14870f8c-bd17-4a13-abc2-58e9467f803b%2C2012d067-fa4d-4961-97b0-6efe0a78ed4f%2Cd28b53c7-3923-44b2-8fde-30a37b2265cb | Concrete | Radial Joint | Drummy
6836bd48-1892-46c7-8f90-50ecc2fd75c7 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | de0202b7-af7b-49d8-8a9d-c6816bcf9505 | 7 |  |  |  | 2025-06-01 17:58:51 AEST | 2025-06-01 18:00:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 659 | 9 |  | Hydrophilic Joint Seal (Circle Joint) | [59 empty] | Circumferential joint has Grout delaminating/ Drummy concrete | [5 empty] | 5a0d33ac-15b9-405a-883d-b2dcf03cfdd6,dee4e6f0-2190-4e36-bb7f-a1757bcf1146 | , | https://web.fulcrumapp.com/photos/view?photos=5a0d33ac-15b9-405a-883d-b2dcf03cfdd6%2Cdee4e6f0-2190-4e36-bb7f-a1757bcf1146 | Concrete | Circular Connection,Circular Joint | Drummy
2aab4f75-f5f3-4b3b-81ef-50b8ce0390be | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:55:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 662 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27036 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 662, 11 to 1 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Corrosion Level 3. Bolt nut missing at 3 o'clock | yes |  |  |  |  | 634fe6dc-7791-49cf-b83e-fad59c80ddac,9b1e24d2-370c-42f8-97bd-363009d69dc4 | , | https://web.fulcrumapp.com/photos/view?photos=634fe6dc-7791-49cf-b83e-fad59c80ddac%2C9b1e24d2-370c-42f8-97bd-363009d69dc4 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
37f93db4-ee95-47b7-b801-3979e5fd2661 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 03:32:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 663 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84634 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 663, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | No change | no |  |  |  |  | 2a1e1119-b02f-45ee-8425-e8a8ea611ea9,6d80502e-12b1-4f8a-8441-8c1eba424122 | , | https://web.fulcrumapp.com/photos/view?photos=2a1e1119-b02f-45ee-8425-e8a8ea611ea9%2C6d80502e-12b1-4f8a-8441-8c1eba424122 | Concrete | Circular Joint | Drummy
904b33de-9625-46f8-ae16-a6b347b49db5 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:58:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 664 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84635 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 664, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Not accessible | [8 empty] | Concrete | Radial Joint | Drummy
7b0e18a3-ea2f-49dd-a101-78bfaa7ff7e4 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 664 | 8 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84636 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 664, 8 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 500mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 500mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
0304f442-cfa8-4c59-b28d-3fb4e6b15b62 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 03:25:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 670 | 1 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27038 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 670, 1 O'clock, Steel Channel Support Bracket |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion. |  | Channel anchor bolts have Level 2 Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Extremely minor corrosion | no |  |  |  |  | bbc84ebe-a098-4f63-904a-3e014fbd66ec,73c7acbd-715f-4989-b061-03f83ab56451,d5c98cdb-73ff-463d-ba8f-c76a3908114b | ,, | https://web.fulcrumapp.com/photos/view?photos=bbc84ebe-a098-4f63-904a-3e014fbd66ec%2C73c7acbd-715f-4989-b061-03f83ab56451%2Cd5c98cdb-73ff-463d-ba8f-c76a3908114b | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
e110ddf8-a47e-4709-a118-48bd9017d257 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 03:27:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 670 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 96838 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 670, 3 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | One channel anchor bolt missing. |  | One channel anchor bolt missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Steelwork Remediation Crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | 93953b61-a45c-4228-a3b5-e6c3a5d7c7b2,25572b66-44ae-448c-9352-bfbb07a26fe9 | , | https://web.fulcrumapp.com/photos/view?photos=93953b61-a45c-4228-a3b5-e6c3a5d7c7b2%2C25572b66-44ae-448c-9352-bfbb07a26fe9 | Steel | Channel Bracket-Bolt | Missing
a2ca0739-f74b-423c-838c-d9e7848a1002 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 03:22:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 671 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84637 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 671, 11 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | Delamination is still noted | no |  |  |  |  | 992405c1-9f0e-48be-b0d7-8b2244a9837f,ca2f2952-48c8-4cee-8be0-c49df73f8f93 | , | https://web.fulcrumapp.com/photos/view?photos=992405c1-9f0e-48be-b0d7-8b2244a9837f%2Cca2f2952-48c8-4cee-8be0-c49df73f8f93 | Concrete | Circular Joint | Drummy
d610b0fd-43d5-4a33-b9ec-83b8ec4ebcbe | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 05:52:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 672 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84638 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 672, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Defect not present at specified location. | yes |  |  |  |  | f0b422df-ab21-4a7d-86d2-e40d8bf5a300 |  | https://web.fulcrumapp.com/photos/view?photos=f0b422df-ab21-4a7d-86d2-e40d8bf5a300 | Concrete | Circular Joint | Drummy
2eefaaf5-7c2f-41b7-a922-5c473286c238 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 674 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68722 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Bored Tunnel - Segment Bolted Joint Circle Joint) - Ring 674, 4 o'clock. Concrete Shell Segment. Identified in 2019. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Previously listed under AIMS defect 30761 under incorrect AIMS quadrant. 30761 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint,Radial Joint | Drummy
c3e1a685-0324-4b2b-95bb-77dbf2a5e1e5 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 03:11:44 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 674 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27039 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 674, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 25% coverage. Channel anchor bolts have level 2 corrosion. |  | Steel channel support bracket has Level 3 - Medium Corrosion up to 25% coverage. Channel anchor bolts have level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Minor corrosion | no |  |  |  |  | ef98b4c1-5ec5-4ef5-8e0e-c5e861e3d500,3192c430-2ea4-4ba0-b07e-27228a8ddc7a | , | https://web.fulcrumapp.com/photos/view?photos=ef98b4c1-5ec5-4ef5-8e0e-c5e861e3d500%2C3192c430-2ea4-4ba0-b07e-27228a8ddc7a | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
346b0d7d-c3dc-4ea6-99c6-2711512ea75d | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 03:01:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 676 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27040 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 676, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor |  |  | Leak is still inactive | no |  |  |  |  | 09a9a28b-8729-47d2-8886-11de25a0841e,8bf23c10-3a51-4823-8de3-dc8321ad27d0 | , | https://web.fulcrumapp.com/photos/view?photos=09a9a28b-8729-47d2-8886-11de25a0841e%2C8bf23c10-3a51-4823-8de3-dc8321ad27d0 | Concrete | Grout Hole | Leaks |  | Not reinforcement
805544e1-20ad-41ec-bfca-8e19f6c675fb | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 06:02:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 676 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84639 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 676, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Defect not present at specified location. | yes |  |  |  |  | a7d7dea2-6c71-40b7-9a97-2f59386d1ea2 |  | https://web.fulcrumapp.com/photos/view?photos=a7d7dea2-6c71-40b7-9a97-2f59386d1ea2 | Concrete | Radial Joint | Drummy
79edba60-77b6-4b19-b2b1-260cae42f3d8 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:59:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 677 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27041 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 677, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | SS |  | Leak is still active | no |  |  |  |  | 69e6e0d3-1ab8-4913-a78a-c301ac756682,8ed5a28f-a22c-4d87-9eb4-003d0f57134a | , | https://web.fulcrumapp.com/photos/view?photos=69e6e0d3-1ab8-4913-a78a-c301ac756682%2C8ed5a28f-a22c-4d87-9eb4-003d0f57134a | Concrete | Grout Hole | Leaks |  | Not reinforcement
f9136cc1-92ba-41bc-a303-d26dd18b5c76 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:56:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 677 | 10 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84640 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 677, 10 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 500mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 500mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination extends from bolted anchor pocket out to mid area | no |  |  |  |  | 47660f65-4e56-4312-b098-29cdabea78e5,9bb58553-c499-4ea8-afd8-cad0ccab0b1c | , | https://web.fulcrumapp.com/photos/view?photos=47660f65-4e56-4312-b098-29cdabea78e5%2C9bb58553-c499-4ea8-afd8-cad0ccab0b1c | Concrete | Radial Joint | Drummy
27cd86e9-78f1-4f76-9e05-8e7318f0e905 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 06:14:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 678 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84642 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 678, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Defect not present at the specified location. | yes | [7 empty] | Concrete | Radial Joint | Drummy
829785c4-54f1-45a2-a40f-c6f810dfa540 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 680 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27042 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 680, 2 o'clock. Concrete Shell Segment.,Still existing in 2017. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 400mm x 250mm. |  | Concrete shell segment has drummy concrete over an area of 400mm x 250mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Reinforcement | Drummy
adf7a818-2a2d-4fc4-ac09-ee992643d7f3 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 681 | 7 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84643 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 681, 7 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 500mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 500mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Break out grout locally, abrasive blast steelwork, and inspect by competent engineer to develop repair detail. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
a98cf7ed-80c5-4bf0-9ea6-45af6bebbd80 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:43:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 682 | 10 | Steel Channel Bracket | Steel Channel Bracket |  | 96839 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 45267.4754 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 682, 10 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Medium - Low Corrosion |  | Steel channel support bracket has Level 2 Medium - Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Minor corrosion | no |  |  |  |  | d0fc68d9-519d-4f7b-9781-3b99aa877b67,2e1060f2-3da1-4a82-a807-8902edd9d0eb | , | https://web.fulcrumapp.com/photos/view?photos=d0fc68d9-519d-4f7b-9781-3b99aa877b67%2C2e1060f2-3da1-4a82-a807-8902edd9d0eb | Steel | Channel Bracket | Corrosion-Surface
08f6d6dc-3d2c-4a84-8dce-ccb82d725ee3 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:42:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 682 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 84644 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 682, 12 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Channel anchor bolt is missing. BHP Review 30/01/2024 AC: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. |  | Channel anchor bolt is missing. BHP Review 30/01/2024 AC: There are 3 bolt holes but only 1 anchor bolt is required as per drawing 117-C-00241/3. Not missing bolts, they are supposed to suit blind holes in the concrete tunnel. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. Defect to be deleted in the next inspection. | GTS Specification. Concrete remediation crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | 01fcde2c-d95d-4e8f-b178-8c73a3612bcb,5e35a737-ae2d-401b-8b5e-1bfe22d5fe52 | , | https://web.fulcrumapp.com/photos/view?photos=01fcde2c-d95d-4e8f-b178-8c73a3612bcb%2C5e35a737-ae2d-401b-8b5e-1bfe22d5fe52 | Concrete,Steel | Channel Bracket,Channel Bracket-Bolt | Missing
b2851992-b6c0-4259-94bc-4487944ddb53 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 05:59:32 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 682 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 27043 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 4 | Level 4 | Level 4 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 682, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 - Major Corrosion |  | Steel channel support bracket has Level 4 - Major Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all repair affected areas, corroded areas. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor | HM |  | Moderate level corrosion is evident in the support bracket and bolts | yes |  |  |  |  | 0d5d247e-8862-4665-bf6e-7c310600d939,e30f430e-49d4-43e9-bbed-e9e22dd8789f | , | https://web.fulcrumapp.com/photos/view?photos=0d5d247e-8862-4665-bf6e-7c310600d939%2Ce30f430e-49d4-43e9-bbed-e9e22dd8789f | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface |  | Only suface not heavy
476d3273-e57e-46b9-b429-8fa184aad9ba | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 06:04:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 682 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27662 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 682, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | HM |  | No active leak present | yes |  |  |  |  | 40349bea-cd3f-48f5-a5db-d81e8b2bd076 |  | https://web.fulcrumapp.com/photos/view?photos=40349bea-cd3f-48f5-a5db-d81e8b2bd076 | Concrete |  | Leaks |  | Not reinforcement
7182e7e8-90fb-4f5a-b425-7af0a2f52eef | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 05:53:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 682 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27358 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Corrosion Under Buildup |  | Corrosion Under Buildup | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 682, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts have level 4 corrosion. |  | Channel anchor bolts have level 4 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | anchor bolt is HSE not financial | Priority: P3 |  |  |  | Repair anchor bolts as per BHP standard drawing 000-S-12598. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | HM |  | Anchor bolts and bracket corrosion is evident. | no |  |  |  |  | de746a5b-44bf-4a86-9983-0db113cafc69,6c4b618c-5e61-4d98-9ff2-17db0e156a47,4130c26a-5096-442c-b328-9586ab10e9ee | ,, | https://web.fulcrumapp.com/photos/view?photos=de746a5b-44bf-4a86-9983-0db113cafc69%2C6c4b618c-5e61-4d98-9ff2-17db0e156a47%2C4130c26a-5096-442c-b328-9586ab10e9ee | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
a2754539-0743-40e6-8928-80279d17d9f2 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-02 00:15:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 686 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27044 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 686, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Medium Corrosion |  | Steel channel support bracket has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Minor corrosion | no |  |  |  |  | dcc89d9f-1428-4d14-b742-aa0f9819ece4,e85ecc69-4ce3-4e5e-b3d7-fafb90b324ab,814525a6-9c19-4ed1-8216-54429b71cc68,3443ed37-0d93-4504-89be-2ee5ef67fb0f | ,,, | https://web.fulcrumapp.com/photos/view?photos=dcc89d9f-1428-4d14-b742-aa0f9819ece4%2Ce85ecc69-4ce3-4e5e-b3d7-fafb90b324ab%2C814525a6-9c19-4ed1-8216-54429b71cc68%2C3443ed37-0d93-4504-89be-2ee5ef67fb0f | Steel | Channel Bracket | Corrosion-Surface
9c86e99d-1025-490e-a079-6c956a330280 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 03:17:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 686 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84645 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 686, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is not evident. Previous patch is sufficient. | yes |  |  |  |  | b830ffab-0ea6-49b1-9d8e-679514291169,d9c4abd8-460f-48e2-84ed-2088c6ba057f | , | https://web.fulcrumapp.com/photos/view?photos=b830ffab-0ea6-49b1-9d8e-679514291169%2Cd9c4abd8-460f-48e2-84ed-2088c6ba057f | Concrete | Circular Joint | Drummy
016c99d9-fa7b-4d65-8278-4b0c29e238c8 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:29:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 687 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84646 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 687, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | Delamination of grout is still noted | no |  |  |  |  | 928e447d-c1ef-4064-b40d-a600f9faca37,8f9cc230-cd00-428e-a5a3-a2b33815ff22 | , | https://web.fulcrumapp.com/photos/view?photos=928e447d-c1ef-4064-b40d-a600f9faca37%2C8f9cc230-cd00-428e-a5a3-a2b33815ff22 | Concrete | Circular Joint | Drummy
e22e90fe-419d-4cf0-9dc3-94e2fd651d39 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:25:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 690 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27045 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 690, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 1 - Minor corrosion. |  | Channel anchor bolts have Level 1 - Minor corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Minor corrosion | no |  |  |  |  | 3549c27e-9ba8-473b-9e78-ab4edf020211,a91f1f06-6293-4d32-9ce6-416078cc37d7 | , | https://web.fulcrumapp.com/photos/view?photos=3549c27e-9ba8-473b-9e78-ab4edf020211%2Ca91f1f06-6293-4d32-9ce6-416078cc37d7 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
b6b4dbbd-a9ae-49ce-908d-ee962aa9d829 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 17 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:20:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 690 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84647 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 690, 12 O'Clock, Segmental Concrete | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 300mm x 100mm adjacent to channel support bracket |  | Concrete shell segment has drummy concrete over an area of 300mm x 100mm adjacent to channel support bracket. FLAG | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | SS |  | This delamination is in the main concrete of the segment, not at one of the bolted connections. Suggest further investigation. | no |  |  |  |  | 7625d965-7759-4c6f-bf78-45cbe02718bc,0812a3d2-c9b4-41db-9034-6fb8ff6fefb9,00dcd9e6-e554-4def-a173-3a7fff856a8f | ,, | https://web.fulcrumapp.com/photos/view?photos=7625d965-7759-4c6f-bf78-45cbe02718bc%2C0812a3d2-c9b4-41db-9034-6fb8ff6fefb9%2C00dcd9e6-e554-4def-a173-3a7fff856a8f | Concrete | Channel Bracket | Drummy
e3c31ec2-c9ba-4801-b1ec-b5748b5b3d6e | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 13 |  |  |  | 2025-05-31 03:32:22 AEST | 2025-05-31 03:38:26 AEST | 30011704-user5@smec.com | james.stone@smec.com | 661 | 12 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Crack generated from preformed anchor holes | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  | Rare (Failure within 50 years) |  | Ring 661, 12 o'clock | [24 empty] | BS |  | 0.1mm wide crack extending from the preformed anchor hole. | [5 empty] | 6b2ea394-8867-4a1b-bc4c-23b0754dbae2,ea0ca6c1-df29-49d5-85f3-674bb8405a36,fbd859e5-da06-435b-aade-dc84938b92e7 | ,, | https://web.fulcrumapp.com/photos/view?photos=6b2ea394-8867-4a1b-bc4c-23b0754dbae2%2Cea0ca6c1-df29-49d5-85f3-674bb8405a36%2Cfbd859e5-da06-435b-aade-dc84938b92e7 | Concrete | Grout Hole | Crack |  | Grout Hole
e0baf49e-5edf-41ef-970b-c76ee4945643 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 9 |  |  |  | 2025-06-01 02:43:46 AEST | 2025-06-01 02:45:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 683 | 11 |  | Segment Bolted Joint (Circle Joint) | [17 empty] | 2 | [14 empty] | Bolted anchor grouted recess |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | SS | [7 empty] | 95d2eec5-d0cd-4990-856f-30ec95e3aaee,4925e19f-6bd7-49f3-84d8-a7f0090580a8 | , | https://web.fulcrumapp.com/photos/view?photos=95d2eec5-d0cd-4990-856f-30ec95e3aaee%2C4925e19f-6bd7-49f3-84d8-a7f0090580a8 | Concrete | Circular Joint | Drummy
2d1c2b45-6974-4b9c-a851-1d3fae1b16b8 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 9 |  |  |  | 2025-06-01 03:14:05 AEST | 2025-06-01 03:16:36 AEST | 30011704-user5@smec.com | james.stone@smec.com | 673 | 11 | [26 empty] | Poor Construction Methods | [7 empty] | Ring bolted connection grouted pocket |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | [19 empty] | SS | [7 empty] | c0d0e85f-4974-440d-be94-25edad77d46f,09c88350-0489-43b1-9daf-8bd7b96cebe9 | , | https://web.fulcrumapp.com/photos/view?photos=c0d0e85f-4974-440d-be94-25edad77d46f%2C09c88350-0489-43b1-9daf-8bd7b96cebe9 | Concrete | Circular Joint | Drummy
5f0ae01e-1c9c-4a6d-86e2-2c88db68cd17 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 9 |  |  |  | 2025-06-01 03:18:43 AEST | 2025-06-01 03:20:13 AEST | 30011704-user5@smec.com | james.stone@smec.com | 672 | 11 |  | Segment Bolted Joint (Circle Joint) | [17 empty] | 3 | [14 empty] | Ring edge bolted connection pocket |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | [19 empty] | SS | [7 empty] | 9ee2f83e-6a9b-4d0b-a92c-09b38d57da69,0ac097b8-fce0-40d9-bb3c-fbc1b0e21e56 | , | https://web.fulcrumapp.com/photos/view?photos=9ee2f83e-6a9b-4d0b-a92c-09b38d57da69%2C0ac097b8-fce0-40d9-bb3c-fbc1b0e21e56 | Concrete | Circular Joint | Drummy
3f19142f-c984-4334-b4e3-af44662b856e | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 10 |  |  |  | 2025-06-01 03:10:43 AEST | 2025-06-01 03:12:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 688 | 4 |  | Channel Anchor Bolts | [32 empty] | Cable tray support bracket bolt |  |  |  |  | Class 3 - Medium corrosion | [19 empty] | HM | [7 empty] | bcf44a75-3d2d-4f2b-83fe-316c383dbc32 |  | https://web.fulcrumapp.com/photos/view?photos=bcf44a75-3d2d-4f2b-83fe-316c383dbc32 | Steel | Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Loose |  | Loose
abdb35ea-034e-47c2-b094-583566d659c9 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 10 |  |  |  | 2025-06-01 03:17:25 AEST | 2025-06-01 03:18:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 686 | 4 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete shell | [5 empty] | Spalled concrete 20 x 20 mm | [18 empty] | HM | [7 empty] | 2ed614e2-2b9c-45f7-bac9-cd06bfecfc2a |  | https://web.fulcrumapp.com/photos/view?photos=2ed614e2-2b9c-45f7-bac9-cd06bfecfc2a | Concrete | Circular Joint | Surface Damage |  | Circular Joint
a92c744b-a63f-486a-ad75-1fe612f1d34e | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 10 |  |  |  | 2025-06-01 05:50:29 AEST | 2025-06-01 05:51:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 683 | 4 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete shell | [5 empty] | Spalled concrete at the joint | [18 empty] | HM | [7 empty] | 32726b3b-d523-41f0-a8ec-5fb7bc4a674f |  | https://web.fulcrumapp.com/photos/view?photos=32726b3b-d523-41f0-a8ec-5fb7bc4a674f | Concrete | Circular Joint | Surface Damage |  | Circular Joint
9e6dd2e6-21c2-4ca4-99dc-e007587c1b26 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 10 |  |  |  | 2025-06-01 06:04:51 AEST | 2025-06-01 06:05:45 AEST | 30011704-user5@smec.com | james.stone@smec.com | 682 | 3 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | HM | [7 empty] | 733d7f0e-f17d-4912-bf87-3228a02e63d7,01bc86dc-b050-4ebf-a1d0-69b04fc23a08 | , | https://web.fulcrumapp.com/photos/view?photos=733d7f0e-f17d-4912-bf87-3228a02e63d7%2C01bc86dc-b050-4ebf-a1d0-69b04fc23a08 | Concrete | Circular Joint | Drummy
9eae968d-a235-4dbd-a9cd-b2988c4ea621 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 10 |  |  |  | 2025-06-01 06:07:42 AEST | 2025-06-01 06:08:36 AEST | 30011704-user5@smec.com | james.stone@smec.com | 681 | 3 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete shell | [5 empty] | Minor spalling of concrete | [18 empty] | HM | [7 empty] | 5a1e7d95-a27d-4903-a7a9-06e1f58a6b95,033c0ff3-8cf6-4278-8760-40ad2e063e3f | , | https://web.fulcrumapp.com/photos/view?photos=5a1e7d95-a27d-4903-a7a9-06e1f58a6b95%2C033c0ff3-8cf6-4278-8760-40ad2e063e3f | Concrete | Grout Hole | Surface Damage |  | Grout Hole
8849fc93-364a-4ecb-9f2a-691a7e658377 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 10 |  |  |  | 2025-06-01 06:09:37 AEST | 2025-06-01 06:10:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 680 | 4 |  | Channel Anchor Bolts | [32 empty] | Cable tray support bracket bolt | [5 empty] | Minor corrosion | [18 empty] | HM | [7 empty] | 67babf15-a711-46f0-944e-27fa5a143d9c,b2e233e0-a7ff-43aa-9168-42eeb2b16ff5 | , | https://web.fulcrumapp.com/photos/view?photos=67babf15-a711-46f0-944e-27fa5a143d9c%2Cb2e233e0-a7ff-43aa-9168-42eeb2b16ff5 | Steel | Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Corrosion-Surface
998d08db-1bca-456d-9fd9-3a87d38b8982 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 10 |  |  |  | 2025-06-01 06:14:42 AEST | 2025-06-01 06:15:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 681 | 3 |  |  | Cable tray | [31 empty] | Cable tray | [5 empty] | Cable tray corroded with section loses | [18 empty] | HM | [7 empty] | fab24070-0f0f-4d96-9e0e-0c98b3a5fef0,9c00eb7d-2119-437a-9d42-ca7c09a99dfe | , | https://web.fulcrumapp.com/photos/view?photos=fab24070-0f0f-4d96-9e0e-0c98b3a5fef0%2C9c00eb7d-2119-437a-9d42-ca7c09a99dfe | Steel | Misc (Pipes/Cable Tray/etc)
93abbc9d-00b8-49e7-839b-aec9c3570f78 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 11 |  |  |  | 2025-06-01 06:10:32 AEST | 2025-07-29 02:13:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 680 | 4 O'Clock |  | Channel Anchor Bolts | [16 empty] | Missing nut, haven't been placed |  | Missing Nut |  |  | Financial |  |  | Missing Component |  |  | Severity Level 2 |  |  | Possible (Failure within 5 Years) |  | 4'O Clock on the steel frame |  | Shear failure of bolt |  |  |  | Missing Nut | [18 empty] | DR |  | Structural Steel has significant loss of section. 5 o'clock bolt nut fully corroded as well as the 4 o'clock bolt nut. | [5 empty] | eae857e3-3b47-45f7-89fd-5648f4959e2e,008f1080-a442-4fee-b66a-327d55730927,5ab172e9-3055-4c60-8ab5-c25ece040604,20b03f77-8a2e-4721-9d80-a4dda7ab44b0,c84cd6ca-a791-4ddd-bc2f-7dcd574cda8b | ,,,, | https://web.fulcrumapp.com/photos/view?photos=eae857e3-3b47-45f7-89fd-5648f4959e2e%2C008f1080-a442-4fee-b66a-327d55730927%2C5ab172e9-3055-4c60-8ab5-c25ece040604%2C20b03f77-8a2e-4721-9d80-a4dda7ab44b0%2Cc84cd6ca-a791-4ddd-bc2f-7dcd574cda8b | Steel | Walkway Support | Missing |  | Walkway Support not Channel Bracket
b681d663-ca52-4c01-b1c0-ac0c2ce1ec50 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 12 |  |  |  | 2025-06-01 02:59:25 AEST | 2025-06-01 03:04:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 664 | 2 to 3 o'clock |  | Channel Anchor Bolts | [15 empty] | Corrosion - Connection |  | 2 |  |  |  | Health & Safety |  |  |  | Corrosion and connectivity |  | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Level 2 corrosion to top bolt and unlighted nut at 3 o'clock |  | Rupture |  |  |  | Surface corrosion and not tighten nuts |  | Loss of minor services (NOT water pipe) | [16 empty] | BS |  | Bolt corrosion and nuts not tighten | [5 empty] | 5d01e366-5527-4c6a-844a-9afea15604bb,716a74b7-61c1-452e-bb34-0969886df5d7 | , | https://web.fulcrumapp.com/photos/view?photos=5d01e366-5527-4c6a-844a-9afea15604bb%2C716a74b7-61c1-452e-bb34-0969886df5d7 | Steel | Channel Bracket-Bolt | Corrosion-Surface
badbe164-cd03-4595-b905-5c8e39e4949d | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 12 |  |  |  | 2025-06-01 03:13:30 AEST | 2025-06-01 03:16:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 669 | 3 |  | Segment Bolted Joint (Circle Joint) | [15 empty] | Concrete Damage due to Cast- In |  | 2 |  |  |  | Health & Safety |  |  | Atmospheric Corrosion of Cast-In |  |  | Severity Level 2 |  |  | Possible (Failure within 5 Years) |  | Ring 669, 3 o'clock |  | Shear failure of bolt |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | [16 empty] | BS |  | New drummy area | [5 empty] | 2e84975d-f899-4c34-b85f-cb0ea458452e |  | https://web.fulcrumapp.com/photos/view?photos=2e84975d-f899-4c34-b85f-cb0ea458452e | Concrete | Circular Joint | Drummy
03e3a524-267e-4852-861b-7bffc4dbfb58 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 8 |  |  |  | 2025-06-01 18:11:23 AEST | 2025-06-01 18:12:31 AEST | 30011704-user5@smec.com | james.stone@smec.com | 661 | 9 |  | Hydrophilic Joint Seal (Circle Joint) | [57 empty] | Kp |  | Circumferential joint has Grout delaminating/ Drummy concrete | [5 empty] | ab397786-d056-4188-b93b-fb57cf7fb859,758909ae-3270-4757-8d62-affe7d154e89,9c917162-bac9-4abf-a12e-3cde78ace4f8,0ac03d55-a142-424b-9a90-ffa274684a50 | ,,, | https://web.fulcrumapp.com/photos/view?photos=ab397786-d056-4188-b93b-fb57cf7fb859%2C758909ae-3270-4757-8d62-affe7d154e89%2C9c917162-bac9-4abf-a12e-3cde78ace4f8%2C0ac03d55-a142-424b-9a90-ffa274684a50 | Concrete | Circular Connection,Circular Joint | Drummy
05b7a42a-dd3a-4ebd-b66e-ac96d48e0cd5 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 6 |  |  |  | 2025-06-02 05:01:29 AEST | 2025-06-02 05:05:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 662 | 6 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Concrete surface damage | 2 |  |  |  | Health & Safety |  |  | Poor Construction Methods |  |  | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | Ring 662, 6 o'clock |  |  | Break up of mortar surface |  |  | mortar damage. possible surface skimming at the time of CP installation. No critical structural defect. | [18 empty] | BS | [7 empty] | 33fa307c-97f2-43b4-a12f-90bb6a7db268,a676da64-267b-4659-8b45-26aa055f3b66,38f0b5d8-72b9-48b7-8289-4a316e2b919f | ,, | https://web.fulcrumapp.com/photos/view?photos=33fa307c-97f2-43b4-a12f-90bb6a7db268%2Ca676da64-267b-4659-8b45-26aa055f3b66%2C38f0b5d8-72b9-48b7-8289-4a316e2b919f | Concrete | Mortar | Surface Damage
c731468f-b99b-4be5-9e8d-608a4d531afe | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 4 |  |  |  | 2025-07-30 03:26:41 AEST | 2025-07-30 03:38:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 688 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Bogdan Stanca |  | The structural steel is corroded with loss of section up to 2mm. The steel is anchored using 3 bolts. The lower bolt has advanced corrosion with nuts fully corroded. The middle bolt has medium corrosion with the nut fully corrected. The top bolt and nut have surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 53487bcb-7eab-4ba9-8ca7-6842268e90e6,dbb0fb4f-6e24-4f42-850a-fc0b819ae855,0bd93b48-5b88-4f00-b77f-f7831c0f1f3b,b243b3ef-3e2b-4c1e-b9d0-4164d767b2b2,16960458-2473-479b-b3ba-28f8e325a26e,c94b605a-11e8-4adf-8c1f-67c0aa10e5ca | Structural Steel general condition ,Structural Steel loss of section ,structural Steel loss of section ,Lower bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=53487bcb-7eab-4ba9-8ca7-6842268e90e6%2Cdbb0fb4f-6e24-4f42-850a-fc0b819ae855%2C0bd93b48-5b88-4f00-b77f-f7831c0f1f3b%2Cb243b3ef-3e2b-4c1e-b9d0-4164d767b2b2%2C16960458-2473-479b-b3ba-28f8e325a26e%2Cc94b605a-11e8-4adf-8c1f-67c0aa10e5ca | Steel | Conveyor Support,Walkway Support | Corrosion-Heavy,Corrosion-Surface
3c3e5fc5-747d-4a97-a13e-c907807732c4 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 4 |  |  |  | 2025-07-30 03:39:00 AEST | 2025-07-30 03:45:10 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 688 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Bogdan Stanca |  | The Structural Steel column has advanced corrosion at the lower end with significant loss of section to the flanges. 1mm section remaining in some areas. The base plate has surface corrosion, anchor bolts have advanced corrosion with nuts fully corroded. |  |  |  | no |  | 4073192c-4500-47e1-a5d7-082140e837df,f5acef72-9e05-45a0-a11b-aca5fc4b65d0,bd290326-e657-4cb2-8f95-2677ade924e5,af27eb41-e269-4a39-8701-faf1c0abbe7e,9cd6b752-fe73-450b-90e1-3be1fce01139,c6308e05-206a-4edc-a21d-1b8f0621d46c | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=4073192c-4500-47e1-a5d7-082140e837df%2Cf5acef72-9e05-45a0-a11b-aca5fc4b65d0%2Cbd290326-e657-4cb2-8f95-2677ade924e5%2Caf27eb41-e269-4a39-8701-faf1c0abbe7e%2C9cd6b752-fe73-450b-90e1-3be1fce01139%2Cc6308e05-206a-4edc-a21d-1b8f0621d46c | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface
9d4222c8-6669-4db8-bbfe-05c1b37e1dd9 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 4 |  |  |  | 2025-07-30 05:56:12 AEST | 2025-07-30 06:48:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 692 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Bogdan Stanca |  | The structural steel is corroded with loss of section up to 2mm. The steel is anchored using 3 bolts. The lower bolt is not visible assuming that it has advanced corrosion with the nut fully corroded . The middle bolt has medium corrosion with the nut fully corrected. The top bolt and nut have surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 562da523-c40b-4f6a-8e23-716270b70ee0,3be01001-cfe5-4281-b0e3-d4ad9b7ecc13,a7d3c214-0d61-4081-af07-7f4a7a5f9ba4,4da8d232-2a85-494f-a252-f5e208e153a2 | Structural Steel general condition ,Structural Steel section loss,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=562da523-c40b-4f6a-8e23-716270b70ee0%2C3be01001-cfe5-4281-b0e3-d4ad9b7ecc13%2Ca7d3c214-0d61-4081-af07-7f4a7a5f9ba4%2C4da8d232-2a85-494f-a252-f5e208e153a2 | Steel | Conveyor Support,Walkway Support | Corrosion-Heavy,Corrosion-Surface
7bea7248-c66e-4ea6-a4f6-484baa6596f9 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 4 |  |  |  | 2025-07-30 05:59:42 AEST | 2025-07-30 06:03:19 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 692 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Bogdan Stanca |  | The Structural Steel column has advanced corrosion at the lower end with loss of section. The base plate has surface corrosion, anchor bolts have advanced corrosion with nuts fully corroded. |  |  |  | no |  | 54928306-1608-4245-b6f6-7be6b84866ca,d395f192-0a46-4902-b28d-3a35062ac6ba | , | https://web.fulcrumapp.com/photos/view?photos=54928306-1608-4245-b6f6-7be6b84866ca%2Cd395f192-0a46-4902-b28d-3a35062ac6ba | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface
da53c5f9-4ea0-41ca-b6a6-9cba03237bb6 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 4 |  |  |  | 2025-07-30 06:06:33 AEST | 2025-07-30 06:26:27 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 696 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Deepak |  | The structural steel is corroded with loss of section up to 1mm. The steel is anchored using 2 bolts. Both bolts are in good condition. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | a7605c20-6237-4bfd-9ec8-0b505cd4a1f7,eb007f09-9757-4e37-8d6e-a766bde3ecec | , | https://web.fulcrumapp.com/photos/view?photos=a7605c20-6237-4bfd-9ec8-0b505cd4a1f7%2Ceb007f09-9757-4e37-8d6e-a766bde3ecec | Steel | Conveyor Support,Walkway Support | Corrosion-Heavy,Corrosion-Surface
1814a6ae-5d4a-452b-a16e-7d7eef6683c3 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 4 |  |  |  | 2025-07-30 06:06:44 AEST | 2025-07-30 06:27:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 696 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Dr |  | The Structural Steel column has advanced corrosion at the lower end with loss of section. The base plate has surface corrosion, anchor bolts are in good condition. |  |  |  | no |  | db518743-e6cb-406b-aabc-bfbf94367b25,c6e8f120-c833-4c2f-855e-d1e4d5b5f3b2,2dd3b1e5-ca08-4a93-97a6-958024e7dd0a | ,, | https://web.fulcrumapp.com/photos/view?photos=db518743-e6cb-406b-aabc-bfbf94367b25%2Cc6e8f120-c833-4c2f-855e-d1e4d5b5f3b2%2C2dd3b1e5-ca08-4a93-97a6-958024e7dd0a | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface
0debda5c-02f2-453d-9d95-2ad9b12d47f4 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 4 |  |  |  | 2025-07-30 06:31:30 AEST | 2025-07-30 06:41:44 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 700 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Deepak |  | The structural steel is corroded with loss of section up to 2mm. The steel is anchored using 3 bolts. The bottom bolt is not visible, the middle bolt and nut are heavily corroded. The top bolt has surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 62dbb51e-e80b-4058-939f-a65a43e1a199,d42fb053-f275-4325-9aaa-ab984a7cd9a3,333f23d4-40e5-4870-aedd-1c39bb30f537,0d3f48d9-e2a7-4d83-a237-bbc8cb17e2f6 | Steel loss,Middle bolt condition ,Top bolt condition ,Structural Steel general condition | https://web.fulcrumapp.com/photos/view?photos=62dbb51e-e80b-4058-939f-a65a43e1a199%2Cd42fb053-f275-4325-9aaa-ab984a7cd9a3%2C333f23d4-40e5-4870-aedd-1c39bb30f537%2C0d3f48d9-e2a7-4d83-a237-bbc8cb17e2f6 | Steel | Conveyor Support,Walkway Support | Corrosion-Surface
fe35e605-9772-4541-ac99-dc2a1a9b0685 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 4 |  |  |  | 2025-07-30 06:31:43 AEST | 2025-07-30 06:42:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 700 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Dr |  | The Structural Steel column has advanced corrosion at the lower end with loss of section. The base plate has surface corrosion, anchor bolts are not accessible. |  |  |  | no |  | e73c270c-a2ca-431c-8db5-c253b1818181 |  | https://web.fulcrumapp.com/photos/view?photos=e73c270c-a2ca-431c-8db5-c253b1818181 | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface
bc577747-9557-48f4-8612-ca0066c35075 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 01:00:11 AEST | 2025-07-31 02:10:07 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 704 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Deepak |  | The structural steel is corroded with loss of section. The steel is anchored using 3 bolts. The bottom bolt is not visible, the middle bolt and nut are heavily corroded. The top bolt has surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 47ed0ee4-4d10-4df0-8a10-69fc33d31d94,f3a820e1-e43b-40aa-91b7-9de09f9ad596,575a6266-188f-473d-95f1-c8fb6d5c46ea | Structural Steel general condition ,Middle bolt not visible ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=47ed0ee4-4d10-4df0-8a10-69fc33d31d94%2Cf3a820e1-e43b-40aa-91b7-9de09f9ad596%2C575a6266-188f-473d-95f1-c8fb6d5c46ea | Steel | Conveyor Support,Walkway Support | Corrosion-Surface
8d7cd0b9-e69a-4b37-be63-d0e26239ddd8 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 01:00:27 AEST | 2025-07-31 01:51:50 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 704 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Dr |  | The Structural Steel column has surface corrosion at the lower end. The base plate and anchor bolts are not accessible. |  |  |  | no |  | a509edf0-58bd-42d4-bac3-9ce707ed2da8,1217e371-5152-46c2-b6f6-c62618055dd1 | , | https://web.fulcrumapp.com/photos/view?photos=a509edf0-58bd-42d4-bac3-9ce707ed2da8%2C1217e371-5152-46c2-b6f6-c62618055dd1 | Steel | Centre Support | Corrosion-Surface
fccab527-4568-49e8-bff4-905b7f7a69d9 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 01:37:21 AEST | 2025-07-31 01:42:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 708 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Bogdan Stanca |  | The Structural Steel column of 1 UC member is in good condition with no significant loss of section. Localised coating damage noted. The base plate is in good condition with minor coating damage. The anchor bolts and nuts have significant corrosion. |  |  |  | no |  | 9a78e5d9-5912-4040-87a0-85c48199dacd,bb65c7bd-031f-4df2-9708-7929ea5a4294,650c119b-232d-4fb2-b942-ddafac4c352e,b538f1e7-f7ff-477d-afa2-a68597b5740a | ,,, | https://web.fulcrumapp.com/photos/view?photos=9a78e5d9-5912-4040-87a0-85c48199dacd%2Cbb65c7bd-031f-4df2-9708-7929ea5a4294%2C650c119b-232d-4fb2-b942-ddafac4c352e%2Cb538f1e7-f7ff-477d-afa2-a68597b5740a | Steel | Centre Support | Corrosion-Heavy
6e419110-16fa-4e9d-bb28-693be5903d2b | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 01:59:09 AEST | 2025-07-31 02:08:22 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 716 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Bogdan Stanca |  | The structural steel has surface corrosion due to coating damage with localised section loss up to 2mm. The steel is anchored using 3 bolts. The bottom bolt and nut has surface corrosion. The middle bolt and nut are corroded. The top bolt and nut are in good condition with minor surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 175445b4-f8f9-4d13-a54b-ac650a6c9f93,1d771657-2b16-4227-959d-44522938deed,da0fb4ea-ca01-41fd-a535-6475f84bad41,9278f234-4c95-41cb-807e-646686f2b06e,dd7a679e-44dc-4572-83e8-09285182360f,c9011ccc-4cdc-431e-88fa-10121c3ad6d1 | Structural Steel general condition ,Structural Steel localised corrosion ,Bottom bolt condition ,Middle bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=175445b4-f8f9-4d13-a54b-ac650a6c9f93%2C1d771657-2b16-4227-959d-44522938deed%2Cda0fb4ea-ca01-41fd-a535-6475f84bad41%2C9278f234-4c95-41cb-807e-646686f2b06e%2Cdd7a679e-44dc-4572-83e8-09285182360f%2Cc9011ccc-4cdc-431e-88fa-10121c3ad6d1 | Steel | Conveyor Support,Walkway Support | Corrosion-Heavy,Corrosion-Surface
ca986917-2604-453e-8dd3-ab38be1266e0 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 01:10:11 AEST | 2025-07-31 01:17:07 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 716 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Bogdan Stanca |  | The Structural Steel column of 2 PFC members back to back has surface corrosion with no significant loss of section. The base plate has surface corrosion, anchor bolts have surface corrosion with nuts partially corroded. |  |  |  | no |  | 933fdff8-4575-453f-a5d7-3c6a272fc5d8,47d470ae-2281-4992-8a31-7742dce9303e,bea920dd-3fce-4a8f-ae27-88bc83c8aeff,877d738f-7fe0-4a74-92fc-b4fb9c984599,dc51527c-07d5-460d-9980-400e68466880,33d1c1ca-2930-4010-8cac-e4a9e45d9d93 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=933fdff8-4575-453f-a5d7-3c6a272fc5d8%2C47d470ae-2281-4992-8a31-7742dce9303e%2Cbea920dd-3fce-4a8f-ae27-88bc83c8aeff%2C877d738f-7fe0-4a74-92fc-b4fb9c984599%2Cdc51527c-07d5-460d-9980-400e68466880%2C33d1c1ca-2930-4010-8cac-e4a9e45d9d93 | Steel | Centre Support | Corrosion-Surface
17dde79a-272f-4c22-ae20-69ceb7ef7ba0 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 02:10:24 AEST | 2025-07-31 02:15:20 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 724 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Bogdan Stanca |  | The structural steel has surface corrosion due to coating damage. The steel is anchored using 3 bolts. The bottom bolt and nut are heavily corroded. The middle bolt and nut are corroded. The top bolt and nut are in good condition with minor surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 4dcfb876-1d2c-4e11-a5b2-8545b7bd8392,0960559e-78ab-4c67-8cbf-2288b7f94dd9,085ce75d-5695-45d7-b342-b0fad880a5da,a436fccc-6a37-4d9e-8efc-4ba044d7abc0,ad5a29f8-36c8-49ed-adf8-9fa3e8807b17 | Structural Steel general condition ,Localised surface corrosion ,Bottom bolt condition ,Middle bolt condition ,Middle bolt condition | https://web.fulcrumapp.com/photos/view?photos=4dcfb876-1d2c-4e11-a5b2-8545b7bd8392%2C0960559e-78ab-4c67-8cbf-2288b7f94dd9%2C085ce75d-5695-45d7-b342-b0fad880a5da%2Ca436fccc-6a37-4d9e-8efc-4ba044d7abc0%2Cad5a29f8-36c8-49ed-adf8-9fa3e8807b17 | Steel | Conveyor Support,Walkway Support | Corrosion-Surface
d21fd344-ee57-4d3a-b74f-ea5db3d4b9d1 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 01:18:25 AEST | 2025-07-31 01:20:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 724 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Bogdan Stanca |  | The Structural Steel column of 1 UC member has surface corrosion with no significant loss of section. The base plate has surface corrosion, anchor bolts have surface corrosion with nuts partially corroded. |  |  |  | no |  | ed48f7e6-c869-4234-9c49-4def7ad2e575,fd3c8526-e49a-4dbc-989e-7834ae6557f9,adac3b37-97cb-465a-af31-abfa2530cb09,03ed442c-a9cb-4fa6-afbf-6e4d12b1daed | ,,, | https://web.fulcrumapp.com/photos/view?photos=ed48f7e6-c869-4234-9c49-4def7ad2e575%2Cfd3c8526-e49a-4dbc-989e-7834ae6557f9%2Cadac3b37-97cb-465a-af31-abfa2530cb09%2C03ed442c-a9cb-4fa6-afbf-6e4d12b1daed | Steel | Centre Support | Corrosion-Surface
3293df4a-cdc9-43f4-99b1-cdbd4760bd37 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 01:27:15 AEST | 2025-07-31 02:09:53 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 732 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Bogdan Stanca |  | The structural steel has surface corrosion due to coating damage. The steel is anchored using 3 bolts. The bottom bolt is heavily corroded with the nut fully corroded. The middle bolt and nut are in good condition with surface corrosion. The top bolt and nut are in good condition with minor surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 14a17d95-6b17-4775-b52a-89e617719396,453ee3e7-5ddc-4d72-bbcd-2fe4a1afa3fb,dbdc571f-754c-4d78-9315-1ee61fd58a7f,7d7ec0f9-b9e3-4ee8-855d-d63e021c9b80 | Structural Steel general condition ,Bottom bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=14a17d95-6b17-4775-b52a-89e617719396%2C453ee3e7-5ddc-4d72-bbcd-2fe4a1afa3fb%2Cdbdc571f-754c-4d78-9315-1ee61fd58a7f%2C7d7ec0f9-b9e3-4ee8-855d-d63e021c9b80 | Steel | Conveyor Support,Walkway Support | Corrosion-Surface
bc856c66-be93-47d7-961e-fec760d74a11 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 01:21:06 AEST | 2025-07-31 02:08:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 732 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Bogdan Stanca |  | The Structural Steel column of 1 UC member is in good condition with no significant loss of section. Localised coating damage noted. The base plate is in good condition with minor coating damage. The anchor bolts are in good condition. |  |  |  | no |  | a5d3ed7d-43b7-4bda-99a2-5203aadea88d,1d6779f0-7403-40e2-9946-91d9e1473e8b,024e7887-11e6-4e94-9141-d1452a21af1d | ,, | https://web.fulcrumapp.com/photos/view?photos=a5d3ed7d-43b7-4bda-99a2-5203aadea88d%2C1d6779f0-7403-40e2-9946-91d9e1473e8b%2C024e7887-11e6-4e94-9141-d1452a21af1d | Steel | Centre Support
383f8cea-d9a1-4f6a-b6ba-38ed93738602 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 05:20:20 AEST | 2025-07-31 05:23:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 736 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Bogdan Stanca |  | The structural steel is in good condition with minor coating damage. The steel is anchored using 3 bolts. The bottom bolt is heavily corroded with the nut fully corroded. The middle bolt and nut are in good condition with surface corrosion. The top bolt and nut are in good condition with minor surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 47d02452-9ace-4b78-a3ec-3d1e5597cddd,f8394c09-2ec8-4ddf-95d7-1111f3a0e60d,a740ae38-0fe9-4335-a40b-677b6b1a27f2,ea990916-8853-499b-b7dd-4e69a3d086e3,f8ca2039-cf38-4614-994f-403fecbf9cdb | Structural Steel general condition ,Structural Steel condition ,Bottom bolt condition ,Middle bolt condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=47d02452-9ace-4b78-a3ec-3d1e5597cddd%2Cf8394c09-2ec8-4ddf-95d7-1111f3a0e60d%2Ca740ae38-0fe9-4335-a40b-677b6b1a27f2%2Cea990916-8853-499b-b7dd-4e69a3d086e3%2Cf8ca2039-cf38-4614-994f-403fecbf9cdb | Steel | Conveyor Support,Walkway Support | Corrosion-Surface
e9939a19-8a51-4cff-85ab-aee34708ea40 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 05:24:01 AEST | 2025-07-31 05:28:33 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 736 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Bogdan Stanca |  | The Structural Steel column of 1 UC member is in good condition with no significant loss of section. Localised coating damage noted. The base plate is in good condition with minor coating damage. The anchor bolts are in fair condition with surface corrosion. The nuts are heavily corroded. |  |  |  | no |  | 07038153-400c-41d5-874d-69640f6959f6,e208519c-5647-4d57-b110-db46cd798b91,02cb2d23-4d8a-403d-a6dd-c3d1d5a45bf1,9b32a176-0100-43da-83ad-05dd4a5031b2 | ,,, | https://web.fulcrumapp.com/photos/view?photos=07038153-400c-41d5-874d-69640f6959f6%2Ce208519c-5647-4d57-b110-db46cd798b91%2C02cb2d23-4d8a-403d-a6dd-c3d1d5a45bf1%2C9b32a176-0100-43da-83ad-05dd4a5031b2 | Steel | Centre Support | Corrosion-Surface
359726ee-0bd6-4459-a04d-8c50ae16f4e6 | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 05:30:43 AEST | 2025-07-31 05:39:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 740 | 5 o'clock |  |  | walkway structural steel and anchors | [56 empty] | Bogdan Stanca |  | The structural steel has surface corrosion with significant loss of section. The steel is anchored using 3 bolts. The bottom bolt is heavily corroded with the nut fully corroded. The middle bolt and nut are heavily corroded. The top bolt and nut are in good condition with minor surface corrosion. |  |  |  | yes | Access to conveyor support at 7 o'clock is not possible.the condition of structural steel at 5 o'clock is to be considered for 7 o'clock too. This is to be applied to all rings from here to 860. | 81dbaa52-0923-4d49-8ede-37fee927d2cf,5b1c5e3e-ad2c-47a5-ac23-f38d44dc2c22,dbb70f07-135a-4769-8614-6ff2b543c367,5f5bc8b3-18d9-4c32-9ed6-de1c70059394,b6e5ec31-18b2-4331-b683-1052366a9ba1 | Structural Steel general condition ,Vertical plate loss of section ,Bottom bolt condition ,Middle bolt and base plate condition ,Top bolt condition | https://web.fulcrumapp.com/photos/view?photos=81dbaa52-0923-4d49-8ede-37fee927d2cf%2C5b1c5e3e-ad2c-47a5-ac23-f38d44dc2c22%2Cdbb70f07-135a-4769-8614-6ff2b543c367%2C5f5bc8b3-18d9-4c32-9ed6-de1c70059394%2Cb6e5ec31-18b2-4331-b683-1052366a9ba1 | Steel | Conveyor Support,Walkway Support | Corrosion-Surface
c4ec0944-a3fb-4d4d-bed1-62fd7fbea00f | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 7ebe35c8-ed28-4786-ab73-7b881201e02a | 3 |  |  |  | 2025-07-31 05:43:03 AEST | 2025-07-31 05:48:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | Ring 740 | 6 o'clock |  |  | Structural Steel column | [56 empty] | Bogdan Stanca |  | The Structural Steel column of 1 UC member is in good condition with no significant loss of section. Localised coating damage noted. The base plate is in fair condition with minor coating damage and signs of steel corrosion under the coating protection. The anchor bolts are in mix condition one with surface corrosion and 2 with significant corrosion and loss of section especially the nuts. The 4th bolt is not accessible. |  |  |  | no |  | 113fedfe-64da-47f1-a703-bf291897321c,69e2bb58-b3ea-4116-a6b5-f71fe8ff0bc8,ba7fa225-adf9-46cc-baaf-05f8781cf203,ef19f58e-4e30-4481-84a4-99cb104e39d8 | ,,, | https://web.fulcrumapp.com/photos/view?photos=113fedfe-64da-47f1-a703-bf291897321c%2C69e2bb58-b3ea-4116-a6b5-f71fe8ff0bc8%2Cba7fa225-adf9-46cc-baaf-05f8781cf203%2Cef19f58e-4e30-4481-84a4-99cb104e39d8 | Steel | Centre Support | Corrosion-Heavy,Corrosion-Surface
10b00a04-a5bb-4549-94d6-28bd7c807766 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 03:00:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 692 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27046 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 692, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 corrosion up to 50% coverage. Channel anchor bolts have Level 2 Medium Corrosion. One bolt is loose. |  | Steel channel support bracket has Level 3 corrosion up to 50% coverage. Channel anchor bolts have Level 2 Medium Corrosion. One bolt is loose. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Bolt has medium level corrosion. | no |  |  |  |  | cf16dc11-5f19-4827-8903-95b3a5ee7e89 |  | https://web.fulcrumapp.com/photos/view?photos=cf16dc11-5f19-4827-8903-95b3a5ee7e89 | Steel | Channel Bracket,Channel Bracket-Bolt | Loose
b01e5395-c00c-49eb-8068-810b0efca49c | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 | -20.3738 | 118.6342 | POINT (118.6342359 -20.3738022) | 2025-05-27 20:13:18 AEST | 2025-06-01 02:10:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 693 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27047 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 693,11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has Leak - Inactive at time of inspection. |  | Concrete shell segment has Leak - Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | - | Working at Heights | Condition Monitoring Competent Supervisor | SS |  | Leak is coming from mounting recess. Slow, but active, with salts building. Adjacent grout injection port has been patched. | yes |  |  |  |  | aa97c9a7-0155-457c-9f82-41775abc4f7d,7f5fd9b4-6ac7-413f-b02e-5453ddd9ff46 | , | https://web.fulcrumapp.com/photos/view?photos=aa97c9a7-0155-457c-9f82-41775abc4f7d%2C7f5fd9b4-6ac7-413f-b02e-5453ddd9ff46 | Concrete | Grout Hole | Leaks
4d9eb393-e16d-4652-908b-0ecc0179c963 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:56:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 694 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27663 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 694, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion |  | Steel channel support bracket has Level 2 - Minor Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Minor corrosion is still evident | no |  |  |  |  | a9797d99-468b-4ec5-a5d9-5944fdcc31ba,002c02e1-f53e-47d6-b418-53100296819d | , | https://web.fulcrumapp.com/photos/view?photos=a9797d99-468b-4ec5-a5d9-5944fdcc31ba%2C002c02e1-f53e-47d6-b418-53100296819d | Steel | Channel Bracket | Corrosion-Surface
1c02ed0f-962e-484a-a10f-9468b6b58318 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:22:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 694 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27048 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing |  |  |  | 4 | [8 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 694, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have level 3 corrosion. Steel channel support bracket has Level 2 corrosion up to 25% coverage. |  | Channel anchor bolts have level 3 corrosion. Steel channel support bracket has Level 2 corrosion up to 25% coverage. FLAG | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | This bracket appears to be placed over a slow leaking grout injection port. No liquid is noted, but salts are showing, at the same location as the grout port would be. The bracket is degrading at an accelerated rate. This should be addressed. Lowest bolt is almost completely gone, and upper ones are showing section loss, as is the bracket at penetrations. | yes |  |  |  |  | 666d451c-fb05-4204-aa70-e66de1ca9f04,7a4310f8-ab09-4be0-a8a8-969a369eac31,ce50875e-2bd8-4bd3-b6c3-49cef7e6be1b,82d2d652-32e4-4d93-bb26-5b664827958b,13cca6da-ca31-4509-ac38-d1ad1f6e297c,699705d9-17b4-482c-b284-56029510c082,f6dc1041-a3c5-4e69-b8a4-6810dc9e97ac,14711c59-de97-4b03-95e6-745c68752df2,9f072eec-bbfb-4edc-9a17-abfd71805efa | ,,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=666d451c-fb05-4204-aa70-e66de1ca9f04%2C7a4310f8-ab09-4be0-a8a8-969a369eac31%2Cce50875e-2bd8-4bd3-b6c3-49cef7e6be1b%2C82d2d652-32e4-4d93-bb26-5b664827958b%2C13cca6da-ca31-4509-ac38-d1ad1f6e297c%2C699705d9-17b4-482c-b284-56029510c082%2Cf6dc1041-a3c5-4e69-b8a4-6810dc9e97ac%2C14711c59-de97-4b03-95e6-745c68752df2%2C9f072eec-bbfb-4edc-9a17-abfd71805efa | Steel | Channel Bracket,Channel Bracket-Bolt,Grout Hole | Corrosion-Heavy,Leaks
f4cac28f-697d-4293-a9f0-18022f84f4ee | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:53:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 694 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27361 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 694, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has one missing bolt. |  | Steel channel support bracket has one missing bolt. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Steelwork Remediation Crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | Bracket bolt is still missing. | no |  |  |  |  | c1d396c2-ca5a-4c5f-bc3d-8e386f52cc82 |  | https://web.fulcrumapp.com/photos/view?photos=c1d396c2-ca5a-4c5f-bc3d-8e386f52cc82 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
001a81d4-afbe-427b-9f13-dc50d4f885f4 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 01:56:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 695 | 11 | Grout Injection Hole | Grout Injection Hole |  | 68723 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 695, 11 o'clock. Concrete Shell Segment - Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | production loss | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | Working at Heights | Standard Repair Detail Competent Supervisor |  |  | Leak still appears to be active | no |  |  |  |  | b2de3abf-8c34-41ca-83d1-ab5e0ccef930,4db7c7dc-2fa8-4e8f-8c41-1c3a04fedffd,7de3b48d-492f-4fe6-ac6e-f2b2adfc7b37 | ,, | https://web.fulcrumapp.com/photos/view?photos=b2de3abf-8c34-41ca-83d1-ab5e0ccef930%2C4db7c7dc-2fa8-4e8f-8c41-1c3a04fedffd%2C7de3b48d-492f-4fe6-ac6e-f2b2adfc7b37 | Concrete | Grout Hole | Leaks |  | Not reinforcement
b6c2e925-7f4b-453c-82e8-bdf8475a2698 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 695 | 8 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84648 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 695, 8 O'Clock, Segmental Concrete | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 100mm x 100mm. |  | Concrete shell segment has drummy concrete over an area of 100mm x 100mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete |  | Drummy
db8a72e6-6b00-4a74-96d9-108d2ccb57fa | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 698 | 2 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96842 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 698, 2 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint,Reinforcement | Drummy
4e7b1971-947a-457c-b63a-d891104a5c47 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:30:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 698 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 96843 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Unknown | Unknown |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 698, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | HM |  | Drumminess is evident | no |  |  |  |  | 099e31a2-1654-46f4-ad2e-fa7c4d098a3f |  | https://web.fulcrumapp.com/photos/view?photos=099e31a2-1654-46f4-ad2e-fa7c4d098a3f | Concrete | Circular Joint | Drummy |  | Not reinforcement
90b2250d-61a0-4ca8-9047-46c37dd2edf8 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 698 | 9 | Grout Injection Hole | Grout Injection Hole |  | 96841 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 698, 9 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and danger to personnel. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Grout Hole | Leaks
a1c32503-bfb9-4a4b-b5d5-6e1773ebcff1 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:18:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 700 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84649 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 700, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is evident. | no |  |  |  |  | b0684d46-ba16-43f4-8a78-fcd9cb8caad1 |  | https://web.fulcrumapp.com/photos/view?photos=b0684d46-ba16-43f4-8a78-fcd9cb8caad1 | Concrete | Circular Joint | Drummy |  | Circular Joint not Radial Joint
a2519501-1e05-4d11-b907-e17cee3d827f | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 01:44:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 702 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27050 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 702, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Minor corrosion | no |  |  |  |  | b3eaab78-a251-410d-b1e2-8613768d3cd9,40d37f11-8c3b-4eb8-b466-35609b2936fb,f181b647-9b47-4326-95fe-0ee1edb0ee22,866d1659-ec8e-438b-b150-fa5f4bdd99d5 | ,,, | https://web.fulcrumapp.com/photos/view?photos=b3eaab78-a251-410d-b1e2-8613768d3cd9%2C40d37f11-8c3b-4eb8-b466-35609b2936fb%2Cf181b647-9b47-4326-95fe-0ee1edb0ee22%2C866d1659-ec8e-438b-b150-fa5f4bdd99d5 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
b77bfd08-e39d-432d-b15f-f43c88914f63 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 02:23:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 702 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 96844 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 702, 10 to 2 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Concrete shell segment offset by 10mm at radial joint. Requires close monitoring. |  | Concrete shell segment offset by 10mm at radial joint. Requires close monitoring. FLAG | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Impact to durability of other components | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS Inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | The displacement was measured at 15mm at the position marked. Suggest close examination of previous images to compare, and discussion to determine next steps. If this additional movement is confirmed, this is a serious defect for the tunnel. | yes |  |  |  |  | 76f753af-93ba-4802-928e-35a80e266fa0,420a380d-404d-4ba3-9783-bc5614bbef1e,998089ba-b3bc-496a-ac54-3fc7a46a7046,a145b4f9-d9ed-43ea-ae24-b920fb7637b3,94b3d545-c523-4d33-890f-e4689481aba6,3515dc8d-b77b-48a2-ae6e-80e2157e4e6e | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=76f753af-93ba-4802-928e-35a80e266fa0%2C420a380d-404d-4ba3-9783-bc5614bbef1e%2C998089ba-b3bc-496a-ac54-3fc7a46a7046%2Ca145b4f9-d9ed-43ea-ae24-b920fb7637b3%2C94b3d545-c523-4d33-890f-e4689481aba6%2C3515dc8d-b77b-48a2-ae6e-80e2157e4e6e | Concrete | Circular Connection,Circular Joint | Displacement |  | Circular Connection and Circular Joint
5a6f56e7-bee6-42ff-bdc9-bca0c3e50a21 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-06-01 01:30:23 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 702 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27051 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Ring 702, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Minor corrosion with some coating failure | no |  |  |  |  | a9760156-a3ac-475a-bcb4-2f69cff9c234,c5c48ac4-22ef-44bc-bd47-0cdb4aecb652,869fc4e1-97a5-4577-8642-2d3da86c3eeb | ,, | https://web.fulcrumapp.com/photos/view?photos=a9760156-a3ac-475a-bcb4-2f69cff9c234%2Cc5c48ac4-22ef-44bc-bd47-0cdb4aecb652%2C869fc4e1-97a5-4577-8642-2d3da86c3eeb | Steel | Channel Bracket,Channel Bracket-Bolt | Coating Failure,Corrosion-Surface
47a5ebbe-e9d0-4111-8ebb-7c8347f8fdff | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:18 AEST | 2025-05-27 20:13:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 702 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 68725 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44540.2967 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 702, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have level 2 corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 25% coverage. Channel anchor bolts have level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [15 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
45b8660c-5c98-4b19-be90-7e3a4fd28d3f | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-01 02:08:58 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 702 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 68724 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 702, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 150mm x 150mm. |  | Concrete shell segment has drummy concrete over an area of 150mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is not evident. Previous patch is sufficient. | yes |  |  |  |  | 74a87ab0-364e-4a41-ae44-330cd89cb307,08c76e88-6ff4-493d-a879-3f9240c8966b | , | https://web.fulcrumapp.com/photos/view?photos=74a87ab0-364e-4a41-ae44-330cd89cb307%2C08c76e88-6ff4-493d-a879-3f9240c8966b | Concrete |  | Drummy |  | Not reinforcement
0395edef-db14-4dc4-a3b2-5118cb3d7ead | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-01 02:01:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 704 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68726 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 704, 4 o'clock. Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints at two locations of size 400mm x 250mm and 350mm x 300mm (both sides of the walkway support). |  | Grout Delamination / debonding at circle segment bolted joints at two locations of size 400mm x 250mm and 350mm x 300mm (both sides of the walkway support). | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | HM |  | Drumminess is not evident. Previous patch is sufficient. | yes |  |  |  |  | 1ee5f9d1-0081-4dd7-8a61-8720d170d0ae,1a98f2ec-56c2-45a1-a4af-9293ace93120 | , | https://web.fulcrumapp.com/photos/view?photos=1ee5f9d1-0081-4dd7-8a61-8720d170d0ae%2C1a98f2ec-56c2-45a1-a4af-9293ace93120 | Concrete | Circular Joint | Drummy |  | Not walkway support
57539fcb-c69e-41b6-96cd-fe76f39e1152 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 23:50:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 706 | 10 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84650 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 706, 10 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Drumminess still evident. Also noted what could be an epoxy or PU injection port close by. | no |  |  |  |  | 085bd0aa-9105-4d77-b451-b073ab7ccfb5,e843b1ae-acbb-46ab-8146-4119db45e36a | , | https://web.fulcrumapp.com/photos/view?photos=085bd0aa-9105-4d77-b451-b073ab7ccfb5%2Ce843b1ae-acbb-46ab-8146-4119db45e36a | Concrete | Circular Joint | Drummy |  | Not grout hole
47ec16c5-9b08-443f-9480-e48dac6e4b50 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 23:47:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 706 | 12 | Channel Anchor Bolts | Channel Anchor Bolts |  | 84651 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 706, 12 O'Clock, Channel Anchor Bolts | Rupture | Rupture |  | Two missing anchor bolts at channel support bracket. |  | Two missing anchor bolts at channel support bracket. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | Replace missing anchor bolts as per approved design drawing. | GTS Specification. Concrete remediation crew. | No | Off-Line | Yes | Walkway | - | Replace Component Competent Supervisor |  |  | Suggest this might not be a defect, as filling every possible bolt hole may not be necessary. | no |  |  |  |  | 6c2d179f-7b68-4b0e-83cc-33315700e206,1f60cda8-4a1b-470d-b520-f0f7f569dc3b | , | https://web.fulcrumapp.com/photos/view?photos=6c2d179f-7b68-4b0e-83cc-33315700e206%2C1f60cda8-4a1b-470d-b520-f0f7f569dc3b | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
a9940005-e4bc-4bdc-bb01-8bbcbfadad1f | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-01 01:47:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 706 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 68727 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 706, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 150mm x 150mm. |  | Concrete shell segment has drummy concrete over an area of 150mm x 150mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | Excavation | Standard Repair Detail Competent Supervisor | HM |  | Drumminess is not evident. Previous patch is sufficient. | yes |  |  |  |  | 2cf42c6b-1809-473d-8007-e6078dacaa28,d3f349d3-42a7-4227-b841-1f31a6d894ff | , | https://web.fulcrumapp.com/photos/view?photos=2cf42c6b-1809-473d-8007-e6078dacaa28%2Cd3f349d3-42a7-4227-b841-1f31a6d894ff | Concrete | Circular Joint | Drummy |  | Circular Joint Not reinforcement
d71b7d60-d26e-4af6-868c-3d1742bb2558 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:20:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 709 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27664 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 709, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding, Walkway | Working at Heights, Confined Space, Hot Work, Excavation | Standard Repair Detail Competent Supervisor |  |  | Leak appears to be inactive at time of this inspection | yes |  |  |  |  | 7a26bfb2-b685-4159-9410-2d1f7c6c669f,0d1d3898-3207-4f37-b8b2-0124f565e91a,cc829166-5242-4569-b029-4f5eb6fbfd22 | ,, | https://web.fulcrumapp.com/photos/view?photos=7a26bfb2-b685-4159-9410-2d1f7c6c669f%2C0d1d3898-3207-4f37-b8b2-0124f565e91a%2Ccc829166-5242-4569-b029-4f5eb6fbfd22 | Concrete | Grout Hole | Leaks |  | Not reinforcement
4cd2b192-92ed-4180-af16-7d39201c7366 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:21:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 710 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27052 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 710, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Same condition | no |  |  |  |  | 43bf242b-f4ae-4846-b66c-833a1c77764a,673f8df7-9363-4e57-b592-ec6ba13e9ce4,86c9f3d3-5d8f-4804-a45f-dd3a688e2093,6313050a-b0c1-47ae-9af7-a8d44c73f606,cef43ac6-5d3a-4b64-bc59-9140d98807d0 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=43bf242b-f4ae-4846-b66c-833a1c77764a%2C673f8df7-9363-4e57-b592-ec6ba13e9ce4%2C86c9f3d3-5d8f-4804-a45f-dd3a688e2093%2C6313050a-b0c1-47ae-9af7-a8d44c73f606%2Ccef43ac6-5d3a-4b64-bc59-9140d98807d0 | Steel | Channel Bracket | Corrosion-Surface
b625e293-6ee5-45aa-a593-abc62327d1d9 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 23:36:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 710 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84652 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44873.5578 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 710, 11 to 1 O'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 1 Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 10% coverage. |  | Channel anchor bolts have Level 1 Low Corrosion. Steel channel support bracket has Level 2 Minor Corrosion up to 10% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Mild corrosion, some coating failure | no |  |  |  |  | 927aec69-cff1-4479-a4aa-24d9e68929fc,d33c8e56-0bf6-457e-87cf-9529dfde94c3 | , | https://web.fulcrumapp.com/photos/view?photos=927aec69-cff1-4479-a4aa-24d9e68929fc%2Cd33c8e56-0bf6-457e-87cf-9529dfde94c3 | Steel | Channel Bracket,Channel Bracket-Bolt | Coating Failure,Corrosion-Surface
97b418d4-9509-4c9f-9517-ec38bb554c67 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 23:32:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 715 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84659 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 715, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 350mm x 250mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 350mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Drumminess still evident | no |  |  |  |  | f036b329-483a-4946-a4a5-970ea592a3d4,422cf7d1-4ccd-4ffa-91c4-f552d440ab10 | , | https://web.fulcrumapp.com/photos/view?photos=f036b329-483a-4946-a4a5-970ea592a3d4%2C422cf7d1-4ccd-4ffa-91c4-f552d440ab10 | Concrete | Radial Joint | Drummy
51b54fb8-0e0d-4a81-8ded-2a113aafbece | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 11 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 23:31:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 716 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84660 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 716, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is not evident. Previous patch is sufficient. | yes |  |  |  |  | 91c1771f-3a52-41c2-ad58-4f55810b6d6a,13109f4c-1c19-4a3f-baa3-bfb1e393bd6f | , | https://web.fulcrumapp.com/photos/view?photos=91c1771f-3a52-41c2-ad58-4f55810b6d6a%2C13109f4c-1c19-4a3f-baa3-bfb1e393bd6f | Concrete | Circular Joint | Drummy
a22204c2-b687-47a8-ac32-84c35296533e | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 4 |  |  |  | 2025-06-01 01:46:40 AEST | 2025-06-01 01:51:10 AEST | 30011704-user5@smec.com | james.stone@smec.com | 700 | 12 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [17 empty] | 3 | [14 empty] | Pipe support bracket fixing | [5 empty] | Fixing has come loose | [18 empty] | SS |  | Inadequate adhesion | [5 empty] | c00aab5e-e444-4df2-b88d-e37718fa2119,0567627c-be5e-4835-b5d0-5ff7556c0d56 | , | https://web.fulcrumapp.com/photos/view?photos=c00aab5e-e444-4df2-b88d-e37718fa2119%2C0567627c-be5e-4835-b5d0-5ff7556c0d56 | Concrete | Misc (Pipes/Cable Tray/etc) | Loose
65bf342d-e226-4a98-80fb-3950ef0bed21 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 6 |  |  |  | 2025-05-31 23:09:46 AEST | 2025-05-31 23:11:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | 720 | 4 |  | Steel Channel Bracket | [32 empty] | Cable tray support bracket |  |  |  |  | Class 3 - Medium corrosion | [19 empty] | HM | [7 empty] | a800cfd1-750d-45fa-8108-93cc0cc5aecf |  | https://web.fulcrumapp.com/photos/view?photos=a800cfd1-750d-45fa-8108-93cc0cc5aecf | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc)
1b999c1c-1f7a-41c6-bc4f-6f1282b527e8 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 6 |  |  |  | 2025-05-31 23:13:24 AEST | 2025-05-31 23:15:25 AEST | 30011704-user5@smec.com | james.stone@smec.com | 718 | 2 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete shell | [5 empty] | Spalled concrete | [18 empty] | HM | [7 empty] | 4f9e9cc8-6d4f-4dfa-89d4-9b65f0a30705,1a867ebe-b83c-4f19-8b9a-b081c3c4eb7b | , | https://web.fulcrumapp.com/photos/view?photos=4f9e9cc8-6d4f-4dfa-89d4-9b65f0a30705%2C1a867ebe-b83c-4f19-8b9a-b081c3c4eb7b | Concrete |  | Surface Damage
3a789719-665b-4ab7-8a82-d5bee1c60742 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 6 |  |  |  | 2025-05-31 23:31:38 AEST | 2025-05-31 23:35:07 AEST | 30011704-user5@smec.com | james.stone@smec.com | 716 | 3 |  | Channel Anchor Bolts | [32 empty] | Cable tray support bracket | [5 empty] | Advanced corrosion of the bolt. | [18 empty] | HM | [7 empty] | a0523691-b8e5-46ab-91b6-4e152d2d80b8,68382061-afb8-43af-ab93-fc9cafc612b9,dc5d7019-8859-4cb8-9667-3a21aa33c331 | ,, | https://web.fulcrumapp.com/photos/view?photos=a0523691-b8e5-46ab-91b6-4e152d2d80b8%2C68382061-afb8-43af-ab93-fc9cafc612b9%2Cdc5d7019-8859-4cb8-9667-3a21aa33c331 | Steel | Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy
5465c3b9-a623-4d6d-b337-d5339b084388 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 6 |  |  |  | 2025-05-31 23:40:57 AEST | 2025-05-31 23:42:39 AEST | 30011704-user5@smec.com | james.stone@smec.com | 714 | 4 |  | Channel Anchor Bolts | [32 empty] | Cable tray support bracket | [5 empty] | Advanced corrosion of the bolt | [18 empty] | HM | [7 empty] | d2b9310a-1a54-45d4-af3d-f5def18fd269 |  | https://web.fulcrumapp.com/photos/view?photos=d2b9310a-1a54-45d4-af3d-f5def18fd269 | Steel | Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Corrosion-Surface |  | Corrossion Surface not heavy
8ab669ee-6cff-4a74-ae44-29198f1ad468 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 6 |  |  |  | 2025-05-31 23:44:48 AEST | 2025-05-31 23:47:58 AEST | 30011704-user5@smec.com | james.stone@smec.com | 712 | 4 |  | Channel Anchor Bolts | [32 empty] | Cable tray support bracket | [5 empty] | Channel anchor bolt has come loose. Requires to be tightened | [18 empty] | HM | [7 empty] | 621c74f4-9dca-4bee-b733-da64ece97834 |  | https://web.fulcrumapp.com/photos/view?photos=621c74f4-9dca-4bee-b733-da64ece97834 | Steel | Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Loose |  | Duplicate - Remove
65f2cfda-13f9-47d3-9064-39a16515ec7e | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 01:27:13 AEST | 2025-06-01 01:28:39 AEST | 30011704-user5@smec.com | james.stone@smec.com | 710 | 4 |  | Steel Channel Bracket | [32 empty] | Cable tray support bracket |  |  |  |  | Class 3 - Medium corrosion | [27 empty] | 425214d1-6ac3-480b-b114-77f228694f32 |  | https://web.fulcrumapp.com/photos/view?photos=425214d1-6ac3-480b-b114-77f228694f32 | Steel | Channel Bracket |  |  | only steel channel
22d2d8de-b0d6-4498-a585-e188a6b59ab4 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 01:35:42 AEST | 2025-06-01 01:38:05 AEST | 30011704-user5@smec.com | james.stone@smec.com | 708 | 4 |  | Steel Channel Bracket | [32 empty] | Cable support bracket | [5 empty] | Advanced corrosion in the bracket at 4 o clock | [18 empty] | HM | [7 empty] | 714ff59f-789c-484a-8f17-a07f3b4f3e11 |  | https://web.fulcrumapp.com/photos/view?photos=714ff59f-789c-484a-8f17-a07f3b4f3e11 | Steel | Channel Bracket | Corrosion-Heavy
47f285f6-1db4-459b-b4e4-7ef10d4ea1b3 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 01:39:28 AEST | 2025-06-01 01:41:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 708 | 4 |  | Channel Anchor Bolts | [32 empty] | Cable support bracket bolt | [5 empty] | Advanced corrosion of the bolt | [18 empty] | HM | [7 empty] | 51fdf27f-1599-4890-bdc2-bf986fe67873,016a1b54-993d-4b66-ad66-3d2165e7c016 | , | https://web.fulcrumapp.com/photos/view?photos=51fdf27f-1599-4890-bdc2-bf986fe67873%2C016a1b54-993d-4b66-ad66-3d2165e7c016 | Steel | Channel Bracket-Bolt | Corrosion-Heavy
20e7ddb5-cb37-4af3-bff0-0375866b9336 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 01:50:15 AEST | 2025-06-01 02:23:30 AEST | 30011704-user5@smec.com | james.stone@smec.com | 705 | 2 |  | Segment Bolted Joint (Circle Joint) | [32 empty] | CONCRETE SHELL | [5 empty] | It appears to have an offset with positioning of the rings next to each other (ring 705 & 706) | [18 empty] | HM | [7 empty] | 324900be-03ee-40eb-abf4-767e8c9c5fa9 |  | https://web.fulcrumapp.com/photos/view?photos=324900be-03ee-40eb-abf4-767e8c9c5fa9 | Concrete | Circular Joint | Displacement
3c934abe-ff79-4d8d-8f54-f0b162e83b15 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 02:15:17 AEST | 2025-06-01 02:17:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 701 | 4 |  | Segment Bolted Joint (Circle Joint) | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | HM | [7 empty] | 23dd5349-57da-4310-8281-da2f09c04245,ca8ef21e-6467-43f7-9dbd-ea41e134fc4b | , | https://web.fulcrumapp.com/photos/view?photos=23dd5349-57da-4310-8281-da2f09c04245%2Cca8ef21e-6467-43f7-9dbd-ea41e134fc4b | Concrete | Circular Joint,Circular Connection | Drummy |  | circular connection as well
f6eee189-ac0a-4988-a255-d2559a932a3c | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 02:32:45 AEST | 2025-06-01 02:35:32 AEST | 30011704-user5@smec.com | james.stone@smec.com | 697 | 4 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | HM | [7 empty] | e3986793-1ed8-4d0e-b46c-d4454d6a33b5 |  | https://web.fulcrumapp.com/photos/view?photos=e3986793-1ed8-4d0e-b46c-d4454d6a33b5 | Concrete | Circular Joint | Drummy
6400617b-8f1c-4e11-8156-1c6c041d8fa6 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 02:35:47 AEST | 2025-06-01 02:36:48 AEST | 30011704-user5@smec.com | james.stone@smec.com | 698 | 3 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | HM | [7 empty] | 91181a4b-2fa9-431a-aecb-72ca8250774e |  | https://web.fulcrumapp.com/photos/view?photos=91181a4b-2fa9-431a-aecb-72ca8250774e | Concrete | Circular Joint | Drummy
7850fe1a-0ac7-49f8-90fe-a816f0c4fbb5 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 02:39:50 AEST | 2025-06-01 02:41:33 AEST | 30011704-user5@smec.com | james.stone@smec.com | 696 | 4 |  | Channel Anchor Bolts | [32 empty] | Cable tray support bracket |  |  |  |  | Class 3 - Medium corrosion | [19 empty] | HM | [7 empty] | b1c00218-9d42-4d6f-9866-2d3a3939c55d |  | https://web.fulcrumapp.com/photos/view?photos=b1c00218-9d42-4d6f-9866-2d3a3939c55d | Steel | Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc)
00e83dc3-7cea-4a26-bc34-58e822ff3522 | f7d03050-0fd5-44cb-af31-a3a632990490 | f7d03050-0fd5-44cb-af31-a3a632990490 | 5 |  |  |  | 2025-06-01 02:46:49 AEST | 2025-06-01 02:47:43 AEST | 30011704-user5@smec.com | james.stone@smec.com | 695 | 4 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | HM | [7 empty] | ebecc3bf-8014-47ea-a3b1-9ffe5eca0363 |  | https://web.fulcrumapp.com/photos/view?photos=ebecc3bf-8014-47ea-a3b1-9ffe5eca0363 | Concrete | Circular Joint | Drummy
ae8328fc-53f8-44fe-a538-8b7ea2b39090 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 23:28:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 722 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 27053 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 722, 11 to 12 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 - Surface Corrosion up to 5% coverage. Channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 3 - Surface Corrosion up to 5% coverage. Channel anchor bolts have Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SAS |  | Corrosion is advancing. There may be a slowly leaking grout port behind the bracket, as the corrosion seems to be coming from the back. There are some yellow deposits, most likely salt, although could be sealant product. This corrosion is a concern. | no |  |  |  |  | 3194f536-13f5-44df-96ab-90e650c0ec22,4ae5e3b1-4b5d-4766-bf54-22b889d1d999,fc643df2-d2fa-470a-a328-2fdcff321335,b15e2a19-f4bc-4791-be18-62a7ee9d6bc1 | ,,, | https://web.fulcrumapp.com/photos/view?photos=3194f536-13f5-44df-96ab-90e650c0ec22%2C4ae5e3b1-4b5d-4766-bf54-22b889d1d999%2Cfc643df2-d2fa-470a-a328-2fdcff321335%2Cb15e2a19-f4bc-4791-be18-62a7ee9d6bc1 | Steel | Channel Bracket,Channel Bracket-Bolt,Grout Hole | Corrosion-Surface,Leaks
4ccea2e3-12e4-415e-b2e0-0505e94f132e | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 22:59:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 724 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27665 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 724, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 5% coverage. Channel anchor bolts have Level 2 Medium Low Corrosion. |  | Steel channel support bracket has Level 2 Corrosion up to 5% coverage. Channel anchor bolts have Level 2 Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Corrosion is still evident. | no |  |  |  |  | 4c68f7d3-999d-4949-a70a-bc401a795d8a,56e30af1-c4b2-47be-bb9c-84f0d4b8e134 | , | https://web.fulcrumapp.com/photos/view?photos=4c68f7d3-999d-4949-a70a-bc401a795d8a%2C56e30af1-c4b2-47be-bb9c-84f0d4b8e134 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
f9211272-5e4c-4a7c-9b2c-2ed6403d4c4a | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 22:57:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 724 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27054 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 724,3 o'clock. Concrete Shell Segment. |  |  |  | Concrete shell segment has section broken away at bolted connection penetration. |  | Concrete shell segment has section broken away at bolted connection penetration. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Broken concrete shell segment is still not repaired | no |  |  |  |  | 14eda884-896c-47c9-b251-161af45b958f,05988443-6e0f-4777-a4c8-0d6b689b6383 | , | https://web.fulcrumapp.com/photos/view?photos=14eda884-896c-47c9-b251-161af45b958f%2C05988443-6e0f-4777-a4c8-0d6b689b6383 | Concrete | Channel Bracket |  |  | Channel Bracket
c8e7d229-0f21-443b-82bb-0a2160fabad9 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 23:13:45 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 726 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84661 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44873.7234 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 726, 11 to 12 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 5% coverage. |  | Steel channel support bracket has Level 2 Corrosion up to 5% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Corrosion is mild. Some minor coating failure | no |  |  |  |  | b5b8888d-48e9-4aea-a12d-581481743bf5,5ca3a49f-9407-432e-93e3-ccaa913f96c4,49711bd1-babb-4733-af07-2508951a2064 | ,, | https://web.fulcrumapp.com/photos/view?photos=b5b8888d-48e9-4aea-a12d-581481743bf5%2C5ca3a49f-9407-432e-93e3-ccaa913f96c4%2C49711bd1-babb-4733-af07-2508951a2064 | Steel | Channel Bracket | Coating Failure
30119814-72c9-4cf4-aa48-a9edd7bf5584 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 22:48:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 726 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 96847 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion ATM | Localised Corrosion ATM |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 726, 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Steel channel support has Level 3 Corrosion and missing bolts. |  | Steel channel support has Level 3 Corrosion and missing bolts. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | - | Not Specified | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all repair affected areas, corroded areas. 3. Replace missing anchor bolt. | Steelwork Remediation Crew. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor |  |  | Advanced corrosion still present. | no |  |  |  |  | 8c8070d0-9ed4-4ca8-85f6-eab0953a11c8,bbe322f2-a5e5-48a1-83fd-a640d809c61c | , | https://web.fulcrumapp.com/photos/view?photos=8c8070d0-9ed4-4ca8-85f6-eab0953a11c8%2Cbbe322f2-a5e5-48a1-83fd-a640d809c61c | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Missing
fc639e3a-7f45-456c-ba83-3eab8043cdd2 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 22:45:16 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 728 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27667 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 728, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 Major Corrosion. |  | Steel channel support bracket has Level 3 Major Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Advanced corrosion is still present. | no |  |  |  |  | 9aecae11-91de-423d-8a19-0c3409c72509,5501adc0-86a7-4dde-94cf-de5fdf7ecbd3 | , | https://web.fulcrumapp.com/photos/view?photos=9aecae11-91de-423d-8a19-0c3409c72509%2C5501adc0-86a7-4dde-94cf-de5fdf7ecbd3 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy
0dfaba7c-3aaf-4331-8ef3-b879566cedac | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 23:11:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 728 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27055 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 728,11 o'clock. Concrete Shell Segment - Grout Injection Hole. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. Nozzle has been broken off from grout hole. |  | Grout injection hole has Leak Active at time of inspection. Nozzle has been broken off from grout hole. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Very Rare Likelihood of failure, resulting in a Priority 4. | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor |  |  | Grout is being pushed back out in a cylinder by water/earth pressure. This should be addressed as a priority. | yes |  |  |  |  | f48563cc-d2e9-4b61-9f63-59661682f969,54d7e00f-34a4-4c20-a7f3-e32f0ded50bd,52de78ae-6c4a-4dae-aaca-6784e16fc876 | ,, | https://web.fulcrumapp.com/photos/view?photos=f48563cc-d2e9-4b61-9f63-59661682f969%2C54d7e00f-34a4-4c20-a7f3-e32f0ded50bd%2C52de78ae-6c4a-4dae-aaca-6784e16fc876 | Concrete | Grout Hole | Leaks
58a4afce-be26-40aa-b310-b46201abe088 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 19:13:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 732 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84662 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 732, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no | [7 empty] | Concrete | Radial Joint | Drummy
a211b59b-3b22-48e6-bee6-9e4636921d49 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 19:15:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 736 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 84663 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 736, 12 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 400mm x 900mm. |  | Concrete shell segment has drummy concrete over an area of 400mm x 900mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), downgraded to P3 and monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | No change | no |  |  |  |  | 46fc0466-a464-4001-861f-f6095d53607e,3d057d38-0bb5-4af8-9de9-c72abd98d129 | , | https://web.fulcrumapp.com/photos/view?photos=46fc0466-a464-4001-861f-f6095d53607e%2C3d057d38-0bb5-4af8-9de9-c72abd98d129 | Concrete | Grout Hole | Drummy |  | Grout Hole
16baceb2-62b7-4ec0-86ca-7417864b72aa | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 737 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27056 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | [13 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 737,4 O'Clock,Concrete Element,Leak found Dry in 2017 |  |  |  | Leak. |  | Leak. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [15 empty] | Concrete |  | Leaks
d12b0f09-a115-4fe4-a9cc-ed2fa34b022b | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 19:12:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 738 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27057 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 738, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 - Major Corrosion Two channel anchor bolts have Level 5 corrosion. |  | Steel channel support bracket has Level 4 - Major Corrosion Two channel anchor bolts have Level 5 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace severely corroded anchor bolts. Alternatively, repair anchor bolts as per BHP standard drawing 000-S-12598. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | Working at Heights | Replace Component Competent Supervisor |  |  | Major corrosion on 4 anchor and steel channel | yes |  |  |  |  | ef50bda2-c727-423f-b645-27511dcd5d4e,8303b134-6f85-403d-a114-6161b14dcfc0,ee9eb6a1-0640-45e4-a8f6-c4ff949563f8,80ace5fa-b1ce-4b59-9f8f-65a17d101ad0,31bd7861-3eea-4cee-9cc6-8d91ea1fbb0f,a90b0ac2-14b6-4dc8-83f3-dd50d6fd0fe7,ab717c59-6c26-42df-935d-6aec7fd0b06c,064b9581-87be-4a29-90a4-502fee1961c5 | ,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=ef50bda2-c727-423f-b645-27511dcd5d4e%2C8303b134-6f85-403d-a114-6161b14dcfc0%2Cee9eb6a1-0640-45e4-a8f6-c4ff949563f8%2C80ace5fa-b1ce-4b59-9f8f-65a17d101ad0%2C31bd7861-3eea-4cee-9cc6-8d91ea1fbb0f%2Ca90b0ac2-14b6-4dc8-83f3-dd50d6fd0fe7%2Cab717c59-6c26-42df-935d-6aec7fd0b06c%2C064b9581-87be-4a29-90a4-502fee1961c5 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
bb815d74-8aa1-434f-b5b2-584e702dbde4 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 738 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68728 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 738, 12 o'clock. Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints and drummy concrete over an area of 300mm x 1200mm. |  | Grout Delamination / debonding at circle segment bolted joints and drummy concrete over an area of 300mm x 1200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), downgraded to P3 and monitor |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Scaffolding | Working at Heights | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
d9775d1c-72e3-44d6-9409-a6ae468669a5 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 738 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84665 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 738, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
c7e0f4f1-bcc7-4730-a9df-0c2cf329cd7c | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 738 | 8 | Ring (Segmental Concrete) - Damage Affecting Multiple Rings |  | Ring (Segmental Concrete) - Damage Affecting Multiple Rings | 84664 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  |  |  |  | Severity Level 5. >= US$2 billion |  | Severity Level 5. >= US$2 billion | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 738, 8 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to progressive failure of a large section of the tunnel. |  | Failure of shell segment in compression or tension leading to progressive failure of a large section of the tunnel. | Concrete shell segment has drummy concrete over an area of 600mm x 400mm. |  | Concrete shell segment has drummy concrete over an area of 600mm x 400mm. | Multiple ring collapse, tunnel flooded and unserviceable. Critical water pipe is cut, leading to loss of production for entire Finucane Island. |  | Multiple ring collapse, tunnel flooded and unserviceable. Critical water pipe is cut, leading to loss of production for entire Finucane Island. | Financial, Severity Level 5 Reason for Not Specified | - | [5 empty] | Break out loose and damaged concrete. Engineer to assess damage to reinforcement and remediation required. All areas of damaged concrete shall be replaced with high strength concrete patch repairs including embedment of galvanic Cathodic Protection (CP) anodes. Corroded reinforcement that has not been removed shall be thoroughly cleaned of all corroded material. Where corroded reinforcement has been removed it should be replaced by welding a new length of N grade reinforcement of the same diameter to the remaining undamaged reinforcing bar. Or replacing the damaged bar with a new N grade bar of the same diameter as the removed bar. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | Walkway | - | Engineering Repair Methodology Required Competent Engineer | [11 empty] | Concrete |  | Drummy
5d513759-d58b-45d6-87d1-0a416f6d0683 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-07-31 05:42:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 740 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68729 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint Radial Joint) - Ring 740, 4 o'clock. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 500mm x 200mm and 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 500mm x 200mm and 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | Previously listed under AIMS defect 30774 under incorrect AIMS quadrant. 30774 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | loss of production | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The defect has not changed from the last inspection. | no | yes |  | no |  | add4d5e3-a97f-4473-b948-86c88dd938ef |  | https://web.fulcrumapp.com/photos/view?photos=add4d5e3-a97f-4473-b948-86c88dd938ef | Concrete | Radial Joint | Drummy
9e3f61db-8eed-495c-a74f-fdd053cdff25 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-07-31 05:41:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 740 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84666 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 740, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Concrete spalling damage adjacent to circle joint. |  | Concrete spalling damage adjacent to circle joint. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | AIMS structural inspector | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | Bogdan Stanca |  | The defect has not changed from the last inspection. | no | yes |  | no |  | 35053b0c-73e5-4cf9-9200-88a57b1c7d07 |  | https://web.fulcrumapp.com/photos/view?photos=35053b0c-73e5-4cf9-9200-88a57b1c7d07 | Concrete | Circular Joint | Surface Damage
a04c9557-6c70-48c5-9603-f87cdfb3d716 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 18:56:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 741 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84667 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 741, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  |  | no | [7 empty] | Concrete | Circular Joint | Drummy
26189b80-f71b-4390-bc0d-bd68bf08d571 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 742 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68730 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Unauthorised Modifications and Repairs |  | Unauthorised Modifications and Repairs | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint (Radial Joint) - Ring 742, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Previously listed under AIMS defect 30777 under incorrect AIMS quadrant. 30777 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Radial Joint | Drummy
5eea0965-3339-4e8d-be84-e068ef1fca49 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:26:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 742 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84668 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 742, 1 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Defect is at 2 o clock. It appears the damage has advanced through initial corrosion. Affected area didn’t change. | yes |  |  |  |  | ee2fe730-a5b9-4218-ac11-2f7b0d199b53,3821e56d-498a-45f1-9659-6f0d840987c1 | , | https://web.fulcrumapp.com/photos/view?photos=ee2fe730-a5b9-4218-ac11-2f7b0d199b53%2C3821e56d-498a-45f1-9659-6f0d840987c1 | Concrete | Circular Joint | Drummy
ce08742c-0b9a-415b-84f9-a1c3a4dd93a8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 18:55:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 742 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27059 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 742, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 Corrosion up to 5% coverage. Channel anchor bolts have Level 2 Medium Low Corrosion. |  | Steel channel support bracket has Level 2 Corrosion up to 5% coverage. Channel anchor bolts have Level 2 Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Delaminated joint repair | no |  |  |  |  | 7530330f-9681-421d-8f89-630389d2b8b4,ede3479c-c6de-4aef-a81f-d9c756e3fab6,922dbe4a-94ed-4a4e-9c2b-e998ac69e0a5 | ,, | https://web.fulcrumapp.com/photos/view?photos=7530330f-9681-421d-8f89-630389d2b8b4%2Cede3479c-c6de-4aef-a81f-d9c756e3fab6%2C922dbe4a-94ed-4a4e-9c2b-e998ac69e0a5 | Steel | Channel Bracket,Channel Bracket-Bolt | Drummy
a7210721-84e7-4054-a0f0-ac9ebd441216 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 742 | 3 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84669 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 742, 3 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
93e19ad3-31b4-4ecc-8b48-d1dde2720f6d | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 19:02:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 743 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27668 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 743, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor |  |  | Chlorine attack around circular Joint | no |  |  |  |  | 6d08e553-09ad-4e44-a9cc-06b4b97a2798,9aee446a-a16c-42a4-98ea-6fc18de561ed,be40e943-cbf0-497c-b5f2-3d7e44dc52bc | ,, | https://web.fulcrumapp.com/photos/view?photos=6d08e553-09ad-4e44-a9cc-06b4b97a2798%2C9aee446a-a16c-42a4-98ea-6fc18de561ed%2Cbe40e943-cbf0-497c-b5f2-3d7e44dc52bc | Concrete | Circular Connection,Circular Joint | Leaks |  | Not reinforcement
e6ca6fa3-7ca8-4edc-9ece-2e6fe1c5eb93 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 18:50:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 745 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27669 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 745, 10 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor |  |  | Aggregates Exposed and Drummy concrete | yes |  |  |  |  | de3e0fcf-d5e1-4761-8afb-f9f644ff5c1e,7027e708-d5b6-4e29-9cdc-96e8819bd499,8742617c-3b3b-43c9-9350-773e945d5983 | ,, | https://web.fulcrumapp.com/photos/view?photos=de3e0fcf-d5e1-4761-8afb-f9f644ff5c1e%2C7027e708-d5b6-4e29-9cdc-96e8819bd499%2C8742617c-3b3b-43c9-9350-773e945d5983 | Concrete | Grout Hole | Drummy,Leaks |  | Not reinforcement
87e07114-42de-422f-ab66-2d1cddcc6205 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 19:22:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 746 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27060 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Ring 746, 11 o'clock. Steel Channel Support Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion. Channel anchor bolts have Level 2 Medium Low Corrosion |  | Steel channel support bracket has Level 2 Minor Corrosion. Channel anchor bolts have Level 2 Medium Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Channel Anchor bolt poorly Corroded | no |  |  |  |  | e9187985-aad4-4aa6-9da1-80f14fd33ca0,99484808-f670-43b0-b60b-e9c94368e2a2,c588aea4-7584-417c-a36f-257e819af5d4,9037f85c-7c37-4b61-b2ae-8f29de2af771 | ,,, | https://web.fulcrumapp.com/photos/view?photos=e9187985-aad4-4aa6-9da1-80f14fd33ca0%2C99484808-f670-43b0-b60b-e9c94368e2a2%2Cc588aea4-7584-417c-a36f-257e819af5d4%2C9037f85c-7c37-4b61-b2ae-8f29de2af771 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
312938bf-1d94-4131-9bbc-916c8da80d82 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 18:49:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 746 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27670 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 746, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 3 Medium Corrosion up to 100% coverage. |  | Steel channel support bracket has Level 3 Medium Corrosion up to 100% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Corroded bracket bolt | [5 empty] | 877e2837-ccc6-40c8-b826-03ad45dbdaea |  | https://web.fulcrumapp.com/photos/view?photos=877e2837-ccc6-40c8-b826-03ad45dbdaea | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
ddf3760c-0608-40ae-9eed-576e598e14b5 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 746 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68732 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 746, 4 o'clock. Segmented Bolted Joint (Radial) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints over an area of 350mm x 300mm. |  | Grout Delamination / debonding at radial segment bolted joints over an area of 350mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | loss of services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Radial Joint | Drummy
42f1280b-7699-44a6-a502-aebdaebb84df | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 747 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84670 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 747, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
e60331b2-83c4-4e75-9aaf-ae007fa6d6f1 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 18:45:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 748 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84671 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 748, 11 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Drummy Grout around 11 o’clock | no |  |  |  |  | c1ba218c-bc45-4cd0-b1eb-89fea792d52d,0c3fbc88-d09e-41bf-af5e-266c6c1dadb3 | , | https://web.fulcrumapp.com/photos/view?photos=c1ba218c-bc45-4cd0-b1eb-89fea792d52d%2C0c3fbc88-d09e-41bf-af5e-266c6c1dadb3 | Concrete | Middle of Panel | Drummy |  | Not circular joint. Middle of Panel
70a5bdb2-68c1-40ab-9a62-63a2a5a78e59 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 748 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68733 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 748, 4 o'clock. Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area 300mm x 250mm. Area now spalling. |  | Grout Delamination / debonding at circle segment bolted joints over an area 300mm x 250mm. Area now spalling. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy,Surface Damage
8c93a47b-28a9-4828-9b8f-7275ef610bc6 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 750 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68734 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint Circle Joint) - Ring 750, 4 o'clock. Concrete Shell Segment. Identified in 2019. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 250mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Previously listed under AIMS defect 30778 under incorrect AIMS quadrant. 30788 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
e0925006-2dc8-4b8f-aad7-297f93a53e37 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 18:35:04 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 750 | 0 | Steel Channel Bracket | Steel Channel Bracket |  | 84672 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44873.7566 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 750, 11 to 12 O'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Corrosion. |  | Channel anchor bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [15 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
9dec51eb-b5a1-4177-82a0-1e9fe123ccad | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 750 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27366 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 750, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Steelwork Remediation Crew. | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor | [11 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
d7e52f58-9cce-46c1-aeda-83ee2588a84c | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 750 | 4 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27671 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 750,4 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Missing Members |  | Missing Members | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [15 empty] | Steel | Channel Bracket-Bolt | Missing
bca7c228-6c30-41e7-85e7-de9745ba9850 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 10 |  |  |  | 2025-05-31 18:30:42 AEST | 2025-05-31 19:22:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 750 | 11 |  | Hydrophilic Joint Seal (Radial Joint) | [59 empty] | 2x Patch Repair around at Radial joint | [5 empty] | 92ee5149-0eee-4b05-bf55-e21d809f3033,c83ad7bb-9774-41e4-927d-3bf5eb169e4c,eb32a92d-5048-4ae8-9a5a-22a23e3495ea | ,, | https://web.fulcrumapp.com/photos/view?photos=92ee5149-0eee-4b05-bf55-e21d809f3033%2Cc83ad7bb-9774-41e4-927d-3bf5eb169e4c%2Ceb32a92d-5048-4ae8-9a5a-22a23e3495ea | Concrete | Radial Joint
0835d6ff-1b40-4a0e-b2b4-c6ab68526db1 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 10 |  |  |  | 2025-05-31 18:35:59 AEST | 2025-05-31 18:38:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 749 | 11 |  | Hydrophilic Joint Seal (Circle Joint) | [59 empty] | Drummy Grout around Ring Edge | [5 empty] | 3eb06cab-bbb4-4190-9a4d-06a2b507ebc9,e98ad8fb-d683-4ab3-9a31-655be11b6e92 | , | https://web.fulcrumapp.com/photos/view?photos=3eb06cab-bbb4-4190-9a4d-06a2b507ebc9%2Ce98ad8fb-d683-4ab3-9a31-655be11b6e92 | Concrete | Circular Joint | Drummy
236d0725-ee37-4799-b9c3-ec30cfaffe31 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 10 |  |  |  | 2025-05-31 18:40:37 AEST | 2025-05-31 18:42:14 AEST | 30011704-user5@smec.com | james.stone@smec.com | 749 | 12 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [17 empty] | 3 | [41 empty] | Drummy Grout around Circular Joint | [5 empty] | a7623cf3-a818-4ba3-9729-c83f4b995fca,774d75a6-c75e-4314-9464-55f5c8683f9c | , | https://web.fulcrumapp.com/photos/view?photos=a7623cf3-a818-4ba3-9729-c83f4b995fca%2C774d75a6-c75e-4314-9464-55f5c8683f9c | Concrete | Circular Connection,Circular Joint | Drummy
25aa6a0e-c411-4612-bc89-9c90a1644578 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 10 |  |  |  | 2025-05-31 19:19:19 AEST | 2025-05-31 19:23:51 AEST | 30011704-user5@smec.com | james.stone@smec.com | 732 | 11 |  |  | Other | [58 empty] | Chlorine build | [5 empty] | 7cde908f-ce13-43da-844a-31c0a15cbb27,04c3b65e-5067-4194-925d-30ae3967f346 | , | https://web.fulcrumapp.com/photos/view?photos=7cde908f-ce13-43da-844a-31c0a15cbb27%2C04c3b65e-5067-4194-925d-30ae3967f346 | Concrete | Grout Hole |  |  | Grout Hole
3f07eaf6-e9b4-4d56-987c-9291c8428249 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | f42d3610-6e6c-463d-9bdb-ee8da5bc2fc8 | 10 |  |  |  | 2025-05-31 19:24:41 AEST | 2025-05-31 19:26:09 AEST | 30011704-user5@smec.com | james.stone@smec.com | 730 | 11 |  | Steel Channel Bracket | [59 empty] | Delimitation of Coating | [5 empty] | 9dd9c729-3500-43cc-b904-cd92efadd0ba,cc1d64a3-d478-4c58-ab9f-6cab709b7205,c249b4bf-2c7c-4d29-a4e5-2df62917c94e,4acc1ec7-ef64-4be9-8a2c-a08f05bc2651 | ,,, | https://web.fulcrumapp.com/photos/view?photos=9dd9c729-3500-43cc-b904-cd92efadd0ba%2Ccc1d64a3-d478-4c58-ab9f-6cab709b7205%2Cc249b4bf-2c7c-4d29-a4e5-2df62917c94e%2C4acc1ec7-ef64-4be9-8a2c-a08f05bc2651 | Steel | Channel Bracket
8d88016c-f6ef-4b3e-aa12-4ee73cbb987b | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 18:24:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 751 | 12 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) | 84673 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 44873.7599 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 751, 12 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Grout spalling from circle joint up to 100mm x 50mm. |  | Grout spalling from circle joint up to 100mm x 50mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Drummy grout about 100x200mm around ring edge | no |  |  |  |  | 7adf2a38-c98d-4e60-8c21-7f2874d695bf,537ddd50-24a0-4cb1-905a-711f407fca5e,8322c287-b872-49e6-93df-7732927594bb | ,, | https://web.fulcrumapp.com/photos/view?photos=7adf2a38-c98d-4e60-8c21-7f2874d695bf%2C537ddd50-24a0-4cb1-905a-711f407fca5e%2C8322c287-b872-49e6-93df-7732927594bb | Concrete | Circular Joint | Drummy,Surface Damage
4e8a8342-19a3-4591-9551-c82963b64336 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 18:21:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 752 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84674 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 752, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 400mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 400mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Drummy grout over an area of about 300x400mm close around ring Joint | no |  |  |  |  | 4abb0ea8-e087-4a13-a6d0-fb995b791c18,cdf65da6-b356-431e-accb-d4ca9c11b9ec | , | https://web.fulcrumapp.com/photos/view?photos=4abb0ea8-e087-4a13-a6d0-fb995b791c18%2Ccdf65da6-b356-431e-accb-d4ca9c11b9ec | Concrete | Circular Joint | Drummy |  | Circular Joint not radial
b9bef3a7-67cf-4398-b378-4c0a00fde3c7 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:29:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 754 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84677 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 754, 1 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | HM |  | Location is 2 o clock. There is advanced in corrosion. Extent of the delaminated area remains the same. | yes |  |  |  |  | a245447a-58af-4d0c-a6be-61504ed096d4,7fb5cad3-eef3-4a49-be96-f1a5d1e0e8c3 | , | https://web.fulcrumapp.com/photos/view?photos=a245447a-58af-4d0c-a6be-61504ed096d4%2C7fb5cad3-eef3-4a49-be96-f1a5d1e0e8c3 | Concrete | Circular Joint | Drummy
6ab26aa1-f980-4d7c-8c78-6ac0f14b121e | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 17:02:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 754 | 11 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84676 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 754, 11 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is unchanged | no |  |  |  |  | 65e850f7-2299-4975-b70d-092071cd4eb9 |  | https://web.fulcrumapp.com/photos/view?photos=65e850f7-2299-4975-b70d-092071cd4eb9 | Concrete | Radial Joint | Drummy
9d2a3e68-3f6e-4996-b319-f1dbcc1feb05 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:51:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 754 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27672 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 754, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion. Channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion. Channel anchor bolts have Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | No change to corrosion. More ore dust than corrosion | no |  |  |  |  | 836df61f-90b6-4888-83f0-a0f5d00e75b6 |  | https://web.fulcrumapp.com/photos/view?photos=836df61f-90b6-4888-83f0-a0f5d00e75b6 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
2b59afa8-01d8-4160-a2c2-62f71e0e0ab9 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 754 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84675 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 754, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
5e008bb2-8d5f-4e4c-b0ff-9d2a528993b3 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 755 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68735 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint Circle Joint) - Ring 755, 4 o'clock. Concrete Shell Segment. Identified in 2019. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Previously listed under AIMS defect 30782 under incorrect AIMS quadrant. 30782 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
b0b0df07-5a12-47d7-bd8c-681aa2e0878b | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 756 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68736 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Ring (Segmental Concrete) - Damage Affecting Single Ring - Ring 756, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Previously listed under AIMS defect 30783 under incorrect AIMS quadrant. 30783 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
c8ff4139-8d32-49e0-a8a3-e6ee659dba46 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:35:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 758 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27673 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 5 | Level 5 | Level 5 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 758, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 Major Corrosion up to 50% coverage. Channel anchor bolts have Level 5 High Corrosion. |  | Steel channel support bracket has Level 4 Major Corrosion up to 50% coverage. Channel anchor bolts have Level 5 High Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | 1. Repair anchor bolts as per BHP standard drawing 000-S-12598. 2. Apply protective coating to extend at least 150mm past all repair affected areas, corroded areas. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | - | Replace Component Competent Supervisor |  |  | Small section, including bolt is very badly corroded. | no |  |  |  |  | e2da9de1-2a3d-4302-958c-33481faa741f,040e7774-b1bf-4096-9dd6-74eb507be4d5 | , | https://web.fulcrumapp.com/photos/view?photos=e2da9de1-2a3d-4302-958c-33481faa741f%2C040e7774-b1bf-4096-9dd6-74eb507be4d5 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
798d2204-97d9-4886-a0bb-9fbd416771c3 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 759 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84678 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 759, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 250mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Radial Joint | Drummy
147b0c28-1a97-4c9f-8c26-c23e208d8fc2 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:31:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 760 | 1 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 84680 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 760, 1 O'Clock, Hydrophyllic Joint Seal (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Circle joint has Grout Delamination / Drummy Grout over one area of 400mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over one area of 400mm x 300mm. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor | SS |  | Location is 2 o clock. Corrosion has advanced through initial inspection. Extent of delaminated area remains the same. | no |  |  |  |  | 512e5b04-9d07-4429-a103-cf34d51eaee1,0371149d-72d7-45f9-bc95-225c35ce5547,3b4db91f-53c6-476f-9c53-aa48c9f67173,85019ca4-7ac2-4f8b-9b25-cb4e7fde3fae | ,,, | https://web.fulcrumapp.com/photos/view?photos=512e5b04-9d07-4429-a103-cf34d51eaee1%2C0371149d-72d7-45f9-bc95-225c35ce5547%2C3b4db91f-53c6-476f-9c53-aa48c9f67173%2C85019ca4-7ac2-4f8b-9b25-cb4e7fde3fae | Concrete | Circular Joint | Drummy
d4e679b4-e742-4252-ae8a-0c7a3585606f | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 760 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 68737 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 760, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 400mm x 250mm. |  | Concrete shell segment has drummy concrete over an area of 400mm x 250mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Reinforcement | Drummy
2839121d-06c2-4e3b-889b-ad1316315f24 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:47:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 762 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27062 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 762, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Surface Corrosion up to 25% coverage. |  | Steel channel support bracket has Level 2 - Surface Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | More mud than corrosion | no |  |  |  |  | fcfbcfeb-6980-4983-bcba-85d33e4a9a05,75ad73d8-18bb-4737-98fc-878ad9898ca2 | , | https://web.fulcrumapp.com/photos/view?photos=fcfbcfeb-6980-4983-bcba-85d33e4a9a05%2C75ad73d8-18bb-4737-98fc-878ad9898ca2 | Steel | Channel Bracket | Corrosion-Surface
5cdb050c-2734-4828-b902-be4a35a00913 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:17:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 762 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84681 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 762, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Circular Joint | Drummy
0a5f655d-9043-43ef-bd08-fc6ff665135a | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:15:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 764 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68738 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 764, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints. 100mm x 350mm |  | Grout Delamination / debonding at radial segment bolted joints. 100mm x 350mm | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | services loss | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Radial Joint | Drummy
d2d4b31a-1c24-4a96-9b82-3ff14bdf9c94 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:44:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 766 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27063 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 766, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 2 Corrosion. |  | Channel anchor bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [7 empty] | no |  |  |  |  | 03a97322-4971-41ad-85a0-81da3eb66b3c,de7fa56b-50f1-4e96-bed1-bd6bfa256bc9 | , | https://web.fulcrumapp.com/photos/view?photos=03a97322-4971-41ad-85a0-81da3eb66b3c%2Cde7fa56b-50f1-4e96-bed1-bd6bfa256bc9 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
0e9988f2-74c8-46c1-92f5-823ad9a0dc6b | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:43:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 766 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84682 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 766, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | No change to delamination | no |  |  |  |  | 35e56719-3256-4771-8dbf-a876fdc45365 |  | https://web.fulcrumapp.com/photos/view?photos=35e56719-3256-4771-8dbf-a876fdc45365 | Concrete | Circular Joint | Drummy
3a3133d0-fad0-48cd-be15-5c91b614d287 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:13:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 766 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27675 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Financial | Financial |  | Missing Component | Missing Component |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 766, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Two channel anchor bolts missing. |  | Two channel anchor bolts missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Steelwork Remediation Crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | No change | no |  |  |  |  | 7c908367-810c-461d-8452-7d3474259dbd,4b036b6a-ad8b-425c-8dea-a2bdf5fbdbfb | , | https://web.fulcrumapp.com/photos/view?photos=7c908367-810c-461d-8452-7d3474259dbd%2C4b036b6a-ad8b-425c-8dea-a2bdf5fbdbfb | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
fa341f4e-454c-4a51-adbc-119a847412e6 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:12:17 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 766 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68739 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 766, 4 o'clock. Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints over an area 350mm x 250mm. |  | Grout Delamination / debonding at circle segment bolted joints over an area 350mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | No | - | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Circular Joint | Drummy
2f442673-614b-4b92-b690-31e4d849e04e | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:11:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 767 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 27369 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 767, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Cable tray has Level 3 - Medium Corrosion |  | Cable tray has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Corrosion still evident | no |  |  |  |  | cdb6b2a3-75df-4836-a7b4-ac36c5793dda,4dc406dc-aded-4f3e-8dff-80021ff2146d | , | https://web.fulcrumapp.com/photos/view?photos=cdb6b2a3-75df-4836-a7b4-ac36c5793dda%2C4dc406dc-aded-4f3e-8dff-80021ff2146d | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface |  | not channel bracket
29a580e7-827d-48bc-8ed7-d950abaeee06 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:09:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 769 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84683 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 769, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 500mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 500mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Circular Joint | Drummy
749f466b-8fc7-46f6-b245-7c8f8c425dcc | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:08:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 770 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84684 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 770, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Radial Joint | Drummy
8ff40dfc-0c41-408f-83e7-ab5aafa12122 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:40:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 771 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84685 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 771, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination has not changed | no |  |  |  |  | 913b9b27-8762-4637-89f6-977c70f56b95,80448f54-8cc6-4660-8a31-f7ae3efd1b21 | , | https://web.fulcrumapp.com/photos/view?photos=913b9b27-8762-4637-89f6-977c70f56b95%2C80448f54-8cc6-4660-8a31-f7ae3efd1b21 | Concrete | Radial Joint | Drummy
28c01c70-46e7-4eb2-a2c9-fa8ba960c05f | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:07:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 771 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68741 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 771, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at radial segment bolted joints |  | Grout Delamination / debonding at radial segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | loss of services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Radial Joint | Drummy
d9a016cd-9035-4dd4-bac1-0edd8f9314fe | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:06:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 772 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84686 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 772, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Previously marked defect does not seem delaminated. Difference in tap tone due to thick layer of curing agent | yes |  |  |  |  | 0a881192-831c-4c34-8a2c-92a29667d8df |  | https://web.fulcrumapp.com/photos/view?photos=0a881192-831c-4c34-8a2c-92a29667d8df | Concrete | Circular Joint | Drummy
78d99452-1a9a-4179-87ff-7fe029669186 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:04:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 772 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84687 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 772, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 400mm x 300mm and 150mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 400mm x 300mm and 150mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | SS |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Radial Joint | Drummy
efc7a20d-13dc-4982-b111-e0ee90841163 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:03:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 773 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27370 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 773, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | leakage should be financial | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Leak is still evident. Note that this does not seem to be water, there are no salts deposited, and the small amount of liquid is viscous. | no |  |  |  |  | 68bd883b-6972-430d-aebf-bf8141a71d02,66ffe96b-4672-4a55-a0d4-c33db28f2bbe | , | https://web.fulcrumapp.com/photos/view?photos=68bd883b-6972-430d-aebf-bf8141a71d02%2C66ffe96b-4672-4a55-a0d4-c33db28f2bbe | Concrete | Grout Hole | Leaks |  | Not reinforcement
e1300a00-d250-424b-b9cb-ff2c4ee4e2f6 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:01:09 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 773 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84688 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 773, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Circular Joint | Drummy
59906dd4-7f35-49b5-8848-ab18584e6009 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 06:00:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 774 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68740 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 774, 4 o'clock. Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints |  | Grout Delamination / debonding at circle segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Circular Joint | Drummy
70d0a5b5-d9ac-46d0-ae2f-3f948f2bd032 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 05:59:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 775 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84690 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 775, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident at this stated location. Previous patch appears in good order. | yes | [7 empty] | Concrete | Circular Joint | Drummy
b04e3594-63aa-4dbf-98ed-cea0b67cd5c2 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 775 | 8 | Grout Injection Hole | Grout Injection Hole |  | 68742 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 775, 8 o'clock. Concrete Shell Segment. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Previously listed under AIMS defect 30785 under incorrect AIMS quadrant. 30785 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Grout Hole,Reinforcement | Leaks
8da34fe7-4bfc-48f8-87ce-d1fbceb24954 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 775 | 9 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27677 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 6 | Condition Rating 6 | Condition Rating 6 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 775, 9 O'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. Leak appears to have increased. |  | Grout injection hole has Leak Active at time of inspection. Leak appears to have increased. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Grout Hole,Reinforcement | Leaks
a1d291c2-1d2e-4b5c-84c9-17443c3addc1 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 05:57:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 776 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84691 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 776, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | No delamination noted at this location. Patching seems in good order. | yes |  |  |  |  | e69028d6-c8c4-4d8c-9b1c-d05a1109d244 |  | https://web.fulcrumapp.com/photos/view?photos=e69028d6-c8c4-4d8c-9b1c-d05a1109d244 | Concrete | Circular Joint | Drummy
2cb516e2-6afe-4c98-98e6-aa4bbf60cc11 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 05:50:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 776 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84692 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 776, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm and 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm and 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order. | yes |  |  |  |  | 7ebf9232-ba9b-4522-b8d2-b2cd049ba88a |  | https://web.fulcrumapp.com/photos/view?photos=7ebf9232-ba9b-4522-b8d2-b2cd049ba88a | Concrete | Radial Joint | Drummy
8edef217-92fe-45a4-8ccc-76ba02c49a5f | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 05:48:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 777 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68743 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint Circle Joint) - Ring 777, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Previously listed under AIMS defect 30786 under incorrect AIMS quadrant. 30786 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order. | yes | [7 empty] | Concrete | Circular Joint | Drummy
278475fd-295f-46ea-a18e-0f040b6d74a8 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 05:46:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 778 | 2 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84695 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 778, 2 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | SS |  | Defect is still the same. Note, location was stated as 4 o’clock, it is actually at 2 oclock | no |  |  |  |  | 112fa85a-16fd-4ee9-8d5d-e0b0c49b658a,7ef3aad1-85ee-4144-8b1f-d01cf7da3938 | , | https://web.fulcrumapp.com/photos/view?photos=112fa85a-16fd-4ee9-8d5d-e0b0c49b658a%2C7ef3aad1-85ee-4144-8b1f-d01cf7da3938 | Concrete | Circular Joint | Drummy
f6fc6bbb-d4c2-4514-af53-17b20cb9ca39 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 05:44:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 778 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 84694 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 778, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm and 150mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm and 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | No delamination noted at the described area | yes | [7 empty] | Concrete | Radial Joint | Drummy
921f0ce0-8c92-4bfb-a4e4-f25af50ed06b | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 22:23:00 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 779 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27064 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 779, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor |  |  | Leak is active. Impacting cable tray and platform steel. | no |  |  |  |  | 6e1aa118-888e-4923-ad42-80b2f6a59b79,74f0d31c-3796-4732-85cc-d8330152797d,f6eb416b-aa6b-4024-ae25-760dab54ed66,9d3838f2-343c-4e89-9dc8-767dd052e36a | ,,, | https://web.fulcrumapp.com/photos/view?photos=6e1aa118-888e-4923-ad42-80b2f6a59b79%2C74f0d31c-3796-4732-85cc-d8330152797d%2Cf6eb416b-aa6b-4024-ae25-760dab54ed66%2C9d3838f2-343c-4e89-9dc8-767dd052e36a | Concrete,Steel | Circular Joint,Misc (Pipes/Cable Tray/etc),Reinforcement | Leaks
1d8a81c6-4ba8-4b14-aef1-a7f62b648b2a | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 780 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68751 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint (Radial Joint) - Ring 780, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of same size 200mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of same size 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | Previously listed under AIMS defect 30790 under incorrect AIMS quadrant. 30790 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | loss of services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Radial Joint | Drummy
a4e02004-2cc7-463b-8f87-b896138ca6db | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 15 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 780 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84696 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 780, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
b8a1d2df-3663-4edc-b5ec-ccbaa2ad9ebe | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 10 |  |  |  | 2025-05-31 06:25:29 AEST | 2025-05-31 06:32:43 AEST | 30011704-user5@smec.com | james.stone@smec.com | 760 | 2 |  | Hydrophilic Joint Seal (Circle Joint) | [17 empty] | 4 | [14 empty] | At bolted connection grouted recess | [5 empty] | Large delaminated and spalled area, encroaches onto adjoining segment. CP wiring is caught into it. | [18 empty] | SS |  | Most likely due to a leak, which may now be inactive. See cable tray defect nearby with advanced corrosion. | [5 empty] | 987c3857-cc0e-4547-a358-e91e02be1be2 |  | https://web.fulcrumapp.com/photos/view?photos=987c3857-cc0e-4547-a358-e91e02be1be2 | Concrete | Circular Joint,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Drummy,Leaks,Surface Damage
7e915015-8204-4f5c-873d-3d2beb386865 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 11 |  |  |  | 2025-05-31 05:34:33 AEST | 2025-05-31 05:41:34 AEST | 30011704-user5@smec.com | james.stone@smec.com | 780 | 3 |  |  | Cable tray and platform | [31 empty] | Cable tray and platform | [5 empty] | Advance corrosion in cable trays due to leak at radial joint. Medium level of corrosion in the platform due to the leak at radial joint | [18 empty] | HM | [7 empty] | 66723365-73aa-40d5-b63e-15df4226904c,d3eb6349-23e6-4e01-88b6-ebc8581292e0,40da109e-8d81-43c6-85fe-ca9d92784d8b,297120ec-ee1b-448f-8de3-c4692657de4e | ,,, | https://web.fulcrumapp.com/photos/view?photos=66723365-73aa-40d5-b63e-15df4226904c%2Cd3eb6349-23e6-4e01-88b6-ebc8581292e0%2C40da109e-8d81-43c6-85fe-ca9d92784d8b%2C297120ec-ee1b-448f-8de3-c4692657de4e | Concrete | Misc (Pipes/Cable Tray/etc),Radial Joint | Leaks
01676bb1-22f2-43c8-ab6a-23fb2a91ce50 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 11 |  |  |  | 2025-05-31 05:47:59 AEST | 2025-05-31 05:50:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | 770 | 3 |  |  | Cable tray | [31 empty] | Cable tray | [5 empty] | Damaged bottom cable tray and top cable tray is mildly corroded | [18 empty] | HM | [7 empty] | d054f76c-a12b-4a29-a96c-bd1d323414fc,2dd511bb-944f-43a5-965f-b547c3cf5fdd | , | https://web.fulcrumapp.com/photos/view?photos=d054f76c-a12b-4a29-a96c-bd1d323414fc%2C2dd511bb-944f-43a5-965f-b547c3cf5fdd | Steel | Misc (Pipes/Cable Tray/etc)
f2be2fca-f97f-4324-85fd-2043c8d915a1 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 11 |  |  |  | 2025-05-31 06:16:56 AEST | 2025-05-31 06:19:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 761 | 3 |  |  | Cable tray | [31 empty] | Cable tray | [5 empty] | Advanced level of corrosion. Section loss in cable tray. | [26 empty] | cd95abd2-4715-4d00-abff-7bad29632fca |  | https://web.fulcrumapp.com/photos/view?photos=cd95abd2-4715-4d00-abff-7bad29632fca | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy
5c410ba4-e943-4320-84eb-c01c48c7ffe4 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 6 |  |  |  | 2025-05-31 22:14:58 AEST | 2025-05-31 22:16:29 AEST | 30011704-user5@smec.com | james.stone@smec.com | 780 | 2 |  | Segment Bolted Joint (Circle Joint) | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | SS | [7 empty] | 1f23edc5-5b00-4947-8bd5-0458bfc94828,97cb5d09-a05b-449e-9f21-bb5e5dcd95f8 | , | https://web.fulcrumapp.com/photos/view?photos=1f23edc5-5b00-4947-8bd5-0458bfc94828%2C97cb5d09-a05b-449e-9f21-bb5e5dcd95f8 | Concrete | Circular Joint | Drummy
8b167bd7-d4bf-4327-b09b-888bae3dd104 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 6 |  |  |  | 2025-05-31 22:24:50 AEST | 2025-05-31 22:26:14 AEST | 30011704-user5@smec.com | james.stone@smec.com | 778 | 2 |  | Segment Bolted Joint (Circle Joint) | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | SS | [7 empty] | 5f739f4d-ccd1-40c2-99f0-5ea3a81fa07f,c723a838-e2fd-4c4e-8de7-5dbc55379107 | , | https://web.fulcrumapp.com/photos/view?photos=5f739f4d-ccd1-40c2-99f0-5ea3a81fa07f%2Cc723a838-e2fd-4c4e-8de7-5dbc55379107 | Concrete | Circular Joint | Drummy
9b218218-a035-4551-b9ac-9cf283696bfc | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 11 |  |  |  | 2025-05-31 06:23:27 AEST | 2025-05-31 06:27:47 AEST | 30011704-user5@smec.com | james.stone@smec.com | 760 | 3 |  |  | Cable tray | [31 empty] | Cable tray | [5 empty] | Advanced corrosion due to leak from the radial joint | [18 empty] | HM | [7 empty] | e4c7a7f7-deed-4773-945e-92295b84d74e,9a495b17-2a9c-4c63-b18a-db79e1a62119,a47db82a-4618-4ba9-9bb9-73951f4ce3cb | ,, | https://web.fulcrumapp.com/photos/view?photos=e4c7a7f7-deed-4773-945e-92295b84d74e%2C9a495b17-2a9c-4c63-b18a-db79e1a62119%2Ca47db82a-4618-4ba9-9bb9-73951f4ce3cb | Concrete | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Leaks |  | Not Radial Joint
2761b0c8-1ca0-46d0-9401-bbf040dc34b7 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 7 |  |  |  | 2025-05-31 18:10:47 AEST | 2025-05-31 18:15:59 AEST | 30011704-user5@smec.com | james.stone@smec.com | 753 | 12 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Patch Repair | [42 empty] | Patch Repair at 12 o’clock | [5 empty] | 6e2f9816-f5cb-48ec-954f-40ee1e01d7c7,882b96d8-d654-4667-ae5e-71d4ac967d5c,8a19f533-0eb8-4fb3-b393-cfc04320630c | ,, | https://web.fulcrumapp.com/photos/view?photos=6e2f9816-f5cb-48ec-954f-40ee1e01d7c7%2C882b96d8-d654-4667-ae5e-71d4ac967d5c%2C8a19f533-0eb8-4fb3-b393-cfc04320630c | Concrete | Radial Joint |  |  | Radial Joint
eb7715bf-6cfc-41f9-9590-0cd757ca10b0 | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 7 |  |  |  | 2025-05-31 18:25:12 AEST | 2025-05-31 18:27:14 AEST | 30011704-user5@smec.com | james.stone@smec.com | 751 | 12 |  |  | Segmental concrete Repair | [58 empty] | 2x Patch Repair at 12 o’clock | [5 empty] | 3f0d0d15-1b32-4767-8d27-25d938572906,bf2dea38-2036-40df-bc4c-f5d1bee483ea | , | https://web.fulcrumapp.com/photos/view?photos=3f0d0d15-1b32-4767-8d27-25d938572906%2Cbf2dea38-2036-40df-bc4c-f5d1bee483ea | Concrete | Radial Joint |  |  | Radial Joint
6636575b-7be3-49b2-9852-91ce4be0fe6c | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3af8c79a-6e39-4440-bc1a-e05ded3e5a4d | 3 |  |  |  | 2025-06-02 04:15:20 AEST | 2025-06-02 04:20:41 AEST | 30011704-user5@smec.com | james.stone@smec.com | 776 | 6 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Concrete crack | 3 |  |  |  | Financial |  |  |  | Leaching thru crack |  | Severity Level 3 |  |  | Possible (Failure within 5 Years) |  | Ring 776, 6 o'clock middle ring |  | Failure of shell segment in compression or tension leading to single ring failure. |  |  |  | Crack segment allowing water to sip through. Leaking active at time of inspection |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | [16 empty] | BS | [7 empty] | 788ce800-826a-49a9-975c-dc0c71b633e8,e789ba9c-97a2-4617-bce7-40b9f9a2a2b8,9869af46-a38d-4e49-aa60-5f643479e698 | ,, | https://web.fulcrumapp.com/photos/view?photos=788ce800-826a-49a9-975c-dc0c71b633e8%2Ce789ba9c-97a2-4617-bce7-40b9f9a2a2b8%2C9869af46-a38d-4e49-aa60-5f643479e698 | Concrete | Middle of Panel | Crack,Leaks |  | Middle of Panel
b16422de-39d4-4999-a6b1-7b496f870157 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 01:04:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 781 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68752 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint Circle Joint) - Ring 781, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | HM |  | Drumminess is evident at joint 780-781 at 4 o clock. Drumminess is not evident at joint 781-782 at 4 o clock. | no |  |  |  |  | 0e508b67-04c7-4227-a40b-a14c632772a1,ff0f9ceb-05aa-4163-a5e4-c02c2f94f6d5,16d7c409-2f4e-413a-b372-db002c111b83,0a851444-0405-47aa-9f1c-d9b7a1b16331 | ,Drumminess is evident on the 781 side of the joint.,Unknown object, | https://web.fulcrumapp.com/photos/view?photos=0e508b67-04c7-4227-a40b-a14c632772a1%2Cff0f9ceb-05aa-4163-a5e4-c02c2f94f6d5%2C16d7c409-2f4e-413a-b372-db002c111b83%2C0a851444-0405-47aa-9f1c-d9b7a1b16331 | Concrete | Circular Joint | Drummy
81f419c6-8fe9-4207-843a-bb18e21fe4fe | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 04:03:15 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 782 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 68753 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Ring (Segmental Concrete) - Damage Affecting Single Ring - Ring 782, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 600mm x 600mm. |  | Concrete shell segment has drummy concrete over an area of 600mm x 600mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | loss of services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Drumminess is not evident. Previous patching is sufficient. | yes |  |  |  |  | cd2bef04-88c2-44ff-a1d0-d87bb3a64c06,eb04393d-234c-48e6-864f-7520f988f072 | , | https://web.fulcrumapp.com/photos/view?photos=cd2bef04-88c2-44ff-a1d0-d87bb3a64c06%2Ceb04393d-234c-48e6-864f-7520f988f072 | Concrete |  | Drummy |  | Duplicate - Remove
c344c693-c208-4448-b1ea-c76a1ec4265d | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 04:00:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 782 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27679 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 782, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts have Level 4 Medium High Corrosion. Missing nut at 2 O'clock |  | Channel anchor bolts have Level 4 Medium High Corrosion. Missing nut at 2 O'clock | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | 1.Replace missing anchor bolt nut. Alternatively, repair anchor bolts as per BHP standard drawing 000-S-12598. 2. Apply protective coating to extend at least 150mm past all repair affected areas, corroded areas. | Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | Hot Work | Replace Component Competent Supervisor | HM |  | Corrosion is still evident at the time of inspection. | no |  |  |  |  | f0ed2012-26f3-40d9-91e1-ff38fd1787c8,8aa72da7-317f-402a-9ae6-4ff482fe16e1 | , | https://web.fulcrumapp.com/photos/view?photos=f0ed2012-26f3-40d9-91e1-ff38fd1787c8%2C8aa72da7-317f-402a-9ae6-4ff482fe16e1 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
da45d115-6352-43dc-96e4-4a72513430e5 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:58:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 782 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84697 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 782, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | HM |  | Drumminess is not evident. Previous patching is sufficient. | yes |  |  |  |  | b7be7a59-d4c1-4f23-89d6-7d28ff69080b,0f925877-6c89-412a-897b-1c9cf9b93795 | , | https://web.fulcrumapp.com/photos/view?photos=b7be7a59-d4c1-4f23-89d6-7d28ff69080b%2C0f925877-6c89-412a-897b-1c9cf9b93795 | Concrete | Circular Joint | Drummy
60f4c3ab-5117-43ce-ad5a-10a6157b6182 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:47:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 785 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27065 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 785, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | Leak is still present. It is impacting cable trays and platform. | no |  |  |  |  | 81c69bf9-01c2-4c77-b556-b26327400561,c8bac978-18e9-4421-a990-38bc15c58cb7,e0f9f019-0e65-4dd6-92e8-280c955cf10a,f3f77562-bac9-4c07-9d32-0b75e8ee21cb,2ab287f3-2a40-4738-b491-a703b571c536,6259037d-0d1e-4348-9929-0dc8d0261422,6114f343-b82b-482b-a5a3-95fae5544c9c | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=81c69bf9-01c2-4c77-b556-b26327400561%2Cc8bac978-18e9-4421-a990-38bc15c58cb7%2Ce0f9f019-0e65-4dd6-92e8-280c955cf10a%2Cf3f77562-bac9-4c07-9d32-0b75e8ee21cb%2C2ab287f3-2a40-4738-b491-a703b571c536%2C6259037d-0d1e-4348-9929-0dc8d0261422%2C6114f343-b82b-482b-a5a3-95fae5544c9c | Concrete | Circular Joint,Misc (Pipes/Cable Tray/etc) | Leaks |  | Not reinforcement
113b46bb-8c52-4c36-b436-e42da8ff4348 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:49:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 785 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84698 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 785, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 500mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 500mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is not evident. Previous patching is sufficient. | yes |  |  |  |  | 265d72f5-3c3d-4b38-9892-96898b3cce41,1d8141ec-02ca-4df4-9fa5-f901004471c3 | , | https://web.fulcrumapp.com/photos/view?photos=265d72f5-3c3d-4b38-9892-96898b3cce41%2C1d8141ec-02ca-4df4-9fa5-f901004471c3 | Concrete | Circular Joint | Drummy
b0b78da3-0d70-4771-a176-e8a3c2f3bbc3 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:31:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 786 | 12 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 84701 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 44873.8336 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 786, 12 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Inadequate repair of the segment bolted radial joint. |  | Inadequate repair of the segment bolted radial joint. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Patch still has inadequate cover | no |  |  |  |  | 1e82c48b-6e98-4f8f-9bb3-1d253e0f16d8 |  | https://web.fulcrumapp.com/photos/view?photos=1e82c48b-6e98-4f8f-9bb3-1d253e0f16d8 | Concrete | Radial Joint
afab0abe-d958-4233-ba25-fc680f232481 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 01:15:24 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 786 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 84700 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 8/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 786, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 500mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 500mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor | HM |  | Drumminess is evident in 785-786 joint at 4 clock. Drumminess is not evident in 786-787 joint at 4 o clock. Previous patching is sufficient. | no |  |  |  |  | 4d5d61ea-89ce-4d9a-be8b-3eafab571688,3170a92d-2a6b-4ec0-9360-aad8414f2945,fab8c4c6-f292-48a2-9280-f7d43feb14f2 | ,, | https://web.fulcrumapp.com/photos/view?photos=4d5d61ea-89ce-4d9a-be8b-3eafab571688%2C3170a92d-2a6b-4ec0-9360-aad8414f2945%2Cfab8c4c6-f292-48a2-9280-f7d43feb14f2 | Concrete | Circular Joint | Drummy
9ceb561c-a5d6-47b2-8289-2799d9931752 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:38:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 788 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85702 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 788, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is not evident. Previous patching is sufficient. | yes |  |  |  |  | bd89ea83-b3a4-4bca-a4ad-5e77e41445c7,75492214-0f42-4c49-89f3-e5f33babb094 | , | https://web.fulcrumapp.com/photos/view?photos=bd89ea83-b3a4-4bca-a4ad-5e77e41445c7%2C75492214-0f42-4c49-89f3-e5f33babb094 | Concrete | Radial Joint | Drummy
362e7fe9-523f-4fea-8c94-6c0acd1d53d5 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:36:21 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 789 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27066 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 789,1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has Cracking. |  | Concrete shell segment has Cracking. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | GTS Specification. Concrete remediation crew. | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor |  |  |  | no |  |  |  |  | b6ca879b-384e-443d-82bf-beb499b2d59d,c7f06322-bfad-4939-8a87-ed3191dea2e7 | , | https://web.fulcrumapp.com/photos/view?photos=b6ca879b-384e-443d-82bf-beb499b2d59d%2Cc7f06322-bfad-4939-8a87-ed3191dea2e7 | Concrete | Radial Joint | Crack |  | Radial Joint Not reinforcement
0509d9b4-5a4a-4a7a-b520-afe4830fe864 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:31:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 789 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27067 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 789,3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has Cracking. |  | Concrete shell segment has Cracking. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | GTS Specification. Concrete remediation crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | No change to the cracking. Not grouted. | no |  |  |  |  | 83adb464-58f3-46bd-882a-9a42886810d2 |  | https://web.fulcrumapp.com/photos/view?photos=83adb464-58f3-46bd-882a-9a42886810d2 | Concrete | Circular Joint | Crack |  | Circular Joint Not reinforcement
0c317945-dd25-4081-833d-a74499e51786 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:28:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 790 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 68754 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Bored Tunnel - Ring (Segmental Concrete) - Damage Affecting Single Ring - Ring 790, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 900mm x 300mm. |  | Concrete shell segment has drummy concrete over an area of 900mm x 300mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Previously listed under AIMS defect 30797 under incorrect AIMS quadrant. 30797 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | Not Specified | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | HM |  | Drumminess is not evident. Previous patching is sufficient | yes |  |  |  |  | 664aa361-f5ad-4432-9385-9f3feec3868a,3236bcde-3c30-4c48-9b04-2e98774a4ff4 | , | https://web.fulcrumapp.com/photos/view?photos=664aa361-f5ad-4432-9385-9f3feec3868a%2C3236bcde-3c30-4c48-9b04-2e98774a4ff4 | Concrete | Circular Joint | Drummy |  | Circular Joint Not reinforcement
e3f4851c-5e11-4cad-a8ef-595d65bf92a3 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:24:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 792 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27680 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 792, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Cable tray has Level 3 - Medium Corrosion |  | Cable tray has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Corrosion is still evident at the time of the inspection. | no |  |  |  |  | b58b921a-8633-4031-9d2c-f298c063d7da |  | https://web.fulcrumapp.com/photos/view?photos=b58b921a-8633-4031-9d2c-f298c063d7da | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
b6b637fc-a40d-4e0a-9eb1-df2abddf386f | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:39:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 793 | 1 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 96850 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed |  |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Unknown | Unknown |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 793, 1 O'Clock, Hydrophilic Joint Seal (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Circle joint seal has leak Active at time of inspection. |  | Circle joint seal has leak Active at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and safety to personnel | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | HM |  | Leak is active. | no |  |  |  |  | d245a678-0623-4d1a-882f-d6bbf96d2cc9,3a1257ba-ba6e-4ad2-8efa-9446d098b502 | , | https://web.fulcrumapp.com/photos/view?photos=d245a678-0623-4d1a-882f-d6bbf96d2cc9%2C3a1257ba-ba6e-4ad2-8efa-9446d098b502 | Concrete | Circular Joint | Leaks |  | Not reinforcement
1ab60c37-cb6c-4791-812d-6f074e86e782 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:15:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 793 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27069 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 793, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Cable tray has Level 3 - Medium Corrosion |  | Cable tray has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Advanced corrosion in cable trays | no |  |  |  |  | 94391b84-a4c0-4afc-b1ba-9937fc499a5d,635aab1f-fcce-44f9-9c3d-c6feff651ca7,da3d6da0-9ed4-4305-bf2a-8b751d3a4a1e | ,, | https://web.fulcrumapp.com/photos/view?photos=94391b84-a4c0-4afc-b1ba-9937fc499a5d%2C635aab1f-fcce-44f9-9c3d-c6feff651ca7%2Cda3d6da0-9ed4-4305-bf2a-8b751d3a4a1e | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy
fa13bad5-9644-472b-b50e-e9f9f2bc0ca1 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:08:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 793 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27068 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 793,2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Circle joint seal has Leak Active at time of inspection. |  | Circle joint seal has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | Water leak with large salt deposits, resulting corrosion of the surrounding metal components. Suggest treatment as a priority. | no |  |  |  |  | 530b97af-4f69-4581-aaad-b6357a1c7041,5b1faf0f-e319-4664-bead-e3bb5cb6054a,2679b108-0f7e-476e-85b0-b9a43b272359,f1f99758-4a43-4b90-b94a-edd17739f2a5,e5e3f2a8-93af-49b9-bf76-1f86ae6d0d4c,56941924-2125-45e4-abd9-b48d897cc96e,17b11059-85b3-447a-abf3-509bf0c12f7d | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=530b97af-4f69-4581-aaad-b6357a1c7041%2C5b1faf0f-e319-4664-bead-e3bb5cb6054a%2C2679b108-0f7e-476e-85b0-b9a43b272359%2Cf1f99758-4a43-4b90-b94a-edd17739f2a5%2Ce5e3f2a8-93af-49b9-bf76-1f86ae6d0d4c%2C56941924-2125-45e4-abd9-b48d897cc96e%2C17b11059-85b3-447a-abf3-509bf0c12f7d | Concrete | Circular Joint | Leaks |  | Not reinforcement
820a5c35-8fe1-4ff8-a0f4-504d88f08a47 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 03:01:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 794 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 68756 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44540.4508 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 794, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 5% coverage. |  | Steel channel support bracket has Level 1 - Surface Corrosion up to 5% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | No change | no |  |  |  |  | 31c149f8-a6a1-419b-b985-80865c0fca5a |  | https://web.fulcrumapp.com/photos/view?photos=31c149f8-a6a1-419b-b985-80865c0fca5a | Steel | Channel Bracket | Corrosion-Surface
2b815deb-e60e-4881-9d33-0c2bd35c5115 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 01:16:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 794 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68755 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 794, 4 o'clock. Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints |  | Grout Delamination / debonding at circle segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is evident in 793-794 joint at 4 o clock. 794-795 Drumminess is not evident. Previous patching is sufficient | no |  |  |  |  | 25761a3d-f887-49bd-b21e-372062c671b5,4053f9b0-9b31-4f2f-8141-69817c904ca1,e978eaf3-e13f-4c34-9f08-bf12c2d430a8 | Drumminess evident in 794 side of the joint ,, | https://web.fulcrumapp.com/photos/view?photos=25761a3d-f887-49bd-b21e-372062c671b5%2C4053f9b0-9b31-4f2f-8141-69817c904ca1%2Ce978eaf3-e13f-4c34-9f08-bf12c2d430a8 | Concrete | Circular Joint | Drummy
1def4a20-4e57-49b7-b489-95011a5aeb28 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:40:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 794 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 27070 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 794,1 o'clock. Concrete Shell Segment |  |  |  | Concrete shell segment has Cracking |  | Concrete shell segment has Cracking | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Leak is active at 2 o clock. | no |  |  |  |  | 8ff21c40-45b6-4115-ad31-c562e9495f36,de2ba1ea-5a49-40dc-b3f4-d6f4d8c1bba3 | , | https://web.fulcrumapp.com/photos/view?photos=8ff21c40-45b6-4115-ad31-c562e9495f36%2Cde2ba1ea-5a49-40dc-b3f4-d6f4d8c1bba3 | Concrete | Circular Joint | Crack,Leaks |  | Circular Joint
74cf932f-a171-433e-ae5a-7800edb1ba70 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:52:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 795 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85703 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 795, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Drummy section is unchanged | no |  |  |  |  | fae394ab-3cb6-484f-9d97-6308983da559,fe9f617f-810b-4fa3-95ab-d3cb0be8b3b0 | , | https://web.fulcrumapp.com/photos/view?photos=fae394ab-3cb6-484f-9d97-6308983da559%2Cfe9f617f-810b-4fa3-95ab-d3cb0be8b3b0 | Concrete | Radial Joint | Drummy
f03f5864-5c02-4607-b610-bd30586841b7 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:51:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 795 | 4 | Grout Injection Hole | Grout Injection Hole |  | 68757 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 795, 4 o'clock. Concrete Shell Segment - Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | HM |  | Leak is not evident. It’s possible patching might have been done. | yes |  |  |  |  | 9a302885-84f8-4f53-9d0f-1b8e55a006ee |  | https://web.fulcrumapp.com/photos/view?photos=9a302885-84f8-4f53-9d0f-1b8e55a006ee | Concrete | Grout Hole | Leaks |  | Not reinforcement
c0b61495-7d05-4a59-b915-c53bc41092df | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:35:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 796 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68758 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 796, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints |  | Grout Delamination / debonding at circle segment bolted joints | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is not evident. Previous patch is sufficient. | yes |  |  |  |  | 3cf100e6-7d3f-4e25-8f13-2fffd8db51af,b126145b-6f75-4236-a8c2-c6493f7bfc5e | , | https://web.fulcrumapp.com/photos/view?photos=3cf100e6-7d3f-4e25-8f13-2fffd8db51af%2Cb126145b-6f75-4236-a8c2-c6493f7bfc5e | Concrete | Radial Joint | Drummy
6f7819eb-4f0e-4a1e-b3d3-48c5beb575e4 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:46:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 797 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85704 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 797, 12 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 300mm x 250mm. |  | Concrete shell segment has drummy concrete over an area of 300mm x 250mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Drummy section is unchanged | no |  |  |  |  | 2bb6c878-79a7-4770-b5ee-aab808766135,5c84a665-8f55-4df2-b590-9ccb2a1d8342 | , | https://web.fulcrumapp.com/photos/view?photos=2bb6c878-79a7-4770-b5ee-aab808766135%2C5c84a665-8f55-4df2-b590-9ccb2a1d8342 | Concrete | Radial Joint | Drummy |  | Radial Joint
5f6854a3-edc2-4d64-8287-988ce6fd1038 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:31:50 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 797 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27071 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 797, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | HM |  | Not active at the time of inspection. Corrosion present on cable trays caused by this leak. | yes |  |  |  |  | df789c6f-68cd-4c8d-8dc4-bf3a0cd28963,ce2b44bd-bb9f-4e06-a0b6-74720a3d1780,2cf14c37-fae8-4395-8555-c8010497b03b,b860f95b-3416-4fe4-9c12-23dab596092d | ,,, | https://web.fulcrumapp.com/photos/view?photos=df789c6f-68cd-4c8d-8dc4-bf3a0cd28963%2Cce2b44bd-bb9f-4e06-a0b6-74720a3d1780%2C2cf14c37-fae8-4395-8555-c8010497b03b%2Cb860f95b-3416-4fe4-9c12-23dab596092d | Concrete | Circular Joint,Misc (Pipes/Cable Tray/etc) | Leaks |  | Not reinforcement
61162c38-4ccb-4bd3-ac57-a4339e37decf | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:41:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 798 | 1 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85707 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 798, 1 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over two areas of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Location is 2 o clock | no |  |  |  |  | 44571ab9-1e4a-43e9-86ab-d9e283b801c7 |  | https://web.fulcrumapp.com/photos/view?photos=44571ab9-1e4a-43e9-86ab-d9e283b801c7 | Concrete | Circular Joint | Drummy
52c0087c-8988-49bc-84bf-fadd93b50798 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:31:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 798 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 85705 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44874.2559 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 798, 11 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion up to 10% coverage. |  | Steel channel support bracket has Level 2 Minor Corrosion up to 10% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Minor corrosion | no |  |  |  |  | 2a10f1b3-de30-4cb4-be88-98e54bb0169d,fe3c8d38-16a6-4b4c-bca0-7d523e2a3224 | , | https://web.fulcrumapp.com/photos/view?photos=2a10f1b3-de30-4cb4-be88-98e54bb0169d%2Cfe3c8d38-16a6-4b4c-bca0-7d523e2a3224 | Steel | Channel Bracket | Corrosion-Surface
d2f1d680-b6b3-4b52-90c5-9ed2fa547776 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:18:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 798 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85706 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 798, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | This defect is quite noticeably drummy, at the radial joint in the segment. It appears that multiple patches have occurred at this location. Requires breaking back and treating. Close to the 11 o’clock mark. | no | [7 empty] | Concrete | Radial Joint | Drummy
0d9a552a-206e-44d9-adf0-0cfbb5097f75 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:29:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 798 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 27072 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing |  |  |  | 4 | [6 empty] | Localised Corrosion ATM |  | Severity Level 2 | Severity Level 2 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Ring 798, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Salts from adjacent leak are affecting the bracket and bolts. One bolt is at failure point. Also to note, adjacent fire main and cable trays are corroded. Suggest immediate treatment of leak and corrosion. | yes |  |  |  |  | a0a880e7-6241-4c86-94bd-e2b1651a7d4a,e0129d1f-3257-4a24-a94d-beabab27b1e6,f02e6d62-2cb6-4838-bb90-5cb5984df3fe,5d4065fa-358d-4bed-82df-0ed1376a538d,9b313235-c06b-430f-a175-c94cccfbd70a,1328f8f8-80f7-4aa8-9724-a67930f5e481,a6c31cb4-2232-4c45-a1b8-88906e42d964 | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=a0a880e7-6241-4c86-94bd-e2b1651a7d4a%2Ce0129d1f-3257-4a24-a94d-beabab27b1e6%2Cf02e6d62-2cb6-4838-bb90-5cb5984df3fe%2C5d4065fa-358d-4bed-82df-0ed1376a538d%2C9b313235-c06b-430f-a175-c94cccfbd70a%2C1328f8f8-80f7-4aa8-9724-a67930f5e481%2Ca6c31cb4-2232-4c45-a1b8-88906e42d964 | Steel | Channel Bracket,Channel Bracket-Bolt,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface,Leaks |  | Corrosion HEavy
bf1fa0d4-5763-450d-981c-d3ed07546112 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-01 18:33:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 800 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85708 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 800, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 300mm x 300mm and 300mm x 400mm.. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 300mm x 300mm and 300mm x 400mm.. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | HM |  | Drumminess is not evident. Previous patch is sufficient. | no |  |  |  |  | 17bb761d-7487-4fdb-ba26-9c708674db9d,65fa2d86-88ad-41e2-857f-9a2a3326b8ee,9bc16e21-0467-4499-83ee-47b61e2c8d0e | ,, | https://web.fulcrumapp.com/photos/view?photos=17bb761d-7487-4fdb-ba26-9c708674db9d%2C65fa2d86-88ad-41e2-857f-9a2a3326b8ee%2C9bc16e21-0467-4499-83ee-47b61e2c8d0e | Concrete | Radial Joint | Drummy
36f7afed-66d1-42ae-9059-367d06f93818 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:43:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 801 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27073 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 801, 1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | HM |  | Leak still seems active, but slow. Large amounts of salt deposits. Location is 2 o clock. | no |  |  |  |  | d9823145-f04e-43cb-aedc-c7c918e73013,64a78f69-bd68-45b9-b9b0-0f387802b709,e03824e6-43cc-4b87-bab4-e02c3ffad9bb,ed2bc8d7-4300-434f-8f12-abe39c6badbc,58d35547-b6c3-422b-9c60-0d2de2b8ff51,1257a2f7-0a2d-49b5-b25d-06acdd576201,9f3415ea-03b4-488a-a0b9-3b533fabc29b | ,,,,,, | https://web.fulcrumapp.com/photos/view?photos=d9823145-f04e-43cb-aedc-c7c918e73013%2C64a78f69-bd68-45b9-b9b0-0f387802b709%2Ce03824e6-43cc-4b87-bab4-e02c3ffad9bb%2Ced2bc8d7-4300-434f-8f12-abe39c6badbc%2C58d35547-b6c3-422b-9c60-0d2de2b8ff51%2C1257a2f7-0a2d-49b5-b25d-06acdd576201%2C9f3415ea-03b4-488a-a0b9-3b533fabc29b | Concrete | Circular Joint | Leaks |  | Not reinforcement
581ff8b6-1dbe-4889-9d8b-4af95b62005a | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 02:07:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 801 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85709 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 801, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 300mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Drumminess is not evident. Previous patch is sufficient | yes |  |  |  |  | 392fc7b7-5e4b-4e8b-b0a1-fcec2486e0b3,1e59ff46-479c-4ae1-b78c-93a3521d11f3 | , | https://web.fulcrumapp.com/photos/view?photos=392fc7b7-5e4b-4e8b-b0a1-fcec2486e0b3%2C1e59ff46-479c-4ae1-b78c-93a3521d11f3 | Concrete | Circular Joint | Drummy
9ce38657-386b-4a3a-8c59-f0bf5f12e84c | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-31 21:55:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 802 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27682 |  | 6513 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 802, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 300mm x 100mm. |  | Concrete shell segment has drummy concrete over an area of 300mm x 100mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P3 |  |  |  | Break out loose and damaged concrete. Engineer to assess damage to reinforcement and remediation required. All areas of damaged concrete shall be replaced with high strength concrete patch repairs including embedment of galvanic Cathodic Protection (CP) anodes. Corroded reinforcement that has not been removed shall be thoroughly cleaned of all corroded material. Where corroded reinforcement has been removed it should be replaced by welding a new length of N grade reinforcement of the same diameter to the remaining undamaged reinforcing bar. Or replacing the damaged bar with a new N grade bar of the same diameter as the removed bar. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | Scaffolding | - | Engineering Assessment Competent Supervisor |  |  | Delamination is still present. | no |  |  |  |  | c56792ab-6c69-4ff3-8a3b-eb43a5f2d4af,0c5a8554-9281-4b43-a252-6cdb8becebc3 | , | https://web.fulcrumapp.com/photos/view?photos=c56792ab-6c69-4ff3-8a3b-eb43a5f2d4af%2C0c5a8554-9281-4b43-a252-6cdb8becebc3 | Concrete | Circular Connection | Drummy |  | Circular Not reinforcement
3429bc62-e35d-461c-97fe-0033d24d713e | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 05:47:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 803 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85710 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 803, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 250mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order. | yes |  |  |  |  | fc854c55-43f7-4609-a7ea-9822fad5eec9 |  | https://web.fulcrumapp.com/photos/view?photos=fc854c55-43f7-4609-a7ea-9822fad5eec9 | Concrete | Circular Joint | Drummy
534a0b51-300f-43d0-8c63-75593fa30d79 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 05:45:55 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 804 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27074 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 804, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Medium Corrosion |  | Steel channel support bracket has Level 2 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Very minor corrosion | no |  |  |  |  | f0cfec66-b947-4a07-9816-c420e4d773d4 |  | https://web.fulcrumapp.com/photos/view?photos=f0cfec66-b947-4a07-9816-c420e4d773d4 | Steel | Channel Bracket | Corrosion-Surface
316e4fa7-1195-40d1-a13b-dd0a9ce1131d | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 23:40:38 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 806 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85711 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 806, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is still evident. Does not seem to have expanded. | no |  |  |  |  | f733e887-55e5-43b3-9b95-5608ee4e7e69 |  | https://web.fulcrumapp.com/photos/view?photos=f733e887-55e5-43b3-9b95-5608ee4e7e69 | Concrete | Circular Joint | Drummy
6181d9e6-32e0-4ef4-b55f-144f8ef36096 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 23:35:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 806 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 85712 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44874.2812 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 806, 12 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 Minor Corrosion |  | Steel channel support bracket has Level 2 Minor Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | On-Line | [6 empty] | Very minor corrosion | no |  |  |  |  | 6a197426-35f5-435c-8e01-5adfc791b158,6827f1c5-e2a1-44eb-9ab4-de097ec10fd2,22c5e210-46a1-4d83-b96c-c33ef8a81634 | ,, | https://web.fulcrumapp.com/photos/view?photos=6a197426-35f5-435c-8e01-5adfc791b158%2C6827f1c5-e2a1-44eb-9ab4-de097ec10fd2%2C22c5e210-46a1-4d83-b96c-c33ef8a81634 | Steel | Channel Bracket | Corrosion-Surface
42b250f6-4714-4206-8389-df4045b14367 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 05:35:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 809 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 85713 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 809, 2 O'Clock, Ring (Segmental Concrete)- Damage Affecting Single Rings | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Unrepaired hole on concrete shell with exposed reinforcement. |  | Unrepaired hole on concrete shell with exposed reinforcement. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | - | Not Specified | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Still to be treated. | no |  |  |  |  | 8674334c-864e-44aa-93da-f5501ca0509f,d484dfea-a7bb-4a75-b5d5-cb5d95a02476 | , | https://web.fulcrumapp.com/photos/view?photos=8674334c-864e-44aa-93da-f5501ca0509f%2Cd484dfea-a7bb-4a75-b5d5-cb5d95a02476 | Concrete | Reinforcement
11319b82-2711-4a9c-bb0a-3331193b9c9e | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 14 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 05:37:56 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 809 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85715 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 809, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order. | yes |  |  |  |  | 295400c6-0485-45d7-86d7-8b307f9a67df |  | https://web.fulcrumapp.com/photos/view?photos=295400c6-0485-45d7-86d7-8b307f9a67df | Concrete | Circular Joint | Drummy
de9268c4-0cb2-4a23-b77c-05d0981ab06c | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 8 |  |  |  | 2025-05-31 02:32:03 AEST | 2025-05-31 02:39:04 AEST | 30011704-user5@smec.com | james.stone@smec.com | 798 | 1 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Leak | 4 | [14 empty] | Adjacent or behind the support bracket. Possibly a faulty mounting recess. | [5 empty] | Active leak is depositing large amounts of salts on the bracket and bolts, the lighting fixture, cable tray and the adjacent fire pressure main. All are corroding badly | [18 empty] | SS |  | This defect should be addressed as a priority. Damage to the hardware in the tunnel, especially the water main, can have catastrophic consequences. See other defects in this and adjacent rings. | [5 empty] | 21d680d8-fa2d-4aa2-9326-aa0696fee073,d210ce30-c135-47f1-a95e-fd767e9db386 | , | https://web.fulcrumapp.com/photos/view?photos=21d680d8-fa2d-4aa2-9326-aa0696fee073%2Cd210ce30-c135-47f1-a95e-fd767e9db386 | Concrete | Misc (Pipes/Cable Tray/etc) | Leaks
19521370-b30f-42b4-a511-666813d07eb3 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 9 |  |  |  | 2025-05-31 02:00:25 AEST | 2025-05-31 02:03:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 801 | 3 |  |  | Cable tray and platform | [31 empty] | Cable tray and platform | [5 empty] | Advanced corrosion due to salt spray | [18 empty] | HM | [7 empty] | 53ec72cb-dc86-47cb-a682-0a08a5c137f8,2b687e9e-05ed-4150-8bff-c6d8c24c4cd8 | , | https://web.fulcrumapp.com/photos/view?photos=53ec72cb-dc86-47cb-a682-0a08a5c137f8%2C2b687e9e-05ed-4150-8bff-c6d8c24c4cd8 | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy
44f0b534-6845-46c9-83d1-669407762e0d | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 9 |  |  |  | 2025-05-31 02:14:50 AEST | 2025-05-31 02:15:43 AEST | 30011704-user5@smec.com | james.stone@smec.com | 800 | 3 |  |  | Cable tray | [31 empty] | Cable tray | [5 empty] | Medium corrosion | [18 empty] | Hm | [10 empty] | Steel | Misc (Pipes/Cable Tray/etc)
cc5fb830-8b4b-4dd6-b450-9740b7be2622 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 9 |  |  |  | 2025-05-31 02:26:37 AEST | 2025-05-31 02:28:37 AEST | 30011704-user5@smec.com | james.stone@smec.com | 798 | 1 |  |  | Pipe | [31 empty] | Pipe | [5 empty] | Advanced corrosion on underside of the pipe caused by leak at the bracket at 1 o clock | [18 empty] | HM | [7 empty] | 8312294c-61c1-4bf0-aff2-dc97ebb3f0b2 |  | https://web.fulcrumapp.com/photos/view?photos=8312294c-61c1-4bf0-aff2-dc97ebb3f0b2 | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Leaks
56e78fb5-4cf7-453e-99ab-39a9674652a3 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 9 |  |  |  | 2025-05-31 02:35:52 AEST | 2025-05-31 02:38:40 AEST | 30011704-user5@smec.com | james.stone@smec.com | 796 | 3 |  |  | Cable tray | [31 empty] | Cable tray | [5 empty] | Advanced corrosion in cable tray due to previous leak (inactive) | [18 empty] | HM | [7 empty] | dc38fe1e-4b27-4d0b-a438-862c7140767a |  | https://web.fulcrumapp.com/photos/view?photos=dc38fe1e-4b27-4d0b-a438-862c7140767a | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Leaks
e480d6bb-6197-4992-a6fe-055227cbdbf5 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 9 |  |  |  | 2025-05-31 03:10:52 AEST | 2025-05-31 03:13:54 AEST | 30011704-user5@smec.com | james.stone@smec.com | 793 | 3 |  |  | Cable tray and platform | [31 empty] | Cable tray and platform | [5 empty] | Advanced corrosion in the cable tray, with section losses. Platform has medium level of corrosion | [18 empty] | HM | [7 empty] | 0dad077a-1a18-4a94-8684-f23172dc703c,ee505f82-f686-4a36-8553-6a395c562d49,e5169e0a-abe8-46bd-8d7c-a2733504b653,75974e59-78da-4f2f-ba68-7b92fb6e011c | ,,, | https://web.fulcrumapp.com/photos/view?photos=0dad077a-1a18-4a94-8684-f23172dc703c%2Cee505f82-f686-4a36-8553-6a395c562d49%2Ce5169e0a-abe8-46bd-8d7c-a2733504b653%2C75974e59-78da-4f2f-ba68-7b92fb6e011c | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy
d77872f1-fb99-4850-8fa1-393dc6aa9c53 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 7 |  |  |  | 2025-05-31 21:58:01 AEST | 2025-05-31 21:59:56 AEST | 30011704-user5@smec.com | james.stone@smec.com | 798 | 2 |  | Segment Bolted Joint (Circle Joint) | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | SS | [7 empty] | b3154245-8e3e-45be-a054-d6b68ab62138,22fc3d19-bad3-4017-a4c8-1cf800f48e11 | , | https://web.fulcrumapp.com/photos/view?photos=b3154245-8e3e-45be-a054-d6b68ab62138%2C22fc3d19-bad3-4017-a4c8-1cf800f48e11 | Concrete | Circular Joint | Drummy
42edb9f2-058b-400b-9835-aad1b2b2c37b | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 7 |  |  |  | 2025-05-31 22:03:54 AEST | 2025-05-31 22:05:06 AEST | 30011704-user5@smec.com | james.stone@smec.com | 794 | 1 |  | Segment Bolted Joint (Circle Joint) | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [27 empty] | c1cf8e30-dd9f-41c1-b3d0-f31867e02b97,9f922f7a-82d1-44a5-9944-1c0ef8bc9d48,647401c9-cecf-437f-aa38-cf66fc4ed046 | ,, | https://web.fulcrumapp.com/photos/view?photos=c1cf8e30-dd9f-41c1-b3d0-f31867e02b97%2C9f922f7a-82d1-44a5-9944-1c0ef8bc9d48%2C647401c9-cecf-437f-aa38-cf66fc4ed046 | Concrete | Circular Joint | Drummy
3738823f-92ac-4abd-8358-fe127713b7c6 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 131c12f8-42fa-4fca-828a-09b38c961c69 | 9 |  |  |  | 2025-05-31 03:52:26 AEST | 2025-05-31 03:54:53 AEST | 30011704-user5@smec.com | james.stone@smec.com | 785 | 3 |  |  | Cable tray and platform | [31 empty] | Cable tray and platform | [5 empty] | Advanced corrosion in cable trays and platforms due to leak from the joint | [18 empty] | HM | [7 empty] | 65669ced-5765-4065-ad43-bd7f7342cc45,52574ae4-1237-48af-be05-eeecb148a30f,e65ecaf2-eb9d-4c17-bd33-e56d9780d5cf,b0f15bd5-a207-4fbe-a87c-58f8b9bd2562 | ,,, | https://web.fulcrumapp.com/photos/view?photos=65669ced-5765-4065-ad43-bd7f7342cc45%2C52574ae4-1237-48af-be05-eeecb148a30f%2Ce65ecaf2-eb9d-4c17-bd33-e56d9780d5cf%2Cb0f15bd5-a207-4fbe-a87c-58f8b9bd2562 | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Leaks
4b74ca1b-118f-4448-b305-796ef7eb96c4 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 05:29:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 811 | 2 | Steel Channel Bracket | Steel Channel Bracket |  | 27377 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 811, 2 o'clock. Steel Channel Support Bracket. |  |  |  | Cable tray has Level 3 - Medium Corrosion |  | Cable tray has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Corrosion no longer evident | yes |  |  |  |  | a48d326e-7f03-443c-95b8-99cd938237f8 |  | https://web.fulcrumapp.com/photos/view?photos=a48d326e-7f03-443c-95b8-99cd938237f8 | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Surface |  | Only Surface
becfa1f7-03da-4f22-8a12-de5b818ecd7d | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 23:29:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 813 | 12 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85716 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 813, 12 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination still evident. Does not appear to have enlarged | no |  |  |  |  | faa7db55-9e38-461b-839f-4399419cc80a,e02d86ab-b64a-4b45-ab3e-e1a7b300c38e | , | https://web.fulcrumapp.com/photos/view?photos=faa7db55-9e38-461b-839f-4399419cc80a%2Ce02d86ab-b64a-4b45-ab3e-e1a7b300c38e | Concrete | Radial Joint | Drummy
5e1d62cc-7651-4aa5-9aa3-0de38fe96fc2 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:53:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 814 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27075 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 814, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 3 Medium Corrosion Steel channel support bracket has Level 2 - Minor Corrosion up to 5% coverage |  | Channel anchor bolts have Level 3 Medium Corrosion Steel channel support bracket has Level 2 - Minor Corrosion up to 5% coverage | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Same condition | no |  |  |  |  | 1a67b3eb-263d-4684-93e5-08951b3771bb |  | https://web.fulcrumapp.com/photos/view?photos=1a67b3eb-263d-4684-93e5-08951b3771bb | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
0eaf7a46-9601-4f04-8511-f8a1d955c8d5 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:52:30 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 814 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 85719 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 814, 3 O'Clock, Steel Channel Bracket | Rupture | Rupture |  | Steel channel anchor bolt is missing. |  | Steel channel anchor bolt is missing. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Not Specified | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | GTS Specification. Concrete remediation crew. | Yes | On-Line | No | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Bolt missing on lower section | no |  |  |  |  | 38b8d32f-2e14-4540-bced-361ee97e5f2c |  | https://web.fulcrumapp.com/photos/view?photos=38b8d32f-2e14-4540-bced-361ee97e5f2c | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
742cf9e5-0a89-4775-ba6c-6b86bedcdebd | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 814 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85717 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 814, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor | [11 empty] | Concrete | Circular Joint | Drummy
c0320a8f-6405-4771-b3b7-a065455da805 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:49:43 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 818 | 4 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 85720 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 44874.34 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Likely (Failure within 2 years) |  | Likely (Failure within 2 years) | Ring 818, 4 O'Clock, Segmented Bolted Joint (Radial Joint) |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 250mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 250mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Delamination is not evident. Previous patch appears in good order. | yes |  |  |  |  | a79fe4cc-07a8-4fce-84b3-44a492b017b0 |  | https://web.fulcrumapp.com/photos/view?photos=a79fe4cc-07a8-4fce-84b3-44a492b017b0 | Concrete | Radial Joint | Drummy
9748b17e-135c-4614-81be-661efbdce5a4 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:45:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 819 | 2 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85722 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 9/11/2022 |  | 31/01/2024 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 819, 2 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Inactive leak from the interface between the circle joint grout pocket and the concrete shell. |  | Inactive leak from the interface between the circle joint grout pocket and the concrete shell. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Engineering Repair Methodology Required Competent Engineer |  |  | No evidence of leak. There is some trickles of epoxy bonding agent seen, but this is not a defect. | yes |  |  |  |  | 3a2d04e0-8628-4672-abdd-11673e76c6ba,9a03353e-3630-4e0d-a91c-982925da4725 | , | https://web.fulcrumapp.com/photos/view?photos=3a2d04e0-8628-4672-abdd-11673e76c6ba%2C9a03353e-3630-4e0d-a91c-982925da4725 | Concrete | Circular Joint | Leaks
c52a7bd2-d2d0-48ce-a9e8-1a411e98444f | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:36:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 820 | 7 | Grout Injection Hole | Grout Injection Hole |  | 68759 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Not Assessable(No Access) | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 820, 7 o'clock. Concrete Shell Segment - Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | loss of services | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer |  |  | Not accessible | [8 empty] | Concrete | Grout Hole,Reinforcement | Leaks
f0c70100-81c2-4923-ae39-ffab34012803 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:35:37 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 822 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85723 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 822, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order. | yes |  |  |  |  | 894e8b22-1ddf-4912-8551-73f75a820a99 |  | https://web.fulcrumapp.com/photos/view?photos=894e8b22-1ddf-4912-8551-73f75a820a99 | Concrete | Circular Joint | Drummy
e2db72f6-a7e7-4d76-b63a-dc566a578eb2 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:32:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 824 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85725 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 824, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order. | yes |  |  |  |  | fb4b0784-ccfd-46d5-969b-d3b940a8a429 |  | https://web.fulcrumapp.com/photos/view?photos=fb4b0784-ccfd-46d5-969b-d3b940a8a429 | Concrete | Circular Joint | Drummy
7401b986-ed3f-4735-97f6-b5ddfa608e62 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:31:26 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 824 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85724 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 824, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 300mm x 100mm and 400mm x 150mm. |  | Radial joint has Grout Delamination / Drummy Grout over two areas of 300mm x 100mm and 400mm x 150mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident. Previous patches appear in good order. | yes |  |  |  |  | 4c916d6f-9d36-4a8b-afc4-d1b51c512559,f5552c1f-6de7-47ac-920c-d1f137b0a6a1 | , | https://web.fulcrumapp.com/photos/view?photos=4c916d6f-9d36-4a8b-afc4-d1b51c512559%2Cf5552c1f-6de7-47ac-920c-d1f137b0a6a1 | Concrete | Radial Joint | Drummy
200467eb-a155-411c-80a3-d29f19c14291 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 825 | 8 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 68760 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 44540.459 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Bored Tunnel - Segment Bolted Joint (Radial Joint) - Ring 825, 8 o'clock. Concrete Shell Segment. |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | Circle joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. |  | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [15 empty] | Concrete | Circular Joint,Radial Joint | Drummy
6b504444-9d61-48a8-9b9f-18b79b81f5b8 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:29:20 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 825 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27076 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 825, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | Yes | Off-Line | Yes | Scaffolding | - | Condition Monitoring Competent Supervisor |  |  | Leak still inactive | no |  |  |  |  | f579beb7-296b-485d-8c7b-2c791dfbae62,ee951223-0074-44ac-8a67-b3a72d114100 | , | https://web.fulcrumapp.com/photos/view?photos=f579beb7-296b-485d-8c7b-2c791dfbae62%2Cee951223-0074-44ac-8a67-b3a72d114100 | Concrete | Grout Hole | Leaks |  | Not reinforcement
43f02b92-9638-47c7-81e0-e05f5abee702 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:27:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 826 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85726 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 826, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order. | yes |  |  |  |  | 48462af9-400c-4a35-833d-14e7ccb9b130 |  | https://web.fulcrumapp.com/photos/view?photos=48462af9-400c-4a35-833d-14e7ccb9b130 | Concrete | Circular Joint | Drummy |  | Circular joint not radial joint
30efb51d-32c7-4e08-b790-b463a64e2346 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:25:35 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 827 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68761 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 827, 4 o'clock. Concrete Shell Segment. - Hydrophyllic Joint Seal - Circle Joint | Shear failure of bolt | Shear failure of bolt |  | Joint seal (Circle joint) has Leak - Active at time of inspection. |  | Joint seal (Circle joint) has Leak - Active at time of inspection. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Previously listed under AIMS defect 30821 under incorrect AIMS quadrant. 30821 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. |  | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | SS |  | Leak does not seem active | yes |  |  |  |  | 7762ec59-c802-48d2-86e5-70e20ac3bed7 |  | https://web.fulcrumapp.com/photos/view?photos=7762ec59-c802-48d2-86e5-70e20ac3bed7 | Concrete | Circular Joint | Leaks
acc66a98-a959-419c-adc3-18ddc0975a18 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:23:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 828 | 5 | Steel Channel Bracket | Steel Channel Bracket |  | 27687 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 828, 5 o'clock. Steel Channel Support Bracket. |  |  |  | Cable tray has Level 3 - Medium Corrosion |  | Cable tray has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | All of the cable trays are in roughly the same condition. Much of what appears to be corrosion is ore dust. | no |  |  |  |  | b8dffc84-af25-4a15-bac4-c4fda3f6a71f |  | https://web.fulcrumapp.com/photos/view?photos=b8dffc84-af25-4a15-bac4-c4fda3f6a71f | Steel | Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface |  | Not Channel Brack
b96a9705-d07c-4588-b536-57aac13b0185 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:18:08 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 830 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68762 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint (Radial Joint) - Ring 830, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | Previously listed under AIMS defect 30823 under incorrect AIMS quadrant. 30823 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | loss of services | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident. Previous patch seems in good oreder. | yes |  |  |  |  | 1f1d4039-43a2-4add-acb7-dd552ef159d1 |  | https://web.fulcrumapp.com/photos/view?photos=1f1d4039-43a2-4add-acb7-dd552ef159d1 | Concrete | Circular Joint | Drummy |  | Not radial
2d17b859-35dd-40ec-b79f-8c8e1f335d8a | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:16:51 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 831 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 68763 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint (Radial Joint) - Ring 831, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Previously listed under AIMS defect 30825 under incorrect AIMS quadrant. 30825 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. | loss of services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident | yes |  |  |  |  | d0216da5-4d0b-4726-9d87-d33d0c3257ad |  | https://web.fulcrumapp.com/photos/view?photos=d0216da5-4d0b-4726-9d87-d33d0c3257ad | Concrete | Circular Joint,Radial Joint | Drummy
3aa99af6-6580-4ff6-951c-c61e85ffe176 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:45:46 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 831 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27077 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 831, 1 o'clock. Concrete Shell Segment - Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | Leak appears to be active. Slow seepage. | no |  |  |  |  | 4efc08d9-45fa-474f-8ab6-a0fa8f917c4d,688fb056-f4fb-4c4c-991c-fafe84cb680a,c4a482d6-c42a-4a53-ba1a-20529b41032b,af59cbc6-b4ee-40a5-b468-bd2b30887704 | ,,, | https://web.fulcrumapp.com/photos/view?photos=4efc08d9-45fa-474f-8ab6-a0fa8f917c4d%2C688fb056-f4fb-4c4c-991c-fafe84cb680a%2Cc4a482d6-c42a-4a53-ba1a-20529b41032b%2Caf59cbc6-b4ee-40a5-b468-bd2b30887704 | Concrete | Grout Hole | Leaks |  | Not reinfrocmeent
57e76eb9-a0bc-407a-bf1d-eddbd920a153 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 23:08:41 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 831 | 11 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27378 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 31/01/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 831, 11 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Inactive at time of inspection. |  | Grout injection hole has Leak Inactive at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P3 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | Working at Heights | Engineering Repair Methodology Required Competent Engineer |  |  | No leak evident. Previous markings crossed out indicating possible treatment has been performed. | no |  |  |  |  | bb2221be-8c1f-470e-9d74-352f4a25e846 |  | https://web.fulcrumapp.com/photos/view?photos=bb2221be-8c1f-470e-9d74-352f4a25e846 | Concrete | Grout Hole | Leaks |  | Not reinforcement
9308902d-6716-4ed3-9406-d5a970048f64 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:07:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 832 | 4 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27688 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7471 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Rare (Failure within 50 years) | Rare (Failure within 50 years) |  | Structure,Ring 832,4 O'Clock,Bolt, Nut, Washer,Identified in 2018 |  |  |  | Missing nut |  | Missing nut | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line | [6 empty] | Nut still missing | no |  |  |  |  | ab192c14-b254-4faa-9fc9-c78a24452dd8 |  | https://web.fulcrumapp.com/photos/view?photos=ab192c14-b254-4faa-9fc9-c78a24452dd8 | Steel | Channel Bracket-Bolt | Missing
98ec2ef5-85e7-4903-a840-5a243888e366 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 03:05:22 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 834 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 68764 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Bored Tunnel - Segment Bolted Joint (Circle Joint) - Ring 834, 4 o'clock. Concrete Shell Segment. | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Previously listed under AIMS defect 30828 under incorrect AIMS quadrant. 30828 marked as repaired and transferred to this AIMS inspection to reflect correct tunnel quadrant defect is located. |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order. | yes |  |  |  |  | 3fcad688-12e9-467a-986d-d75b6661e563 |  | https://web.fulcrumapp.com/photos/view?photos=3fcad688-12e9-467a-986d-d75b6661e563 | Concrete | Circular Joint | Drummy
a8d1b753-0b1c-4f08-8f79-fdf0dd2bb938 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-01 15:17:05 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 834 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 27078 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 834, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion Channel anchor bolts have Level 2 corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion Channel anchor bolts have Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | SS |  | Coating failure noted, with corrosion worse in those areas. Still overall minor | no |  |  |  |  | 4b4970f6-2564-4173-9a77-f0978e01e1c2,d05a7d43-6b79-48fc-84a9-1d8c4c9224bd,f2b1fde8-c7be-43ef-af88-0cbcd702f2e4,d070b8ff-e235-4a99-8ab5-d2be621b8cb9 | ,,, | https://web.fulcrumapp.com/photos/view?photos=4b4970f6-2564-4173-9a77-f0978e01e1c2%2Cd05a7d43-6b79-48fc-84a9-1d8c4c9224bd%2Cf2b1fde8-c7be-43ef-af88-0cbcd702f2e4%2Cd070b8ff-e235-4a99-8ab5-d2be621b8cb9 | Steel | Channel Bracket,Channel Bracket-Bolt | Coating Failure,Corrosion-Surface
c3148454-1f2f-41b1-b90c-f21738246aea | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:54:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 835 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85727 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 835, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Delamination not evident. Previous patch seems in good order. | yes |  |  |  |  | 2fbc1ce2-4d9e-400f-bac8-3f7b08d2a970 |  | https://web.fulcrumapp.com/photos/view?photos=2fbc1ce2-4d9e-400f-bac8-3f7b08d2a970 | Concrete | Circular Joint | Drummy
a7663157-b741-41d9-aaf6-6bf35c8525c9 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:50:36 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 836 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27689 |  | 6513 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 836, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace missing and refasten loose anchor bolts as per original approved design. | Steelwork Remediation Crew. | No | Off-Line | Yes | - | - | Maintenance Repair Competent Supervisor |  |  | Single bolt only still noted | no |  |  |  |  | 64602d6e-dac2-46c2-a3d4-c581119fff02 |  | https://web.fulcrumapp.com/photos/view?photos=64602d6e-dac2-46c2-a3d4-c581119fff02 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
41710811-4062-4b54-b28b-4391c644ac96 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:46:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 837 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27079 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 837,1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | Leak is very minor, but appears still active. | no |  |  |  |  | 10035fdb-4f70-4d90-92ca-19228210b621,ba98c1ee-da82-4995-bdbb-7321612943e9,81f1f015-1cf5-4c55-9e09-7ec47f9349df | ,, | https://web.fulcrumapp.com/photos/view?photos=10035fdb-4f70-4d90-92ca-19228210b621%2Cba98c1ee-da82-4995-bdbb-7321612943e9%2C81f1f015-1cf5-4c55-9e09-7ec47f9349df | Concrete | Grout Hole | Leaks |  | Not reinforcement
f3164352-a2b1-4da6-8aec-85e8bbe690c5 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 22:56:31 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 838 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27080 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 838, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Channel anchor bolts have Level 2 Medium Low Corrosion |  | Channel anchor bolts have Level 2 Medium Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | No change | no |  |  |  |  | 5b3bdd3b-fd1d-42cf-9717-7b60176e36ac,a1ec7f36-dff9-489c-a154-e849c2b1409b | , | https://web.fulcrumapp.com/photos/view?photos=5b3bdd3b-fd1d-42cf-9717-7b60176e36ac%2Ca1ec7f36-dff9-489c-a154-e849c2b1409b | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
aa72b23b-5d25-47e1-a66b-199c8f3a6d12 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:40:48 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 839 | 8 | Segment Bolted Joint (Radial Joint) |  | Segment Bolted Joint (Radial Joint) | 68765 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 44540.4792 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Bored Tunnel - Segment Bolted Joint (Radial Joint) - Ring 839, 8 o'clock. Concrete Shell Segment. |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Not accessible | [8 empty] | Concrete | Circular Joint,Radial Joint | Drummy
daa8ea7a-3f65-4b3d-89c7-f33d9eaec066 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 10 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:39:54 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 840 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 68766 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Possible (Failure within 5 Years) | Possible (Failure within 5 Years) |  | Ring 840, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 300mm x 300mm. |  | Concrete shell segment has drummy concrete over an area of 300mm x 300mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 |  | Not Specified | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | BHP WAIO standard drawing 000-S-12618. Concrete Remediation Crew. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor |  |  | Delamination is not evident. Patched areas seem to be in good order. | yes |  |  |  |  | 4a726dca-09cc-4aa3-9191-53f103048622 |  | https://web.fulcrumapp.com/photos/view?photos=4a726dca-09cc-4aa3-9191-53f103048622 | Concrete |  | Drummy |  | Not reinforcement
a12e90e5-dd5b-44fc-bbb7-ce40e7ae82fa | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 6 |  |  |  | 2025-05-30 02:43:56 AEST | 2025-05-30 02:47:24 AEST | 30011704-user5@smec.com | james.stone@smec.com | 838 | 3 |  | Steel Channel Bracket | [17 empty] | 3 | [6 empty] | Localised Corrosion EXT | [7 empty] | Channel bracket bolt | [5 empty] | Bolt and surround are corroding. Possibly due to proximity of water spray on conveyor | [18 empty] | SS | [7 empty] | 003f5f60-5497-490e-977f-4d0dcbd7c13f,d5832382-e9fa-4006-9363-1f53741757b3 | , | https://web.fulcrumapp.com/photos/view?photos=003f5f60-5497-490e-977f-4d0dcbd7c13f%2Cd5832382-e9fa-4006-9363-1f53741757b3 | Steel | Channel Bracket,Channel Bracket-Bolt
336af5d0-54db-4204-909f-73f165c687f9 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 6 |  |  |  | 2025-05-30 02:54:20 AEST | 2025-05-30 03:02:23 AEST | 30011704-user5@smec.com | james.stone@smec.com | 835 | 3 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [16 empty] | Drilling | 3 | [7 empty] | Test drilling location |  | Severity Level 2 |  |  | Unlikely (Failure within 20 years) |  | 4 x drill locations | [5 empty] | Test holes that have not been patched. Reinforcement is seen in one them. | [18 empty] | SS |  | Holes to patch | [5 empty] | 8425d80f-4640-424f-8d25-7963c090775b,d1b65e8b-75c1-4ce3-a8f2-5f1ca3f4baa2 | , | https://web.fulcrumapp.com/photos/view?photos=8425d80f-4640-424f-8d25-7963c090775b%2Cd1b65e8b-75c1-4ce3-a8f2-5f1ca3f4baa2 | Concrete | Reinforcement | Test Hole
322a1a70-40f6-45fc-a241-979b6d62e86f | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 5 |  |  |  | 2025-05-30 23:17:38 AEST | 2025-05-30 23:20:26 AEST | 30011704-user5@smec.com | james.stone@smec.com | 824 | 11 |  | Grout Injection Hole | [17 empty] | 2 | [7 empty] | Drummy patch | [6 empty] | Grout injection hole grout plug | [5 empty] | Grout plug is drummy and loose | [18 empty] | SS |  | Previously marked, but not on our list | [5 empty] | 2a2d77fb-7457-4d15-8d2e-11dbdc21ff13,b7e23ae2-1a2e-4989-94b1-ce2aa00d8c95 | , | https://web.fulcrumapp.com/photos/view?photos=2a2d77fb-7457-4d15-8d2e-11dbdc21ff13%2Cb7e23ae2-1a2e-4989-94b1-ce2aa00d8c95 | Concrete | Grout Hole | Drummy,Loose
57e7fa07-b3fb-4bda-a807-8e2b48e7a563 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | b6011d5e-37b6-4a15-819c-99c4b84f3c91 | 4 |  |  |  | 2025-06-01 15:19:39 AEST | 2025-06-01 15:21:52 AEST | 30011704-user5@smec.com | james.stone@smec.com | 833 | 9 |  |  | Previous marking UTL adjacent CP cable to rebar | [64 empty] | 7b030d71-d947-4c58-a9c0-51cd685be3a4 |  | https://web.fulcrumapp.com/photos/view?photos=7b030d71-d947-4c58-a9c0-51cd685be3a4 | Concrete | Circular Joint |  |  | Circular Joint - Not reinforcement
0bdc0d39-7c9a-473f-8b79-787072aa8b06 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:34:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 843 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85729 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 843, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident. Previous patch appears in good order | yes |  |  |  |  | 988871f0-dcf1-4f23-bcf0-4ff5d1efb2d4,8261f4ae-ea81-4cfe-b157-f32548352172 | , | https://web.fulcrumapp.com/photos/view?photos=988871f0-dcf1-4f23-bcf0-4ff5d1efb2d4%2C8261f4ae-ea81-4cfe-b157-f32548352172 | Concrete | Circular Joint | Drummy
4c288b01-708c-4545-a901-7a021f6a614b | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:31:53 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 843 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85728 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 843, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 400mm across both Ring 843 and 844. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 400mm across both Ring 843 and 844. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Not accessible | [8 empty] | Concrete | Circular Joint | Drummy
4542efe6-0fbf-403a-90f7-7b24b34a7d27 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:31:07 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 844 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85730 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 844, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident | yes |  |  |  |  | e4b923ec-16a8-4c19-a7eb-760dee2f8682 |  | https://web.fulcrumapp.com/photos/view?photos=e4b923ec-16a8-4c19-a7eb-760dee2f8682 | Concrete | Radial Joint | Drummy
21607b44-6f75-4726-ae6f-69aff8b27c39 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-01 14:44:40 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 844 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85731 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 844, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Drummy concrete around CP negative connection to rebar | [5 empty] | 90998106-1107-47cc-91da-9404fecfd6e0,c29a7a61-63a6-4ab5-8299-0cc71885d525 | , | https://web.fulcrumapp.com/photos/view?photos=90998106-1107-47cc-91da-9404fecfd6e0%2Cc29a7a61-63a6-4ab5-8299-0cc71885d525 | Concrete | Circular Joint,Reinforcement | Drummy
935430bf-6549-4a83-82f1-389b0f767016 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:47:18 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 844 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27081 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 844,1 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Engineering Repair Methodology Required Competent Supervisor |  |  | Leak appears to be still occurring. Strangely, does not appear to be water, dark stain. | no |  |  |  |  | 4ceabdb5-a690-4589-871b-dd758e7e6212,085f0461-f363-4665-aa44-3d4f07d2b144,b52e5cfa-16c8-4adc-9cfd-6dbe72993817 | ,, | https://web.fulcrumapp.com/photos/view?photos=4ceabdb5-a690-4589-871b-dd758e7e6212%2C085f0461-f363-4665-aa44-3d4f07d2b144%2Cb52e5cfa-16c8-4adc-9cfd-6dbe72993817 | Concrete | Grout Hole | Leaks |  | NOT REINFORCEMENT
da18ce8b-65fb-44ad-8f75-d9e2c6a138e9 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:25:27 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 845 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27379 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 845, 2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor |  |  | Leak is small, but seems to be slowly continuing. Also, more on 846 than 845 | no |  |  |  |  | 1fc221fc-03a5-4088-a950-99b25945f337,cacdf798-c6b5-4d1e-8187-a05778e54827 | , | https://web.fulcrumapp.com/photos/view?photos=1fc221fc-03a5-4088-a950-99b25945f337%2Ccacdf798-c6b5-4d1e-8187-a05778e54827 | Concrete | Circular Joint | Leaks |  | Not reinforcement
65272d25-ad7b-4f62-8623-7783457e4a0e | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:48:11 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 846 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27082 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 846, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Same condition | no |  |  |  |  | 83958348-9c1c-4be0-9a4a-b3950c1c6591,6007dfd9-7c74-4c88-a642-df47c7920322,f74c7e83-983e-4492-a062-ea3a1f7c84db | ,, | https://web.fulcrumapp.com/photos/view?photos=83958348-9c1c-4be0-9a4a-b3950c1c6591%2C6007dfd9-7c74-4c88-a642-df47c7920322%2Cf74c7e83-983e-4492-a062-ea3a1f7c84db | Steel | Channel Bracket | Corrosion-Surface
9c1480d3-7094-407e-8c85-a214c5887e0a | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-01 14:26:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 846 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27083 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 2 | Level 2 | Level 2 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 846, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolts have Level 2 Medium Low Corrosion 1 Anchor Bolt Missing |  | Channel anchor bolts have Level 2 Medium Low Corrosion 1 Anchor Bolt Missing | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace missing anchor bolts as per original design. | Monitor for further deterioration. Consider widescale coating / corrosion remediation project. Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | Scaffolding | Working at Heights | Replace Component Competent Supervisor | SS |  | Some coating failure around bolts, missing bolt still not placed | no |  |  |  |  | e3d3016a-d725-4069-b397-7a1e9986c18c,b5cfdf3b-7cdd-4a03-9186-59ad5585e016 | , | https://web.fulcrumapp.com/photos/view?photos=e3d3016a-d725-4069-b397-7a1e9986c18c%2Cb5cfdf3b-7cdd-4a03-9186-59ad5585e016 | Steel | Channel Bracket,Channel Bracket-Bolt | Coating Failure,Missing
42f7ede2-da90-439c-b445-33aa897a8c5e | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:21:02 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 846 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85732 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 846, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 300mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | This does not seem to be delamination. Joint sealant appears to be placed to address a leak, some overspray was returning a drummy sound | yes |  |  |  |  | a205d660-8a36-412d-b5da-4a0e695b27fa |  | https://web.fulcrumapp.com/photos/view?photos=a205d660-8a36-412d-b5da-4a0e695b27fa | Concrete | Circular Joint | Drummy,Leaks
f3a83a78-bf58-447f-b46d-275f4160bab8 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:10:57 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 847 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27380 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 847, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Cable tray has Level 3 - Medium Corrosion |  | Cable tray has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Affected section appears to have been replaced | yes |  |  |  |  | 08cd9ee7-e2ab-4b45-ba57-eddc87319e5a |  | https://web.fulcrumapp.com/photos/view?photos=08cd9ee7-e2ab-4b45-ba57-eddc87319e5a | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
a50ab87a-22ec-4245-9eaa-f18872027eb8 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:08:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 848 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27690 |  | 6513 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 848, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace missing and refasten loose anchor bolts as per original approved design. | Steelwork Remediation Crew. | No | Off-Line | Yes | - | - | Maintenance Repair Competent Supervisor |  |  | Still only 1 bolt on lower section | no |  |  |  |  | 9f8d9d64-a6e6-4637-882e-caca92cd5ec3 |  | https://web.fulcrumapp.com/photos/view?photos=9f8d9d64-a6e6-4637-882e-caca92cd5ec3 | Steel | Channel Bracket,Channel Bracket-Bolt | Missing
bfc9dfe7-c77b-4bf4-9bb2-0cb38c60a6b3 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:54:12 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 850 | 1 | Steel Channel Bracket | Steel Channel Bracket |  | 27084 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7381 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 850, 1 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | HM |  | Fixings are showing corrosion. Bolts corrosion level 3 and bracket corrosion level 2 | yes |  |  |  |  | 89da0a90-f2be-4572-a740-c7dc37b74d04,48a68b6c-077e-437c-928c-465e719e76b7,6f954e89-cd35-4281-bedc-d883f69ce055,9c190259-7198-4ffd-99cf-c94dc1592316 | ,,, | https://web.fulcrumapp.com/photos/view?photos=89da0a90-f2be-4572-a740-c7dc37b74d04%2C48a68b6c-077e-437c-928c-465e719e76b7%2C6f954e89-cd35-4281-bedc-d883f69ce055%2C9c190259-7198-4ffd-99cf-c94dc1592316 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
64fd9a81-faf1-4b89-845f-899e750961d2 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 22:43:52 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 850 | 11 | Steel Channel Bracket | Steel Channel Bracket |  | 68767 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44540.4833 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 850, 11 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 5% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. |  | Steel channel support bracket has Level 2 - Minor Corrosion up to 5% coverage. Channel anchor bolts have Level 2 - Medium Low Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Corrosion on bracket is very mild, slightly more advanced on the bolts | no |  |  |  |  | 9504e466-fa9a-47fa-947b-6462dd6f4119,8be0fa1f-691a-4bf3-808e-3a519d9186a6 | , | https://web.fulcrumapp.com/photos/view?photos=9504e466-fa9a-47fa-947b-6462dd6f4119%2C8be0fa1f-691a-4bf3-808e-3a519d9186a6 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Surface
3dcd4291-72b8-4e8d-9c60-e2b329b5083e | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 22:41:42 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 850 | 12 | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | 85738 |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 614-860) | SIM-FixedPlant |  |  | 44874.3935 |  |  | No | Missing | [12 empty] | Severity Level 4 | Severity Level 4 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 850, 12 O'Clock, Ring (Segmental Concrete)-Damage Affecting Single Rings |  |  |  | Concrete shell segment has Cracking - Cracking extending 0.3m and 0.25mm in width. |  | Concrete shell segment has Cracking - Cracking extending 0.3m and 0.25mm in width. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | Crack is visible, but does not seem to have extended or widened | no |  |  |  |  | a544ab65-595a-4a48-9f1a-96e16c2b4f4e |  | https://web.fulcrumapp.com/photos/view?photos=a544ab65-595a-4a48-9f1a-96e16c2b4f4e | Concrete | Middle of Panel | Crack |  | Middle of Panel
2df6207a-f0f6-4803-86a8-e4d850d4ceff | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:02:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 850 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27691 |  | 6513 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Loose Bolt |  | Loose Bolt | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 850, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Channel anchor bolt is missing. | Channel anchor bolt is missing. |  | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Replace missing and refasten loose anchor bolts as per original approved design. | Steelwork Remediation Crew. | No | Off-Line | Yes | - | - | Maintenance Repair Competent Supervisor |  |  | Bolt has been placed | yes |  |  |  |  | aba46d0b-7f9f-48a3-a85b-608173078ede |  | https://web.fulcrumapp.com/photos/view?photos=aba46d0b-7f9f-48a3-a85b-608173078ede | Steel | Channel Bracket,Channel Bracket-Bolt | Loose,Missing
9d86cd8a-86b1-4ea0-aef8-823ebf0c51cd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 02:01:14 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 850 | 3 | Hydrophilic Joint Seal (Circle Joint) |  | Hydrophilic Joint Seal (Circle Joint) | 85736 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Additional Components | Additional Components |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 850, 3 O'Clock, Hydrophyllic Joint Seal (Circle Joint) | Failure to seal joint | Failure to seal joint |  | Circle joint seal has Leak Active at time of inspection. |  | Circle joint seal has Leak Active at time of inspection. | Water leak through joint, leading to accelerated concrete damage (locally). | Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | On-Line | No | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Fine leak still noted | no |  |  |  |  | b844287a-846a-46c7-be30-5732966aeade,8e323ad1-b6f1-46ac-a230-5e1f3cfbb899 | , | https://web.fulcrumapp.com/photos/view?photos=b844287a-846a-46c7-be30-5732966aeade%2C8e323ad1-b6f1-46ac-a230-5e1f3cfbb899 | Concrete | Circular Joint | Leaks
ac91ac91-fbb6-4ac7-9863-9e8a88e9575a | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:59:34 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 850 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85733 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 850, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination is not evident | yes |  |  |  |  | ae4591f2-45e7-40d0-95b5-98e83422e868 |  | https://web.fulcrumapp.com/photos/view?photos=ae4591f2-45e7-40d0-95b5-98e83422e868 | Concrete | Circular Joint | Drummy |  | Circular Joint not Radial Joint
e54eb539-429a-4c1f-b3e7-dcf940f932fb | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-27 20:13:19 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 851 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27381 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 851, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Cable tray has Level 3 - Medium Corrosion |  | Cable tray has Level 3 - Medium Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [15 empty] | Steel | Channel Bracket,Misc (Pipes/Cable Tray/etc) | Corrosion-Heavy,Corrosion-Surface
3a752242-c4c2-4047-a16c-a86edddb980c | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-02 00:56:59 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 852 | 1 | Grout Injection Hole | Grout Injection Hole |  | 85741 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 852, 1 O'Clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has leak - active at time of inspection. |  | Grout injection hole has leak - active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | - | Loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Notification 437157510 was raised for GTS to prepare appropriate engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Grout injection hole leak appears to have stopped, with large amounts of salt deposited on wall. Note salt deposits have built up on fire pressure main. Should be assessed for remaining life. | no |  |  |  |  | c5aad5a0-c8a4-4277-925c-be5766e1f4d3,a4698240-3839-423b-8711-5cf53af97061,820a6810-b375-4810-9cfe-c94bc82485f7,5b8a25be-831c-48da-a882-3e8402f47fa2,32ec9547-1d77-453a-9dcc-2e5de84e0fe5,f2c2b18e-2b92-4da4-ace5-b70a7d2150f8 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=c5aad5a0-c8a4-4277-925c-be5766e1f4d3%2Ca4698240-3839-423b-8711-5cf53af97061%2C820a6810-b375-4810-9cfe-c94bc82485f7%2C5b8a25be-831c-48da-a882-3e8402f47fa2%2C32ec9547-1d77-453a-9dcc-2e5de84e0fe5%2Cf2c2b18e-2b92-4da4-ace5-b70a7d2150f8 | Concrete | Grout Hole | Leaks
b1192069-4688-43a7-b6aa-5a4fead41aa4 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:43:39 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 852 | 4 | Segment Bolted Joint (Radial Joint) | Segment Bolted Joint (Radial Joint) |  | 85739 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 852, 4 O'Clock, Segmented Bolted Joint (Radial Joint) | Shear failure of bolt | Shear failure of bolt |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. |  | Radial joint has Grout Delamination / Drummy Grout over an area of 300mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. | Loss of production and services | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | Delamination not evident | yes |  |  |  |  | 1465abf7-0511-4a7e-82c3-3a3a76ff97c5,31aff4ce-7bf1-4752-92fc-c2d4c54bc375 | , | https://web.fulcrumapp.com/photos/view?photos=1465abf7-0511-4a7e-82c3-3a3a76ff97c5%2C31aff4ce-7bf1-4752-92fc-c2d4c54bc375 | Concrete | Circular Joint | Drummy |  | Circular Joint not Radial
f24aa8db-ced3-4f87-b5b4-e096f0396bb9 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:39:28 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 853 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85742 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 853, 4 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 300mm x 100mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | 30/01/2024 AC: As per agreed with GTS Structural Engineer (JZ), monitor. |  | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Concrete Remediation Crew. Structural Engineer. | Yes | Off-Line | Yes | Walkway | - | Condition Monitoring Competent Supervisor |  |  | This is not delamination. Overspray of some build product has left a layer that sounds drummy. Concrete is not affected. | yes |  |  |  |  | 2d951471-5498-4244-b0d0-438ae558350c,6263a192-1f79-41d8-9870-f6fd7728f559 | , | https://web.fulcrumapp.com/photos/view?photos=2d951471-5498-4244-b0d0-438ae558350c%2C6263a192-1f79-41d8-9870-f6fd7728f559 | Concrete | Circular Joint | Drummy
a27de921-8021-42fc-8fe3-c5337f8a519c | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:35:13 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 854 | 12 | Steel Channel Bracket | Steel Channel Bracket |  | 85743 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 44874.4031 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 854, 12 O'Clock, Steel Channel Bracket |  |  |  | Channel anchor bolts have Level 2 Corrosion. |  | Channel anchor bolts have Level 2 Corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line | [6 empty] | No access currently | [8 empty] | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
4d6da948-e299-43f3-b128-afded06dcfe6 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:34:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 854 | 2 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27692 |  | 6513 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Other |  | Other | Missing Bolt(s) | Missing Bolt(s) | Missing Bolt(s) | Health & Safety | Health & Safety |  | Missing Component | Missing Component |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 854, 2 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has missing bolts. |  | Steel channel support bracket has missing bolts. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 | 61ce4cea-a557-48c9-bf55-6d582ed81b90,5b5d98db-c62c-425d-92ec-7790992ed957 | , | https://web.fulcrumapp.com/photos/view?photos=61ce4cea-a557-48c9-bf55-6d582ed81b90%2C5b5d98db-c62c-425d-92ec-7790992ed957 | Replace missing fastener as per original design specification | Steelwork Remediation Crew. | No | Off-Line | Yes | Scaffolding | - | Maintenance Repair Competent Supervisor |  | Nut is missing | Bolts still missing | no |  |  |  |  | d6be7f7c-fce6-4657-8f0e-97992bf197a4 |  | https://web.fulcrumapp.com/photos/view?photos=d6be7f7c-fce6-4657-8f0e-97992bf197a4 | Steel | Channel Bracket-Bolt | Missing |  | Onyl Bolt
4b045063-fd47-4715-aef7-400253e91aff | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:33:29 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 854 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27085 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  | 31/01/2024 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 4 | Condition Rating 4 | Condition Rating 4 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 854, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Joint seal (Circle joint) has Leak Active at time of inspection. |  | Joint seal (Circle joint) has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | change in HSE to financial because of the long run repair cost | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer |  |  | Leakage not evident at time of inspection | yes |  |  |  |  | c44405fb-d87f-457e-adb2-104d45edc3bb,dafcad3b-67ab-420a-825b-dd3a4e60a8c3 | , | https://web.fulcrumapp.com/photos/view?photos=c44405fb-d87f-457e-adb2-104d45edc3bb%2Cdafcad3b-67ab-420a-825b-dd3a4e60a8c3 | Concrete | Circular Joint | Leaks |  | NOt Reinforcement
420d1c52-32d8-451d-8039-cfc21c9945b0 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:30:49 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 854 | 2 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  | 27383 |  | 6513 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Repair Verified | 20/10/2021 |  | 16/02/2023 | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 854,2 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout Delamination / debonding at circle segment bolted joints over 200mm x 200mm area. |  | Grout Delamination / debonding at circle segment bolted joints over 200mm x 200mm area. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Perform UT to find the extent of the delamination. Assess the results and develop a engineering repair detail as required | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Engineering Assessment Competent Supervisor |  | No change | No delamination noted. | yes |  |  |  |  | f9bd514b-2b03-4b17-a437-f9dffbdb2aa4,680d98d9-30bf-4134-9274-3b2e7fe59002 | , | https://web.fulcrumapp.com/photos/view?photos=f9bd514b-2b03-4b17-a437-f9dffbdb2aa4%2C680d98d9-30bf-4134-9274-3b2e7fe59002 | Concrete | Radial Joint | Drummy |  | Radial Joint - Not reinforcement
8a47921b-09ad-4bfc-8951-8e906d32110b | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 22:26:10 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 858 | 11 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27086 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 3 | Level 3 | Level 3 | Financial | Financial |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. >= US$2 million, < US$50 million |  | Severity Level 2. >= US$2 million, < US$50 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 858, 11 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support has level 3 corrosion at 5% coverage. Channel anchor bolts have level 3 corrosion. |  | Steel channel support has level 3 corrosion at 5% coverage. Channel anchor bolts have level 3 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Repair anchor bolts as per BHP standard drawing 000-S-12598. | Monitor for further deterioration. Consider widescale coating / corrosion remediation project. Steelwork Remediation Crew. BHPIO SPEC-000-S-0061 and Steel Corrosion Repair Guideline 0136559. Steelwork repair drawing set. 000-S-12034/5 000-S-12598/0 000-S-12619/0 000-S-12620/0 000-S-12621/0 000-S-12622/0 000-S-12623/0 Risk assess corrosion repairs in tunnel and protection of services and plant. Approval by BHP required. | No | Off-Line | Yes | - | Working at Heights | Standard Repair Detail Competent Supervisor | SS |  | Corrosion is extremely mild, most effects seem to be ore dust | no |  |  |  |  | e85b4097-43e3-4a98-ba41-02a748cf3395,acc66b7d-0c94-4d60-83a2-5ddc1ed627a0 | , | https://web.fulcrumapp.com/photos/view?photos=e85b4097-43e3-4a98-ba41-02a748cf3395%2Cacc66b7d-0c94-4d60-83a2-5ddc1ed627a0 | Steel | Channel Bracket,Channel Bracket-Bolt | Corrosion-Heavy,Corrosion-Surface
bb2b5c32-5f3b-40eb-a830-0fe3efee55a3 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:24:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 858 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  | 27693 |  | 7768 | UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Loose Bolt |  | Loose Bolt | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 858, 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has missing bolts. |  | Steel channel support bracket has missing bolts. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 30/01/2024 AC: As per agreed with GTS Structural Engineer (James Zheng), monitor. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Rare Likelihood of failure, resulting in a Priority 4. | Loss of services. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | Steelwork Remediation Crew. | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor |  | No change | Bolt head cut off | no |  |  |  |  | 0a143a2e-03f0-42fb-a3c8-cd60c6366776,93da9803-9500-4ccd-99e2-b711c0cf056f,6f2bbb8a-8cb6-4667-b875-9075cd233587 | ,, | https://web.fulcrumapp.com/photos/view?photos=0a143a2e-03f0-42fb-a3c8-cd60c6366776%2C93da9803-9500-4ccd-99e2-b711c0cf056f%2C6f2bbb8a-8cb6-4667-b875-9075cd233587 | Steel | Channel Bracket,Channel Bracket-Bolt | Loose,Missing
c9e11ebb-3c99-4a4e-b71e-e10b85f23828 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-06-01 13:53:47 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 859 | 9 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85744 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 859, 9 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 500mm x 300mm over both Ring 858 and 859. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 500mm x 300mm over both Ring 858 and 859. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Delaminated at 9 o’clock join. | yes |  |  |  |  | 90d6cccf-53b1-4f7c-81ed-bcd27c04188d,39c75c7f-e343-463d-a49d-14b802d9d0cc,7d8a1496-53aa-4ec1-a779-7b882953e557 | ,, | https://web.fulcrumapp.com/photos/view?photos=90d6cccf-53b1-4f7c-81ed-bcd27c04188d%2C39c75c7f-e343-463d-a49d-14b802d9d0cc%2C7d8a1496-53aa-4ec1-a779-7b882953e557 | Concrete | Circular Joint | Drummy
7edb29a9-1d69-4cf6-9c13-c9d89dc162f9 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 22:10:25 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 860 | 12 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  | 85745 |  | 7768 | UHT001 | Bored Tunnel (Ring 614 -860) | SIM-FixedPlant | Nelson Point | Assessed | 9/11/2022 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 860, 12 O'Clock, Segmented Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350mm x 300mm over both Ring 859 and 860. Spalling has also occurred. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 350mm x 300mm over both Ring 859 and 860. Spalling has also occurred. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | 1. Further engineering review required to develop appropriate engineering repair methodology. 2. Repair damaged area of concrete as per approved engineering repair methodology. Refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | Walkway | - | Standard Repair Detail Competent Supervisor |  |  | Delamination and edge spall still evident | no |  |  |  |  | 1af3ace5-7eff-4329-a31c-8aff320a3e8f,df463dd3-334b-4e5d-8b0c-3e5e70b5652d | , | https://web.fulcrumapp.com/photos/view?photos=1af3ace5-7eff-4329-a31c-8aff320a3e8f%2Cdf463dd3-334b-4e5d-8b0c-3e5e70b5652d | Concrete | Circular Joint | Drummy,Surface Damage
69b2867f-aaea-49ca-ab3f-a912d1514ddf | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 13 |  |  |  | 2025-05-27 20:13:19 AEST | 2025-05-30 01:19:01 AEST | sandy.tulloch@smec.com | james.stone@smec.com | 860 | 3 | Steel Channel Bracket | Steel Channel Bracket |  | 27384 |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 614-860) | SIM-FixedPlant |  |  | 43656.7421 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 860, 3 o'clock. Steel Channel Support Bracket. |  |  |  | Steel channel support bracket has Level 2 - Medium-Low Corrosion |  | Steel channel support bracket has Level 2 - Medium-Low Corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | 077bce82-36d2-4e2d-8056-492e05a400e0 |  | https://web.fulcrumapp.com/photos/view?photos=077bce82-36d2-4e2d-8056-492e05a400e0 |  |  | Yes | Off-Line | [5 empty] | Unsure about the location taken in photograph | No corrosion noted | yes |  |  |  |  | 8bd1b49f-cf04-4367-976a-0e6a854b0df6,2f53b288-548f-490f-aa4c-24a88e3b9c33,bc4e831c-d5ca-4da4-97c1-b164951bfd00,b0ddd17d-d7e0-42e3-9936-faadaca4dfa7,16dd34ca-31a5-4241-9471-d6d855f68fdf,d6c04fe2-f0f6-4346-b981-f54d235d81dc | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=8bd1b49f-cf04-4367-976a-0e6a854b0df6%2C2f53b288-548f-490f-aa4c-24a88e3b9c33%2Cbc4e831c-d5ca-4da4-97c1-b164951bfd00%2Cb0ddd17d-d7e0-42e3-9936-faadaca4dfa7%2C16dd34ca-31a5-4241-9471-d6d855f68fdf%2Cd6c04fe2-f0f6-4346-b981-f54d235d81dc | Steel | Channel Bracket | Corrosion-Heavy,Corrosion-Surface
1d5d0a80-6c62-4a91-83b9-43c85e97d5be | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 7 |  |  |  | 2025-05-30 01:52:31 AEST | 2025-05-30 01:56:28 AEST | 30011704-user5@smec.com | james.stone@smec.com | 851 | 1, 3 |  | Hydrophilic Joint Seal (Circle Joint) | [17 empty] | 2 | [7 empty] | Possible leak | [6 empty] | Two locations, spreading from joint | [5 empty] | Very small amount of moisture noted at two locations, emanating from joint. | [18 empty] | SS | [7 empty] | 6dba0b3d-429d-4271-b280-00af8b3b7e7d,13d13001-7c79-4a62-a73e-50082d79d555,cdadcf12-d2e9-434c-9064-768652e906ae,21b4b803-f902-43a8-9a0c-55b6451f90f3 | ,,, | https://web.fulcrumapp.com/photos/view?photos=6dba0b3d-429d-4271-b280-00af8b3b7e7d%2C13d13001-7c79-4a62-a73e-50082d79d555%2Ccdadcf12-d2e9-434c-9064-768652e906ae%2C21b4b803-f902-43a8-9a0c-55b6451f90f3 | Concrete | Circular Joint | Leaks
4bf6d7b6-da46-4f96-878e-4aef6dbed6e6 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 6 |  |  |  | 2025-05-30 22:10:39 AEST | 2025-05-30 22:15:08 AEST | 30011704-user5@smec.com | james.stone@smec.com | 860 | 12 | [19 empty] | 2 | [7 empty] | Movement | [6 empty] | Through middle of anchor grout pockets | [5 empty] | 0.2mm crack through middle of anchor pocket grout patches. Indicates slight movement in this terminal ring. | [18 empty] | SS | [7 empty] | 01a3ff99-6c0d-4b48-bfeb-ff6a623bd5ad,f238aec1-7293-4560-9c74-95093ea24354,cef9265f-bb07-4bb1-85a7-36aeeb1b393a | ,, | https://web.fulcrumapp.com/photos/view?photos=01a3ff99-6c0d-4b48-bfeb-ff6a623bd5ad%2Cf238aec1-7293-4560-9c74-95093ea24354%2Ccef9265f-bb07-4bb1-85a7-36aeeb1b393a | Concrete | Radial Joint | Crack |  | Radial Joint
f6f4f776-266e-43b8-99b7-40b9fe753093 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 6 |  |  |  | 2025-05-30 22:15:21 AEST | 2025-05-30 22:20:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 860 | 11 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [17 empty] | 2 | [7 empty] | Movement | [6 empty] | At segment edge, adjacent CP junction enclosure | [5 empty] | Spall of 250x250 mm, appears due to movement clash at edges | [18 empty] | SS |  | Has been previously marked, but is not in provided defect list | [5 empty] | 1038523a-55a8-49e3-ba00-6fa4e31e2708,1446dd7d-a9b5-47de-840a-93db140455c9 | , | https://web.fulcrumapp.com/photos/view?photos=1038523a-55a8-49e3-ba00-6fa4e31e2708%2C1446dd7d-a9b5-47de-840a-93db140455c9 | Concrete | Circular Joint | Surface Damage |  | Circualr Joint
5b9ae53f-f738-46f9-a3be-3e69de9950e0 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 6 |  |  |  | 2025-05-30 22:30:48 AEST | 2025-05-30 22:32:38 AEST | 30011704-user5@smec.com | james.stone@smec.com | 857 | 12 |  | Ring (Segmental Concrete) - Damage Affecting Single Ring | [17 empty] | 2 | [14 empty] | Bolted connections anchor pocket grout |  |  |  |  | Radial joint has Grout Delamination / Drummy Grout over an area of 200mm x 200mm. | [19 empty] | SS |  | Sone drumminess, no spall | [5 empty] | 88ea98b9-2181-46b4-8d33-d53bdc9008b1,d430ee71-d7cb-478a-a0b3-7a1b1e090014 | , | https://web.fulcrumapp.com/photos/view?photos=88ea98b9-2181-46b4-8d33-d53bdc9008b1%2Cd430ee71-d7cb-478a-a0b3-7a1b1e090014 | Concrete | Radial Joint | Drummy,Surface Damage
7bfc90f8-9d1c-4a24-95f5-18d329b1bf63 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 3 |  |  |  | 2025-06-02 00:49:56 AEST | 2025-06-02 00:51:12 AEST | 30011704-user5@smec.com | james.stone@smec.com | 846 | 1 |  | Segment Bolted Joint (Circle Joint) | [32 empty] | Concrete shell |  |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 100mm x 100mm. | [19 empty] | HM | [7 empty] | a224c58c-147d-410e-897e-00faac994b84,521b338e-acca-41f7-8383-4260bba4d54e | , | https://web.fulcrumapp.com/photos/view?photos=a224c58c-147d-410e-897e-00faac994b84%2C521b338e-acca-41f7-8383-4260bba4d54e | Concrete | Circular Joint | Drummy
c7ecd9fc-b9c6-4ae6-bb76-c9e1b41d4f32 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 253 | 2 | Steel Channel Bracket | Steel Channel Bracket |  |  |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 10/07/2019 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Almost Certain (Failure within 1 year) |  | Almost Certain (Failure within 1 year) | Ring 253, 2 O'Clock, Cable Tray |  |  |  | Cable tray has Level 4 corrosion. |  | Cable tray has Level 4 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 3 | [5 empty] | No | Off-Line |  |  |  |  | SS |  | No change | no | yes | P4 | yes | Suggest update priority and risk to low. | 6542efdb-6cbe-4132-8adc-7cc76f562702,44ae40f8-88d6-4f0f-aa98-8ab6683ccf3a | , | https://web.fulcrumapp.com/photos/view?photos=6542efdb-6cbe-4132-8adc-7cc76f562702%2C44ae40f8-88d6-4f0f-aa98-8ab6683ccf3a | Steel | Channel Bracket | Corrosion-Heavy
de3c3b0b-de3a-4777-8b9c-9ef8e140c1b3 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 318 | 11 | Steel Channel Bracket | Steel Channel Bracket |  |  |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 18/06/2022 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 318, 11 O'Clock, Steel Channel Bracket |  |  |  | Steel channel support bracket has Level 2 corrosion. |  | Steel channel support bracket has Level 2 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Steel channel bracket is heavily corroded and must be replaced. Level 4 corrosion. | yes | no | P2 | no |  | dc99e5e8-f8cd-4045-a94b-1514d0afe38b,bb48fcf7-ecf5-4ea3-8497-e9e1f3424a1e,13448950-cafa-43fe-89f7-25b5dfee2b8a | ,, | https://web.fulcrumapp.com/photos/view?photos=dc99e5e8-f8cd-4045-a94b-1514d0afe38b%2Cbb48fcf7-ecf5-4ea3-8497-e9e1f3424a1e%2C13448950-cafa-43fe-89f7-25b5dfee2b8a | Steel | Channel Bracket | Corrosion-Heavy
b0b47953-a806-4bbb-b346-e309a40cf0b2 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 534 | 2 | Steel Channel Bracket | Steel Channel Bracket |  |  |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 400-613) | SIM-FixedPlant |  |  | 18/09/2024 |  |  | No | Missing | [12 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Ring 534, 2 O'clock, Steel Channel Bracket and Anchor Bolts |  |  |  | Steel channel support bracket has Level 1 corrosion around the anchor bolts. Channel anchor bolts have Level 1 corrosion. |  | Steel channel support bracket has Level 1 corrosion around the anchor bolts. Channel anchor bolts have Level 1 corrosion. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Severe level 5 corrosion due to the active leak at the grout hole. | yes | no | P2 |  |  | 879e381a-27ae-4e14-bdc3-748ea3f11f1e,a2487185-90f8-4a29-8515-2c831d79021b | , | https://web.fulcrumapp.com/photos/view?photos=879e381a-27ae-4e14-bdc3-748ea3f11f1e%2Ca2487185-90f8-4a29-8515-2c831d79021b | Steel | Channel Bracket | Corrosion-Heavy |  | Corrosion heavy
fdfd1a40-8015-492c-ad73-b6ed0237bfd6 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 116 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  |  |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 116, 3 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineers (VS), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | HM |  | Severe corrosion to the steel channel bracket. | no | yes | P2 |  |  | 8559e52e-0689-4b6b-b847-2f88bd75e8b7,f8fab306-d703-4e0b-bf40-ed88155bb797,c4398150-350e-44fa-942c-7fc43b6cddf4,164c42db-4875-4db6-a9dc-9a4e9b84a96f,f5857d2a-ccc2-4df9-9260-0ce16a4875df,9ba48e91-858a-4bee-ab21-5dab1b0e6149 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=8559e52e-0689-4b6b-b847-2f88bd75e8b7%2Cf8fab306-d703-4e0b-bf40-ed88155bb797%2Cc4398150-350e-44fa-942c-7fc43b6cddf4%2C164c42db-4875-4db6-a9dc-9a4e9b84a96f%2Cf5857d2a-ccc2-4df9-9260-0ce16a4875df%2C9ba48e91-858a-4bee-ab21-5dab1b0e6149 | Steel | Channel Bracket | Corrosion-Heavy |  | Not reinforcement
d3441148-d829-477d-8e44-ba424255fa30 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 120 | 7 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  |  |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Repair Verified | 5/10/2022 |  |  | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 120, 7 o'clock. Concrete Liner Panel. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Hydrophilic Joint Seal (Radial) has Leak - Active at time of inspection. |  | Hydrophilic Joint Seal (Radial) has Leak - Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Rare Likelihood of failure, resulting in a Priority 3. | loss of production and services | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Engineering Repair Methodology Required Competent Engineer | SS |  | The curved footing bracket is showing advanced corrosion. Salt deposits in the area due to segment groput hole leak. The leak is inactive at the time of inspection. | no | no | P4 | yes | Suggest reducing priority to P3 | 2b268461-d53a-45fd-adac-98c18e5a5825,c42c0ec9-73ef-4c70-8dfa-813242dde071,daa25e5c-2ff1-4544-a399-517623e169e0,bd3ff3a5-9c77-4b37-a62d-75446c36d17a | ,,, | https://web.fulcrumapp.com/photos/view?photos=2b268461-d53a-45fd-adac-98c18e5a5825%2Cc42c0ec9-73ef-4c70-8dfa-813242dde071%2Cdaa25e5c-2ff1-4544-a399-517623e169e0%2Cbd3ff3a5-9c77-4b37-a62d-75446c36d17a | Steel | Conveyor Support | Corrosion-Heavy |  | Conveyor Support
1db0c3d8-63dc-45da-95ab-25a376c86c2e | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 54 | 1 | Steel Channel Bracket | Steel Channel Bracket |  |  |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 54, 1 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel bracket has Level 3 - Medium Corrosion up to 25% coverage. |  | Steel channel bracket has Level 3 - Medium Corrosion up to 25% coverage. | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | 16/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P3. | injury risk | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | AA |  | Corrosion pf channel bracket present | no | yes | P3 | no |  | 1f383807-dda2-44bf-990e-70fe2d5a1c16,e087ab60-0124-496c-b357-fc17ccfe3b5c | , | https://web.fulcrumapp.com/photos/view?photos=1f383807-dda2-44bf-990e-70fe2d5a1c16%2Ce087ab60-0124-496c-b357-fc17ccfe3b5c | Steel | Channel Bracket | Corrosion-Heavy
9bf3a74b-1f2b-44ac-b802-1c09f241f0ac | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 473 | 11 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  |  |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Financial | Financial |  | Chloride Induced |  | Chloride Induced | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 473, 11 o'clock, Segment Bolted Joint (Circle Joint). | Shear failure of bolt | Shear failure of bolt |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400 mm x 300 mm. Concrete spalling was observed with level 2 corrosion on reinforcement. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 400 mm x 300 mm. Concrete spalling was observed with level 2 corrosion on reinforcement. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 4 and Unlikely Likelihood of failure, resulting in a Priority 3. |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | KP |  | Condition change as reinforcements are corroding and Drumminess in concrete is spreading | yes | yes | P3 |  |  | 6c7e43fc-a773-4c31-9098-86d80fbe1d22 |  | https://web.fulcrumapp.com/photos/view?photos=6c7e43fc-a773-4c31-9098-86d80fbe1d22 | Concrete | Circular Joint | Drummy |  | Not reinforcement
e6cd345a-0f58-4979-adab-56d8808b54ba | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 492 | 1 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  |  |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 492, 1 o'clock, Grout Injection Hole | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 23/10/2024 AC: As per agreed with GTS Mechanical Engineer (RP), included repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. | No | Off-Line | Yes | Scaffolding | - | Standard Repair Detail Competent Supervisor | Dr |  | Major leak still present and active. Salt deposits are still present and has corroded the pipe below and walkway as well. | yes | yes | P2 |  |  | d8d82f5c-2c04-4f2f-abf6-860e0ef36802,216f497e-da60-4854-ba6c-77c1f8bacf9f,7661700e-2260-4a8b-950b-7186676f5bbd,a14f9d37-8709-462b-83ad-8221c9bf0dd9,7ff5c47f-8502-44fa-9259-490849ff02dd,7bafc784-7c44-4171-a905-fe7dd45d78a1 | ,,,,, | https://web.fulcrumapp.com/photos/view?photos=d8d82f5c-2c04-4f2f-abf6-860e0ef36802%2C216f497e-da60-4854-ba6c-77c1f8bacf9f%2C7661700e-2260-4a8b-950b-7186676f5bbd%2Ca14f9d37-8709-462b-83ad-8221c9bf0dd9%2C7ff5c47f-8502-44fa-9259-490849ff02dd%2C7bafc784-7c44-4171-a905-fe7dd45d78a1 | Concrete | Grout Hole | Leaks
e3fdd570-0e7a-4a0f-b079-d6a694b6490d | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 276 | 5 | Steel Channel Bracket | Steel Channel Bracket |  |  |  |  | Tunnel Harbour UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant |  |  | 10/07/2019 |  |  | No | [13 empty] | Severity Level 2 | Severity Level 2 |  | Unlikely (Failure within 20 years) | Unlikely (Failure within 20 years) |  | Structure,Ring 276,5 O'Clock,Support Bracket,Identified in 2018 |  |  |  | Class 4 - Medium high corrosion |  | Class 4 - Medium high corrosion | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  |  |  |  | Priority 4 | [5 empty] | No | Off-Line |  |  |  |  | KP |  | No change in the condition, actively corroding base plate and bolts | yes | no | P3 |  |  | e5dbf056-48cf-43f0-9c50-b93e696ef8c1,05721f7a-c81d-44de-b8d1-5168cf817697 | , | https://web.fulcrumapp.com/photos/view?photos=e5dbf056-48cf-43f0-9c50-b93e696ef8c1%2C05721f7a-c81d-44de-b8d1-5168cf817697 | Steel | Centre Support | Corrosion-Heavy |  | Centre support and bolt no Channel bracket
ac09cdad-bdda-4795-b595-cc8d97c94c3e | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 366 | 3 | Channel Anchor Bolts | Channel Anchor Bolts |  |  |  | 8677 | UHT001 | Service Supports (Ring 226-399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion - Structure Member/Platework | Corrosion - Structure Member/Platework |  | Level 3 | Level 3 | Level 3 | Health & Safety | Health & Safety |  | Localised Corrosion EXT | Localised Corrosion EXT |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 366, 3 O'clock, Steel Channel Bracket and Anchor Bolt | Rupture | Rupture |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. |  | Steel channel support bracket has Level 3 corrosion. Channel anchor bolts have Level 3 corrosion. | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). | Loss of minor services (NOT water pipe). Water leak through joint, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Unlikely Likelihood of failure, resulting in a Priority 4. | Not Specified | Priority: P3 |  |  |  | Replace damaged bolts one at a time as per original design specification. Remove corrosion by abrasive blasting or mechanical means and reinstate protective coatings in accordance with BHP specifications. | Steelwork Remediation Crew. BHPIO SPEC-000-S-00061 and Steel Corrosion Repair Guideline 0136559. | No | Off-Line | Yes | - | - | Blast & Paint Repair Competent Supervisor | Dr |  | Corrosion has advanced. | yes | yes | P2 |  |  | 5ca8bb34-d645-499b-b62e-7fd9e9661844 |  | https://web.fulcrumapp.com/photos/view?photos=5ca8bb34-d645-499b-b62e-7fd9e9661844 | Steel | Channel Bracket | Corrosion-Heavy
5f4ff749-df9a-407a-b8db-6510ca12da8b | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 387 | 4 | Segment Bolted Joint (Circle Joint) |  | Segment Bolted Joint (Circle Joint) |  |  |  | Tunnel Harbour UHT001 | Bored Tunnel (Ring 226-399) | SIM-FixedPlant |  |  | 20/02/2023 |  |  | No | Missing | [12 empty] | Severity Level 3 | Severity Level 3 |  | Possible (Failure within 5 years) |  | Possible (Failure within 5 years) | Ring 387, 4 O'Clock, Segmented Bolted Joint (Circle Joint) |  |  |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 200mm. |  | Circle joint has Grout Delamination / Drummy Grout over an area of 150mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  |  |  |  | Priority 4 | [5 empty] | Yes | Off-Line |  |  |  |  | Dr |  | Delaminated and drummy concrete is still present on the same size with concrete spalling. | yes | no | P4 | yes | Location at 5 O Clock not at 4. | 059a1ee2-0d1f-4ff7-b378-80d6bba6c553,743cb8bb-b97c-4350-a402-459e6ff9141f,e740c33c-dc31-4f2b-9816-acaa0171c74d,a05c7714-5418-4928-9ea2-18e7a76ac334 | ,,, | https://web.fulcrumapp.com/photos/view?photos=059a1ee2-0d1f-4ff7-b378-80d6bba6c553%2C743cb8bb-b97c-4350-a402-459e6ff9141f%2Ce740c33c-dc31-4f2b-9816-acaa0171c74d%2Ca05c7714-5418-4928-9ea2-18e7a76ac334 | Concrete | Circular Joint | Drummy
00a33b31-71e8-4f6d-9ab6-edc0c8359f30 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 532 | 12 | Grout Injection Hole | Grout Injection Hole |  |  |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 532, 12 o'clock, Grout Injection Hole. | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak - Inactive at time of inspection. | Grout injection hole has Leak - Inactive at time of inspection. |  | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 07/09/2023 AC: As per agreed with GTS Structural Engineers (Carlos Torres & Hiruni Kellapatha), monitor. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Inactive leak shall be assessed as P3 as discussed with BHP AIMS. | Priority: P3 |  |  |  | Review and assess condition at the next inspection. | AIMS structural inspector | Yes | Off-Line | Yes | - | - | Condition Monitoring Competent Supervisor | Dr |  | Leak is active at time of inspection with salt deposits collected from the grout injection hole. Severe corrosion present on steel bracket and on pipe below. Grid mesh on walkway has been replaced during the shit due to severe corrosion. | yes | no | P2 | no |  | be4afb89-b0db-4375-9612-9d0ed0e9823e,00debf6a-03ef-4e51-b725-7818096e2170,a898d8ae-ffd3-459e-8256-99fcd18db57a,cc507814-2682-4353-87f7-1e1726041949 | ,,, | https://web.fulcrumapp.com/photos/view?photos=be4afb89-b0db-4375-9612-9d0ed0e9823e%2C00debf6a-03ef-4e51-b725-7818096e2170%2Ca898d8ae-ffd3-459e-8256-99fcd18db57a%2Ccc507814-2682-4353-87f7-1e1726041949 | Concrete | Grout Hole | Leaks
4af5d8c3-ced7-43d2-aba9-f4f910d09387 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 384 | 12 | Grout Injection Hole | Grout Injection Hole |  |  |  | 8677 | UHT001 | Bored Tunnel (Ring 226 -399) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons |  | Severity Level 3. Life altering or long term/permanent disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 384, 12 O'clock, Grout Injection Hole | Break up of grout and water leaks | Break up of grout and water leaks |  | Grout injection hole has Leak Active at time of inspection. |  | Grout injection hole has Leak Active at time of inspection. | Leaks through tunnel liner, leading to accelerated concrete damage (locally). | Leaks through tunnel liner, leading to accelerated concrete damage (locally). |  | Health & Safety, Severity Level 2 | 16/10/2024 AC: As per agreed with GTS Mechanical Engineers (CC), included repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 2 and Unlikely Likelihood of failure, resulting in a Priority 4. | Reduced structural reliability and mean time to failure. Active leak shall be assessed as P2 as discussed with BHP AIMS. | Priority: P2 |  |  |  | Engineering leak seal repair detail and work scope to be developed to address leak to shell segments. Carry out leak seal in accordance with approved remediation work scope. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | Dr |  | Same as defect noted at 1 O' Clock. Incorrectly noted twice at 12 O' Clock. | yes | yes | P2 |  |  | 844f3bb8-d61d-4982-94b4-cc0ee95e8f70,f9463ec2-6e90-4de1-b029-18401b935896 | , | https://web.fulcrumapp.com/photos/view?photos=844f3bb8-d61d-4982-94b4-cc0ee95e8f70%2Cf9463ec2-6e90-4de1-b029-18401b935896 | Concrete | Grout Hole | Leaks |  | MIsc as well
eb0afdf9-538f-45c1-9aac-ac175c0d890c | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 526 | 4 | Segment Bolted Joint (Circle Joint) | Segment Bolted Joint (Circle Joint) |  |  |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Financial | Financial |  | Poor Construction Methods | Poor Construction Methods |  | Severity Level 3. >= US$50 million, < US$250 million |  | Severity Level 3. >= US$50 million, < US$250 million | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 526, 4 o'clock, Segment Bolted Joint (Circle Joint) | Shear failure of bolt | Shear failure of bolt |  | Grout Delamination / debonding at circle segment bolted joints at two locations. Each grout patch size is 200mm x 200mm. |  | Grout Delamination / debonding at circle segment bolted joints at two locations. Each grout patch size is 200mm x 200mm. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. | Movement of shell rings about joint resulting in leak, leading to accelerated concrete damage. |  | Financial, Severity Level 3 Reason for Not Specified | - |  | Priority: P3 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Concrete Remediation Crew. Structural Engineer. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | Defect is still present at the radial joint. Concrete spalling and cracking. | no | no | P3 | yes |  | 2985edae-a663-437e-b1af-2b2f93534bb7,71eb524a-f415-4c86-9865-83c2cc09a8b9 | , | https://web.fulcrumapp.com/photos/view?photos=2985edae-a663-437e-b1af-2b2f93534bb7%2C71eb524a-f415-4c86-9865-83c2cc09a8b9 | Concrete | Circular Joint | Surface Damage
735c7364-2716-45b5-b243-723abf80ffd9 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 496 | 3 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  |  |  | 8714 | UHT001 | Bored Tunnel (Ring 400 -613) | SIM-FixedPlant | Nelson Point | Not Assessable(Not Applicable to this Inspection Type) | 6/08/2024 |  | No | No | No | Other |  | Other | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Other Condition - Refer to Detailed Defect Description | Health & Safety | Health & Safety |  | Additional Components | Additional Components |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 496, 3 O'clock, Concrete shell segment at bolted connection penetration | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. | Concrete shell segment at bolted connection penetration has Leak - Active at time of inspection. |  | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | Active leak shall be assessed as P2 as discussed with BHP AIMS. | Not Specified | Priority: P2 |  |  |  | Carry out leak seal repair. Extent and quantity of similar defects should be considered to optimise remediation programme strategy. Refer to Notification 437157510 for appropriate similar engineering repair methodology. | Engineering repair method and specification required. Concrete remediation crew. AIMS Planning and Projects. | No | Off-Line | Yes | - | - | Standard Repair Detail Competent Supervisor | Dr |  | Severe level 5 corrosion on steel chanell due to the leak thru segment grout hole. | yes | no | P2 |  |  | 09be2354-dfd1-4927-bf25-20bdb710006e,6c4c1495-095a-4420-a089-27112e71446c,cb492a97-ec5f-4993-ac2c-ee168ecbfbe4,7a1a269a-7198-4cb9-996c-851d3bd8d098,73a16de5-b885-460d-835e-5c3a23b37a28 | ,,,, | https://web.fulcrumapp.com/photos/view?photos=09be2354-dfd1-4927-bf25-20bdb710006e%2C6c4c1495-095a-4420-a089-27112e71446c%2Ccb492a97-ec5f-4993-ac2c-ee168ecbfbe4%2C7a1a269a-7198-4cb9-996c-851d3bd8d098%2C73a16de5-b885-460d-835e-5c3a23b37a28 | Steel | Channel Bracket | Corrosion-Heavy |  | Channel Bracket and Bolt
6b12f86b-2c04-4d8b-a07b-dac4fbf4b05a | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 48 | 4 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  |  |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 3 | Condition Rating 3 | Condition Rating 3 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 48, 4 o'clock. Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete shell segment has drummy concrete over an area of 600mm x 600mm. |  | Concrete shell segment has drummy concrete over an area of 600mm x 600mm. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Legacy defect migrated from SDRS spreadsheet Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | - | - | Scheduled Maintenance Competent Supervisor | AC BP |  | Spalling is larger than typical delam grout pad. Parent concrete is affected. | no | yes | P3 | no |  | d24ab333-0cff-43b8-973a-bfa16a23bb97,bb2122d9-92e7-4ccb-b7d0-9943ea437e2a,c1766210-0a1e-4109-ae1d-df32805cfeda,642c2038-d25a-4b63-b6a9-0ec6b991e8cd | ,,, | https://web.fulcrumapp.com/photos/view?photos=d24ab333-0cff-43b8-973a-bfa16a23bb97%2Cbb2122d9-92e7-4ccb-b7d0-9943ea437e2a%2Cc1766210-0a1e-4109-ae1d-df32805cfeda%2C642c2038-d25a-4b63-b6a9-0ec6b991e8cd | Concrete | Circular Joint | Drummy |  | Circular Joint - Not reinforcement
44268584-4dd7-4883-9e2a-3eef16179624 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 1 | 0 | Ring (Segmental Concrete) - Damage Affecting Single Ring | Ring (Segmental Concrete) - Damage Affecting Single Ring |  |  |  | 7671 | UHT001 | Bored Tunnel (Ring 1- 225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion of Reinforcement | Corrosion of Reinforcement |  | Condition Rating 5 | Condition Rating 5 | Condition Rating 5 | Health & Safety | Health & Safety |  | Chloride Induced |  | Chloride Induced | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses |  | Severity Level 4. 1-5 fatalities or chronic life threatening illnesses | Likely (Failure within 2 Years) | Likely (Failure within 2 Years) |  | Ring 1, Full circumference, Concrete Shell Segment. | Failure of shell segment in compression or tension leading to single ring failure. | Failure of shell segment in compression or tension leading to single ring failure. |  | Concrete annular has drummy and spalling concrete all around. |  | Concrete annular has drummy and spalling concrete all around. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. | Single ring collapse and partial flooding of tunnel. Critical water pipe remains serviceable. |  | Health & Safety, Severity Level 4 | 15/05/2024 AC: As per agreed with GTS Structural Engineer (VS), upgraded to P2 and revised recommended action to include repair methodology provided by GTS. Prior to the AIMS BLD V6.0 update, this Defect was assessed with a Health & Safety Impact, Severity Level 5 and Unlikely Likelihood of failure, resulting in a Priority 2. | Not Specified | Priority: P2 |  |  |  | Repair damaged area of concrete, refer to Notification 437157740 for similar appropriate engineering repair methodology. | Nil | No | Off-Line | Yes | Scaffolding | - | Scheduled Maintenance Competent Supervisor | SS |  | The grout behind Ring 1 at interface with the cast in situ concrete portal Is delaminating with surface defect. Active water leak from behind the precast segments is noted at edge ony. | no | yes | P2 | yes | Reduce priority and risk. This defect relates to cladding/shotcrete, not the structural components. | 21276bec-a0b1-49d4-a4f4-8172ae62b33d,8e6f022d-e6ae-4182-af75-87932f19471e,b0c6914d-44a9-4d23-a026-af990b2b8f76,3c57cfa0-dc3f-4401-b704-21b62ba67e3e | ,,, | https://web.fulcrumapp.com/photos/view?photos=21276bec-a0b1-49d4-a4f4-8172ae62b33d%2C8e6f022d-e6ae-4182-af75-87932f19471e%2Cb0c6914d-44a9-4d23-a026-af990b2b8f76%2C3c57cfa0-dc3f-4401-b704-21b62ba67e3e | Concrete | Concrete | Drummy
94ac57f3-dfa0-4162-b757-f8f3441f8120 | af5cf9d7-2ea4-4457-9557-527081137d3a | af5cf9d7-2ea4-4457-9557-527081137d3a | 1 |  |  |  | 2025-09-16 19:14:53 AEST | 2025-09-16 19:14:53 AEST | sandy.tulloch@smec.com | sandy.tulloch@smec.com | 134 | 0 | Channel Anchor Bolts | Channel Anchor Bolts |  |  |  | 7671 | UHT001 | Service Supports (Ring 1-225) | SIM-FixedPlant | Nelson Point | Assessed | 5/10/2022 |  | No | No | No | Corrosion - Connection | Corrosion - Connection |  | Level 4 | Level 4 | Level 4 | Health & Safety | Health & Safety |  | Corrosion Under Buildup |  | Corrosion Under Buildup | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons |  | Severity Level 2. Non-life altering or short-term disabling injury or illness to >=1 persons | Almost Certain (Failure within 1 Year) | Almost Certain (Failure within 1 Year) |  | Ring 134, 1 & 3 o'clock. Steel Channel Support Bracket. | Rupture | Rupture |  | Steel channel support bracket has Level 4 Major Corrosion up to 25% coverage. Channel anchor bolts have Level 2 3 |  | Steel channel support bracket has Level 4 Major Corrosion up to 25% coverage. Channel anchor bolts have Level 2 3 | Loss of minor services (NOT water pipe) | Loss of minor services (NOT water pipe) |  | Health & Safety, Severity Level 2 | Legacy defect migrated from SDRS spreadsheetPrior to the AIMS BLD V6.0 update, this Defect was assessed with a Financial Impact, Severity Level 3 and Possible Likelihood of failure, resulting in a Priority 3. | Loss of minor services (NOT water pipe) | Priority: P3 |  |  |  | 1. Abrasive blast to extend at least 150mm past corroded areas to determine extent of corrosion. Refer to Document No. 0136559 - Steelwork Corrosion Repair Guideline Document for details. 2. Apply protective coating to extend at least 150mm past all corroded areas. | Nil | No | Off-Line | Yes | - | Working at Heights | Scheduled Maintenance Competent Supervisor | HM |  | Steel channel bracket and anchor bolt is heavily corroded at 1 & 3 o' clock. | no | yes | P2 | no |  | d77c133a-53e2-4dd4-ba36-bee3907f5285,edaf1aa8-7c72-4636-a99c-8b8ad1cd5496,2be78ddc-c48e-4b69-98d1-e1e2be196de6,cf3ffb0e-df2f-40b3-a53c-02e114f30297,fc7ecf2d-279d-4284-bb44-e094abaf936f,9888b100-0e3e-4f5d-96ed-26a878d29599,f8998f8a-4346-45eb-ac89-2fa69500c9ba,810a9103-0137-459b-adf3-96244c180337,5de84dd3-9b52-4462-8576-5dc02fedb22a,59a2f3d9-5ce7-4ca9-9a22-3d6b71cea106 | ,,,,,,,,, | https://web.fulcrumapp.com/photos/view?photos=d77c133a-53e2-4dd4-ba36-bee3907f5285%2Cedaf1aa8-7c72-4636-a99c-8b8ad1cd5496%2C2be78ddc-c48e-4b69-98d1-e1e2be196de6%2Ccf3ffb0e-df2f-40b3-a53c-02e114f30297%2Cfc7ecf2d-279d-4284-bb44-e094abaf936f%2C9888b100-0e3e-4f5d-96ed-26a878d29599%2Cf8998f8a-4346-45eb-ac89-2fa69500c9ba%2C810a9103-0137-459b-adf3-96244c180337%2C5de84dd3-9b52-4462-8576-5dc02fedb22a%2C59a2f3d9-5ce7-4ca9-9a22-3d6b71cea106 | Steel | Channel Bracket | Corrosion-Heavy

## previous_photos
fulcrum_id | fulcrum_parent_id | fulcrum_record_id | version | caption | latitude | longitude | geometry | file_size | uploaded_at | exif_date_time | exif_gps_altitude | exif_gps_date_stamp | exif_gps_time_stamp | exif_gps_dop | exif_gps_img_direction | exif_gps_img_direction_ref | exif_gps_latitude | exif_gps_latitude_ref | exif_gps_longitude | exif_gps_longitude_ref | exif_make | exif_model | exif_orientation | exif_pixel_x_dimension | exif_pixel_y_dimension | exif_software | exif_x_resolution | exif_y_resolution
80dbd20b-d251-4ea5-b669-1b098286b517 | 1bb58b15-c900-4cda-a13d-46fa091d07a8 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 722141 | 2025-05-29 11:26:50 AEST | 2025-05-29 14:00:43 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2505.1.1 (18441), Android 14, samsung, SM-S901E
23492d72-6c74-466c-9895-50d3f7913ff5 | 72a0a338-7d9d-461e-84fa-98e8ff13c143 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 220447 | 2025-05-30 01:14:09 AEST | 2025-05-29 14:34:37 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2505.0.2 (12314), iOS 17.6.1, Apple, iPad Mini 6 | 72 | 72
f2b02e96-7a74-4e5c-89d2-1c8f8710c3c1 | 72a0a338-7d9d-461e-84fa-98e8ff13c143 | 7e727b96-7206-4f43-982f-dc9a2b271ad6 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 308148 | 2025-05-30 01:14:11 AEST | 2025-05-29 14:34:52 AEST | [10 empty] | Apple | iPad mini | BottomRight | 1080 | 810 | Fulcrum iOS 2505.0.2 (12314), iOS 17.6.1, Apple, iPad Mini 6 | 72 | 72
61ce4cea-a557-48c9-bf55-6d582ed81b90 | 4d6da948-e299-43f3-b128-afded06dcfe6 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 680275 | 2025-05-29 12:18:21 AEST | 2025-05-29 20:17:04 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2505.1.1 (18441), Android 14, samsung, SM-S901E
5b5d98db-c62c-425d-92ec-7790992ed957 | 4d6da948-e299-43f3-b128-afded06dcfe6 | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 604319 | 2025-05-29 12:18:18 AEST | 2025-05-29 20:17:04 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2505.1.1 (18441), Android 14, samsung, SM-S901E
077bce82-36d2-4e2d-8056-492e05a400e0 | 69b2867f-aaea-49ca-ab3f-a912d1514ddf | 110a175f-a692-4ca9-89a8-2a7da948c4bd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 714276 | 2025-05-29 11:56:49 AEST | 2025-05-29 19:56:02 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2505.1.1 (18441), Android 14, samsung, SM-S901E

## photos
fulcrum_id | fulcrum_parent_id | fulcrum_record_id | version | caption | latitude | longitude | geometry | file_size | uploaded_at | exif_date_time | exif_gps_altitude | exif_gps_date_stamp | exif_gps_time_stamp | exif_gps_dop | exif_gps_img_direction | exif_gps_img_direction_ref | exif_gps_latitude | exif_gps_latitude_ref | exif_gps_longitude | exif_gps_longitude_ref | exif_make | exif_model | exif_orientation | exif_pixel_x_dimension | exif_pixel_y_dimension | exif_software | exif_x_resolution | exif_y_resolution
a94807ff-0280-42fd-9f1a-09d02951e350 | b1982b59-a408-4e84-a0a3-6b76cdaaa108 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 557558 | 2025-07-30 04:10:23 AEST | 2025-07-30 11:31:05 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
521e53b8-bc23-4411-bd0e-d7d179c28578 | b1982b59-a408-4e84-a0a3-6b76cdaaa108 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 590332 | 2025-07-30 04:10:26 AEST | 2025-07-30 11:31:05 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c289668f-7805-45c1-9d71-acfe9b9a70c6 | 0e43a454-5936-417b-8411-d5e03c0490d9 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 542632 | 2025-07-30 04:10:27 AEST | 2025-07-30 11:32:11 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a9f93e1a-1b1e-4c5f-8aad-b490cd349b74 | 0e43a454-5936-417b-8411-d5e03c0490d9 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 562075 | 2025-07-30 04:10:29 AEST | 2025-07-30 11:32:11 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3fc54fb9-8ec9-4568-8cc3-ba4e882bab7b | 7a90b69f-a3e6-43a4-8871-ba37454e4ceb | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 408373 | 2025-07-27 21:10:09 AEST | 2025-07-27 17:50:18 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 | 105.7041 | T | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a574f345-3278-44dd-91ea-a35d2e1177c6 | 7a90b69f-a3e6-43a4-8871-ba37454e4ceb | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 282750 | 2025-07-27 21:10:06 AEST | 2025-07-27 17:50:44 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 | 105.7041 | T | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e773bb75-0a4b-4742-9711-e10e299e465f | 7a90b69f-a3e6-43a4-8871-ba37454e4ceb | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 372002 | 2025-07-27 21:10:03 AEST | 2025-07-27 17:51:43 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 | 105.7041 | T | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
9677d833-72da-4599-b75d-69bc3069dce4 | 7a90b69f-a3e6-43a4-8871-ba37454e4ceb | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3157 | 118.5808 | POINT (118.58076944444444 -20.315730555555557) | 258132 | 2025-07-27 09:55:20 AEST | 2025-07-27 17:50:17 AEST | 0 | 2025-07-26 | 23:50:24 | 1414 | 325.3032 | T | -20.3157 | S | 118.5808 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
184463c9-c3a8-4dcd-8f6c-2468000f7d38 | 9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 334105 | 2025-07-24 17:52:49 AEST | 2025-07-24 18:19:18 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
8bdf6a6e-8b3b-4785-ac61-d3a621d0b6b6 | 9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 203664 | 2025-07-24 17:52:52 AEST | 2025-07-24 18:19:30 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
99ff6f4e-14a5-489a-bad2-efa96a7614de | 9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 390909 | 2025-07-24 17:53:07 AEST | 2025-07-24 18:19:55 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
0dc61c65-86a7-403f-9dfa-f803847a5631 | 9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 312864 | 2025-07-27 21:10:00 AEST | 2025-07-27 17:53:42 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
3ff22668-0493-4efe-8d28-06a281f8ab27 | 9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 432809 | 2025-07-27 21:09:56 AEST | 2025-07-27 17:54:06 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
52c471c3-3437-4933-bf3d-babb91d96234 | 9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 256944 | 2025-07-27 21:09:53 AEST | 2025-07-27 17:54:10 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b82752d8-2366-4009-ac4b-4b91e8b5b41a | 9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 437589 | 2025-07-27 21:09:50 AEST | 2025-07-27 17:54:18 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
9926ef99-2ba9-4e92-853b-ca00d463cc4c | 9cb72fd4-2a0e-42ed-818a-65ac188aca8f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 351444 | 2025-07-27 21:09:47 AEST | 2025-07-27 17:54:25 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d7c14cf2-81b7-4ba1-b0fd-2454de075748 | 7f761d96-ac2a-4b92-a637-e996fe372129 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 299715 | 2025-07-24 13:54:38 AEST | 2025-07-24 18:30:51 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
99067542-2a77-410f-8c36-9d48058a73d0 | 7f761d96-ac2a-4b92-a637-e996fe372129 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 162452 | 2025-07-24 13:54:35 AEST | 2025-07-24 18:31:00 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
bad9450c-d892-466c-aea1-60e34abd62f3 | 968d0d8d-b055-46b7-9db2-78ea73528cef | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 265588 | 2025-07-24 13:54:58 AEST | 2025-07-24 18:18:53 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d3d5e04f-bedb-49f7-8205-03ded8c2d9bb | 968d0d8d-b055-46b7-9db2-78ea73528cef | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 274102 | 2025-07-24 13:54:53 AEST | 2025-07-24 18:19:07 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
1b492bf1-dd0d-4053-ac3f-746fc008858e | 968d0d8d-b055-46b7-9db2-78ea73528cef | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 192523 | 2025-07-24 13:54:50 AEST | 2025-07-24 18:19:37 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
21c11c36-abbe-43c2-9d7b-869ff8a2a7b3 | 968d0d8d-b055-46b7-9db2-78ea73528cef | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3198 | 118.5855 | POINT (118.5854611111111 -20.31976388888889) | 204132 | 2025-07-24 17:53:10 AEST | 2025-07-24 18:37:04 AEST | 8.7238 | 2025-07-24 | 00:33:32 | 2110.3613 | 272.5486 | T | -20.3198 | S | 118.5855 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
5e7c4bc4-7559-4e7d-bcda-54ede796c462 | 968d0d8d-b055-46b7-9db2-78ea73528cef | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3198 | 118.5855 | POINT (118.5854611111111 -20.31976388888889) | 238766 | 2025-07-24 17:53:12 AEST | 2025-07-24 18:37:29 AEST | 8.7238 | 2025-07-24 | 00:33:32 | 2110.3613 | 272.5486 | T | -20.3198 | S | 118.5855 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
036b3b3e-c9d7-4df9-8a08-0311de9d705d | 1f1b4238-2c21-4a9d-88fa-46f015a460bf | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 183816 | 2025-07-24 13:54:47 AEST | 2025-07-24 18:25:36 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
f4cffe92-ac14-4ccc-b517-a3092442057e | 1f1b4238-2c21-4a9d-88fa-46f015a460bf | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 171379 | 2025-07-24 13:54:44 AEST | 2025-07-24 18:25:52 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b8757818-970f-41c4-87ad-6fd20bde8eef | 1f1b4238-2c21-4a9d-88fa-46f015a460bf | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 284306 | 2025-07-24 13:54:41 AEST | 2025-07-24 18:26:10 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
21276bec-a0b1-49d4-a4f4-8172ae62b33d | e3a099cc-22d6-4701-a40b-64adffd15e6d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 485662 | 2025-07-30 04:10:34 AEST | 2025-07-30 11:34:14 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8e6f022d-e6ae-4182-af75-87932f19471e | e3a099cc-22d6-4701-a40b-64adffd15e6d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 546623 | 2025-07-30 04:10:41 AEST | 2025-07-30 11:34:14 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b0c6914d-44a9-4d23-a026-af990b2b8f76 | e3a099cc-22d6-4701-a40b-64adffd15e6d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 520901 | 2025-07-30 04:10:39 AEST | 2025-07-30 11:34:14 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3c57cfa0-dc3f-4401-b704-21b62ba67e3e | e3a099cc-22d6-4701-a40b-64adffd15e6d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 436922 | 2025-07-30 04:10:37 AEST | 2025-07-30 11:34:14 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0174535a-2bc8-4c6c-a5fb-2d7ebe3436f1 | 5608525a-a39b-49d7-989a-da8b981809f4 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 156853 | 2025-07-24 13:54:32 AEST | 2025-07-24 18:33:58 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
0782e471-e902-4320-b2a2-86e4f334a743 | 5608525a-a39b-49d7-989a-da8b981809f4 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 145513 | 2025-07-24 13:54:29 AEST | 2025-07-24 18:34:19 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
bc8075f5-eeff-4ed2-9d9f-3a30f236c1c3 | 10d7222e-9782-498b-8b98-404e3995b27b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3155 | 118.5805 | POINT (118.58051111111111 -20.315527777777778) | 180497 | 2025-07-27 09:59:54 AEST | 2025-07-27 17:59:17 AEST | 0 | 2025-07-26 | 23:56:36 | 1414.1222 | 301.2512 | T | -20.3155 | S | 118.5805 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
1f64275b-c28e-4041-81f4-fd8439e390a8 | b9abdc46-80b1-4c40-826b-a978b855b310 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3197 | 118.5815 | POINT (118.58145555555555 -20.31966388888889) | 243343 | 2025-07-28 19:08:25 AEST | 2025-07-28 23:42:01 AEST | 5.8419 | 2025-07-28 | 05:41:37 | 2550.2458 | 229.7009 | T | -20.3197 | S | 118.5815 | E | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
3f5b084b-5459-4bcb-a31f-68bd2e3f90e8 | 3578efe7-a275-415c-a9be-83a8ccd73fcd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 378512 | 2025-07-27 21:09:45 AEST | 2025-07-27 17:57:35 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
bc4aab33-d441-4abe-aada-2e42fb3f9249 | 3578efe7-a275-415c-a9be-83a8ccd73fcd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 338268 | 2025-07-27 21:09:41 AEST | 2025-07-27 17:57:41 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a751eb4a-4806-4d10-9dfc-2eb62d66c0a6 | 3578efe7-a275-415c-a9be-83a8ccd73fcd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 387887 | 2025-07-27 21:09:38 AEST | 2025-07-27 17:57:48 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d22245cc-9d72-4e59-8566-cd538ebc7f36 | fb8a19a9-0eee-4134-bc19-152d4bb867db | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 265075 | 2025-07-24 13:54:11 AEST | 2025-07-24 19:04:10 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e0da654a-cda5-4fe8-a173-75539a430b0e | d2ffae24-ec6c-425e-b3e1-4b82c759625c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 421430 | 2025-07-31 13:36:08 AEST | 2025-07-31 08:58:48 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a3c43e32-4ed7-420f-8d76-6aef2312a986 | 8429f7d8-bc66-438e-af5c-92d90ac90986 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 460961 | 2025-07-24 13:53:53 AEST | 2025-07-24 19:21:14 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
33f56796-f7f0-490c-88db-6973fd75967d | 190f23f7-5ffa-43d4-9cd5-7c0d12a1148c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 433360 | 2025-07-24 13:54:07 AEST | 2025-07-24 19:15:35 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
2650350b-4fc7-4b59-af33-0c85d52e8150 | 190f23f7-5ffa-43d4-9cd5-7c0d12a1148c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 318765 | 2025-07-24 13:54:02 AEST | 2025-07-24 19:15:50 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
f1c0012b-81c6-4300-9405-f6d6cf190d7d | 190f23f7-5ffa-43d4-9cd5-7c0d12a1148c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 468849 | 2025-07-24 13:53:59 AEST | 2025-07-24 19:17:05 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
43cf7236-abfd-40fe-b560-8f8af40cbf4e | 396e9b60-bd06-4442-ab63-c93f988c5e61 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58206388888888 -20.316583333333334) | 257946 | 2025-07-24 17:53:16 AEST | 2025-07-24 19:24:57 AEST | 8.7238 | 2025-07-24 | 01:24:20 | 1414 | 184.8148 | T | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
b1aff8e7-5c4a-4d09-bcbd-95b2a5561201 | 396e9b60-bd06-4442-ab63-c93f988c5e61 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58206388888888 -20.316583333333334) | 267976 | 2025-07-24 17:53:19 AEST | 2025-07-24 19:25:22 AEST | 8.7238 | 2025-07-24 | 01:24:20 | 1414 | 182.7282 | T | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
c0afe889-8075-4c9c-b0c4-1f818576179b | 396e9b60-bd06-4442-ab63-c93f988c5e61 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58212222222222 -20.31663888888889) | 248380 | 2025-07-24 17:53:25 AEST | 2025-07-24 19:35:14 AEST | 8.7238 | 2025-07-24 | 01:34:49 | 1414 | 197.5314 | T | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
e6236844-5434-47b6-b04f-bb852078808a | 396e9b60-bd06-4442-ab63-c93f988c5e61 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58212222222222 -20.31663888888889) | 222315 | 2025-07-24 17:53:28 AEST | 2025-07-24 19:35:47 AEST | 8.7238 | 2025-07-24 | 01:35:27 | 1414 | 181.9106 | T | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
74a9a1ae-ceff-4379-801b-a8b882ed86d8 | e27d23f8-7284-40b3-b57a-02331141d626 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 841819 | 2025-07-30 03:57:46 AEST | 2025-07-30 11:56:43 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
49b43731-4d22-487c-9489-db6960f6e8a2 | e27d23f8-7284-40b3-b57a-02331141d626 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 755705 | 2025-07-30 03:57:14 AEST | 2025-07-30 11:56:43 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
388e83b4-8d90-4a28-b3e0-c609483b6c04 | 9e35d7e8-e025-4d5f-a828-8f758283bce7 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 609524 | 2025-07-31 13:36:11 AEST | 2025-07-31 09:06:04 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f8b7bfc6-75ac-43e5-9713-f8757f19ec1c | 9e35d7e8-e025-4d5f-a828-8f758283bce7 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 443814 | 2025-07-31 13:36:09 AEST | 2025-07-31 09:06:04 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5d518eba-eefe-489b-b1e9-5a34b235ca76 | d8911c4c-47bb-44f1-8c59-c4d3146ed36e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58212222222222 -20.31663888888889) | 380818 | 2025-07-24 17:53:31 AEST | 2025-07-24 19:38:44 AEST | 8.7238 | 2025-07-24 | 01:37:27 | 1414 | 141.4788 | T | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
af909b1d-fb07-4182-8795-bcf506ea0858 | d8911c4c-47bb-44f1-8c59-c4d3146ed36e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58212222222222 -20.31663888888889) | 190071 | 2025-07-24 17:53:34 AEST | 2025-07-24 19:39:23 AEST | 8.7238 | 2025-07-24 | 01:37:27 | 1414 | 100.696 | T | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
c5f7d2c2-3716-4f77-8f0c-156e38f932f4 | aa6687f7-0267-4cb4-ab67-ba14e5cf1d33 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3189 | 118.5846 | POINT (118.58463888888889 -20.318941666666667) | 375156 | 2025-07-27 18:51:18 AEST | 2025-07-27 18:11:42 AEST | 0 | 2025-07-27 | 00:11:29 | 1414 | 264.3321 | T | -20.3189 | S | 118.5846 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
dd38181e-1139-46bb-a992-aa254d97a15e | 43d3fe01-953d-4cac-b04d-4633f8bc6904 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 192685 | 2025-07-24 17:53:37 AEST | 2025-07-24 19:51:34 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
a2ce154c-a40b-4014-aea7-95c7c66ffe28 | 43d3fe01-953d-4cac-b04d-4633f8bc6904 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 279349 | 2025-07-27 21:09:17 AEST | 2025-07-27 18:13:45 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c14b73e6-af96-4425-9c65-624edb90d645 | 00cda714-0c80-4992-82ee-cc664ce74862 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 384867 | 2025-07-24 13:53:39 AEST | 2025-07-24 19:47:13 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
3465c876-82f9-49f7-9e0d-599143993618 | 00cda714-0c80-4992-82ee-cc664ce74862 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 420438 | 2025-07-24 13:53:34 AEST | 2025-07-24 19:47:37 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
7c85fb44-2252-47dd-bc5d-dc7f7e566008 | c9e84d13-19b7-4bcf-bde8-07fff10546d7 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3156 | 118.5806 | POINT (118.58059999999999 -20.315591666666666) | 172123 | 2025-07-27 18:51:21 AEST | 2025-07-27 18:16:10 AEST | 0 | 2025-07-27 | 00:15:11 | 1414 | 274.7514 | T | -20.3156 | S | 118.5806 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
e59587ee-72aa-4fc6-a657-caa28feb90d1 | f7dcc05c-efe7-48ac-abc1-3071afb31f0b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 405084 | 2025-07-24 13:53:29 AEST | 2025-07-24 19:53:31 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
2158f87d-95c6-4473-bd98-c7d9603f12f1 | f7dcc05c-efe7-48ac-abc1-3071afb31f0b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 397805 | 2025-07-24 13:53:23 AEST | 2025-07-24 19:54:35 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
eb84e8c8-319f-4e2c-8c2f-ab9280e948a1 | f7dcc05c-efe7-48ac-abc1-3071afb31f0b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58212222222222 -20.31663888888889) | 196634 | 2025-07-24 17:53:40 AEST | 2025-07-24 20:10:01 AEST | 8.7238 | 2025-07-24 | 02:08:16 | 1414 |  |  | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
22ea825b-a6ab-4c94-b634-082714711f3d | f7dcc05c-efe7-48ac-abc1-3071afb31f0b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58212222222222 -20.31663888888889) | 174612 | 2025-07-24 17:53:43 AEST | 2025-07-24 20:10:29 AEST | 8.7238 | 2025-07-24 | 02:08:16 | 1414 |  |  | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
b4462138-0f94-47da-a639-e3401da60364 | aa2f6c5a-25cc-4725-adc7-02733d06eb5b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 535178 | 2025-07-31 13:36:14 AEST | 2025-07-31 09:10:29 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
793b4e49-8a9a-4e2e-adc3-af444eb9f1c0 | aa2f6c5a-25cc-4725-adc7-02733d06eb5b | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 451802 | 2025-07-31 13:36:12 AEST | 2025-07-31 09:10:29 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
afd41dfa-28f0-4631-aa30-0147e16ab012 | 665f2a1a-cffe-4f55-bf81-70ca463a5681 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 421775 | 2025-07-24 13:53:19 AEST | 2025-07-24 20:02:41 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d4392b5a-281a-429d-b7ea-5c786b5e4358 | 665f2a1a-cffe-4f55-bf81-70ca463a5681 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 570262 | 2025-07-24 13:53:13 AEST | 2025-07-24 20:02:48 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c42b3328-a4bd-480e-824c-01b7c98e9c69 | 21caa9db-8e37-4fcf-82b1-d535498059d0 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58213055555555 -20.316644444444446) | 310702 | 2025-07-24 17:53:46 AEST | 2025-07-24 20:15:45 AEST | 8.7238 | 2025-07-24 | 02:12:15 | 1414 |  |  | -20.3166 | S | 118.5821 | E | Apple | iPad mini | BottomRight | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
43301d51-a346-4bd9-81f1-b516be02ce90 | 21caa9db-8e37-4fcf-82b1-d535498059d0 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58213055555555 -20.316644444444446) | 169243 | 2025-07-24 17:53:58 AEST | 2025-07-24 20:16:17 AEST | 8.7238 | 2025-07-24 | 02:12:15 | 1414 |  |  | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
86f8d434-03a7-473d-90e0-65e6770e7686 | 21caa9db-8e37-4fcf-82b1-d535498059d0 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5821 | POINT (118.58213055555555 -20.316644444444446) | 198412 | 2025-07-24 17:54:04 AEST | 2025-07-24 20:16:33 AEST | 8.7238 | 2025-07-24 | 02:12:15 | 1414 |  |  | -20.3166 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2506.0.0 (12319), iOS 17.5.1, Apple, iPad Mini 6 | 72 | 72
d62748ee-f383-4939-977e-736a77101dbd | 309e7188-8bbd-4207-8b31-586a481af661 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 328967 | 2025-07-24 13:53:08 AEST | 2025-07-24 20:09:03 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
12b70aa8-736e-4022-8dd9-2975f0ea89d3 | 309e7188-8bbd-4207-8b31-586a481af661 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 395274 | 2025-07-24 13:53:03 AEST | 2025-07-24 20:09:17 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
5d6e5a2c-feda-44dc-8d3f-e1b4977a278e | e57784ec-7102-439d-b632-8599eea2498d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3185 | 118.5821 | POINT (118.58214722222222 -20.318527777777778) | 380424 | 2025-07-28 19:08:18 AEST | 2025-07-29 00:47:09 AEST | 5.8419 | 2025-07-28 | 06:46:32 | 1475.0466 | 230.9534 | T | -20.3185 | S | 118.5821 | E | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
1363b019-8935-4f1a-81da-784e4b71a31a | e57784ec-7102-439d-b632-8599eea2498d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3185 | 118.5821 | POINT (118.58214722222222 -20.318527777777778) | 267524 | 2025-07-28 19:08:13 AEST | 2025-07-29 00:47:39 AEST | 5.8419 | 2025-07-28 | 06:46:32 | 1475.0466 | 39.948 | T | -20.3185 | S | 118.5821 | E | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
1c55a815-8b5c-4f0a-8afa-f07269dce205 | 89709a5b-3004-44aa-90e3-8e9e2b4a08e5 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3186 | 118.5819 | POINT (118.58190277777777 -20.318619444444444) | 381290 | 2025-07-28 19:08:01 AEST | 2025-07-29 01:04:45 AEST | 5.8419 | 2025-07-28 | 07:01:03 | 1688.528 | 93.2493 | T | -20.3186 | S | 118.5819 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
a7c35281-8da2-4deb-aab8-5551367e17a1 | cc1c9911-1c67-43f6-b97f-484e62651750 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3319 | 118.584 | POINT (118.58401111111111 -20.3319) | 256255 | 2025-07-28 19:08:07 AEST | 2025-07-29 00:57:00 AEST | 5.8419 | 2025-07-28 | 06:53:24 | 3391.1797 |  |  | -20.3319 | S | 118.584 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
889bdb70-495a-4ee3-9094-aee88e0020dc | 4c6d4c04-769b-4e7f-89e3-c71edba8f7e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 571519 | 2025-07-30 07:21:39 AEST | 2025-07-30 13:43:06 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c2f6d6dc-cafa-4244-8fd0-1a1c90b313de | 4c6d4c04-769b-4e7f-89e3-c71edba8f7e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 562103 | 2025-07-30 07:21:34 AEST | 2025-07-30 13:43:06 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
60d9b77c-91ad-4d20-8ae8-7d6c0bf0bfe7 | 4c6d4c04-769b-4e7f-89e3-c71edba8f7e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 620149 | 2025-07-30 07:21:36 AEST | 2025-07-30 13:43:06 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
89085428-410d-48ed-80d1-042cbb1d2db9 | 4c6d4c04-769b-4e7f-89e3-c71edba8f7e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 578881 | 2025-07-30 07:21:41 AEST | 2025-07-30 13:43:06 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5e25c115-9eaf-476c-a6ea-dd57ea5496fb | 5f95acb9-9168-4587-bb03-eb7c246c0018 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 315884 | 2025-07-24 13:52:59 AEST | 2025-07-24 20:21:06 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b4da837f-ba14-4327-a60f-f8cd8045ae99 | 5f95acb9-9168-4587-bb03-eb7c246c0018 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 285419 | 2025-07-24 13:52:56 AEST | 2025-07-24 20:21:24 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
7def633e-56a7-431e-97f0-317202dd404b | 64e464c3-133d-4749-afe0-1f6604ffce0d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 366703 | 2025-07-27 21:08:59 AEST | 2025-07-27 18:28:28 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e9cf9620-2059-4ef3-b0ab-50c9d0853fa0 | 64e464c3-133d-4749-afe0-1f6604ffce0d | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 286636 | 2025-07-27 21:08:56 AEST | 2025-07-27 18:28:36 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b1316c2d-014a-4f16-a2ce-0ab14adc2601 | 27f72c2e-c932-45e6-ac5b-3323bcd17354 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 575483 | 2025-07-31 13:36:17 AEST | 2025-07-31 09:20:53 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ed0a5bb1-b2a3-4eb1-beba-c529fb825872 | 27f72c2e-c932-45e6-ac5b-3323bcd17354 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 592909 | 2025-07-31 13:36:16 AEST | 2025-07-31 09:20:53 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7657abd2-933d-4f0e-9571-a50cca82e908 | cb8ab833-88ba-478e-bb56-b954ac7c2dde | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3169 | 118.5822 | POINT (118.58218333333333 -20.316877777777776) | 287427 | 2025-07-27 18:51:24 AEST | 2025-07-27 18:33:00 AEST | 0 | 2025-07-27 | 00:33:06 | 1414.399 | 2.2916 | T | -20.3169 | S | 118.5822 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
dcd4cd89-bce7-46c4-8cee-6e0b30a41cde | cb8ab833-88ba-478e-bb56-b954ac7c2dde | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3169 | 118.5822 | POINT (118.58218333333333 -20.316869444444443) | 236212 | 2025-07-27 18:51:27 AEST | 2025-07-27 18:33:34 AEST | 0 | 2025-07-27 | 00:33:10 | 1414 | 327.9802 | T | -20.3169 | S | 118.5822 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
f601cac6-3a40-4f1e-84c1-bae86bbbbb4a | cb8ab833-88ba-478e-bb56-b954ac7c2dde | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3166 | 118.5819 | POINT (118.58186944444444 -20.316613888888888) | 200100 | 2025-07-27 18:51:30 AEST | 2025-07-27 18:34:59 AEST | 0 | 2025-07-27 | 00:34:48 | 1414 | 348.7892 | T | -20.3166 | S | 118.5819 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
5655ae2a-2cec-4d90-b6a4-688d4cff08a3 | ed209b8e-6b25-4764-b1c2-5e04ec1d01e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 574739 | 2025-07-31 13:36:19 AEST | 2025-07-31 09:31:10 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2576eb06-f883-4e25-944d-4a1f4c1e57fc | ed209b8e-6b25-4764-b1c2-5e04ec1d01e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 624505 | 2025-07-31 13:36:22 AEST | 2025-07-31 09:31:10 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
11acccef-68fe-4377-a8bd-bb0e49859f3a | ed209b8e-6b25-4764-b1c2-5e04ec1d01e3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 518376 | 2025-07-31 13:36:21 AEST | 2025-07-31 09:31:10 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
44771b59-7f54-4111-b860-eb6f9c2596a3 | cb3e1f88-0dcd-4b5b-92de-9f8390deea54 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 341590 | 2025-07-27 21:08:54 AEST | 2025-07-27 18:33:30 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
6584974a-639c-4fea-abd5-0cf43e238304 | cb3e1f88-0dcd-4b5b-92de-9f8390deea54 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 326950 | 2025-07-27 21:08:51 AEST | 2025-07-27 18:33:36 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
9aa900c1-31d0-4e1c-a238-c1277cc1e0ad | cb3e1f88-0dcd-4b5b-92de-9f8390deea54 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 249849 | 2025-07-27 21:08:48 AEST | 2025-07-27 18:36:20 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a31c0952-da4d-4d29-8e99-813783262cc8 | 6bf454ee-f2b0-414b-bcb7-7dbe150c9ce2 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 335562 | 2025-07-27 21:08:46 AEST | 2025-07-27 18:43:01 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
3baca9c7-022d-4a2a-869b-6f8200c77332 | 6bf454ee-f2b0-414b-bcb7-7dbe150c9ce2 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 282784 | 2025-07-27 21:08:43 AEST | 2025-07-27 18:43:14 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c0109a4d-e3e8-4bff-a9f0-e8fba56d214b | 6bf454ee-f2b0-414b-bcb7-7dbe150c9ce2 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 308762 | 2025-07-27 21:08:40 AEST | 2025-07-27 18:43:47 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
cd3d274f-959c-4823-9530-d38dc1fb6c02 | f2c8edd3-54b8-4298-a633-cc03289de1aa | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 638996 | 2025-07-31 13:36:27 AEST | 2025-07-31 09:33:02 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fccafe11-9ba1-4f61-bd5c-f7300230d06c | f2c8edd3-54b8-4298-a633-cc03289de1aa | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 527169 | 2025-07-31 13:36:25 AEST | 2025-07-31 09:33:02 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cc272869-3584-4df2-9bc5-e54c144fd94b | f2c8edd3-54b8-4298-a633-cc03289de1aa | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 416944 | 2025-07-31 13:36:24 AEST | 2025-07-31 09:33:02 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b9f88f98-91f1-4a99-80dc-0fcc79827c40 | 91255cb9-8493-4a9b-b6a1-dfb1cad90bbf | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 691472 | 2025-07-31 13:36:29 AEST | 2025-07-31 09:40:47 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ea32ae07-b823-4520-8f26-8196b85ad429 | 91255cb9-8493-4a9b-b6a1-dfb1cad90bbf | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 723373 | 2025-07-31 13:36:30 AEST | 2025-07-31 09:40:47 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5d1dafbf-97e5-4a95-97bb-6463d92e4785 | 6fa797c6-42f2-431a-9908-185da306164c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3191 | 118.5848 | POINT (118.584775 -20.319069444444445) | 228301 | 2025-07-27 18:51:32 AEST | 2025-07-27 18:43:26 AEST | 0 | 2025-07-27 | 00:43:25 | 1414.0162 | 329.3521 | T | -20.3191 | S | 118.5848 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
062632a3-779b-49d9-8896-e426de0a7d1f | 47231d0c-cc6c-4d84-8f5a-908503133a3e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 510101 | 2025-07-31 13:36:37 AEST | 2025-07-31 09:43:43 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3ca9c28b-a84f-4630-9b4f-02465cf46de9 | 47231d0c-cc6c-4d84-8f5a-908503133a3e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 629645 | 2025-07-31 13:36:35 AEST | 2025-07-31 09:43:43 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
aaf3dbfb-0acd-419e-92a9-42309929fc1f | 47231d0c-cc6c-4d84-8f5a-908503133a3e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 456087 | 2025-07-31 13:36:32 AEST | 2025-07-31 09:43:43 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f24fb635-4a88-4f79-9dd6-b81d81d5f6d8 | 47231d0c-cc6c-4d84-8f5a-908503133a3e | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 400494 | 2025-07-31 13:36:34 AEST | 2025-07-31 09:43:43 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f856f1d7-a692-47dc-a0bb-a21a0aecbd23 | 53d6b10b-086e-4381-8b15-cecc73860404 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 652590 | 2025-07-31 13:36:38 AEST | 2025-07-31 09:52:19 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3a6b8936-d794-4de5-a4ad-94d2d0d1f2b8 | ec43b587-91b0-45c3-a467-8d7325623ce3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 287343 | 2025-07-27 18:51:37 AEST | 2025-07-27 18:55:29 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
8c7a7c0b-7e1c-4887-bd6b-250b2ed306e2 | ec43b587-91b0-45c3-a467-8d7325623ce3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 891701 | 2025-07-31 03:53:47 AEST | 2025-07-31 09:32:15 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
291277bb-9d78-4540-a02d-c015234cb742 | ec43b587-91b0-45c3-a467-8d7325623ce3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 834521 | 2025-07-31 01:58:06 AEST | 2025-07-31 09:32:15 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
4f130d79-ccf9-49cd-a811-01fb7df13452 | ec43b587-91b0-45c3-a467-8d7325623ce3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 853504 | 2025-07-31 01:58:36 AEST | 2025-07-31 09:32:15 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c2f95db6-cfad-4990-a4a0-2f615f3ae1dd | ec43b587-91b0-45c3-a467-8d7325623ce3 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 831826 | 2025-07-31 01:58:17 AEST | 2025-07-31 09:32:15 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c29b5e9d-be15-414c-8f36-ec511d85470f | ce66b86b-d6d7-4841-9508-fda6159a4479 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 760890 | 2025-07-31 01:33:26 AEST | 2025-07-31 09:28:51 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
866c2bcd-2b87-46fe-8ce8-5280ed8151cf | ce66b86b-d6d7-4841-9508-fda6159a4479 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 796324 | 2025-07-31 01:33:51 AEST | 2025-07-31 09:28:51 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
bf3b5ea7-ca69-45b5-ad4d-998cc54127df | c7246497-e015-445d-9194-a766b87aa3f8 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3181 | 118.5775 | POINT (118.5774611111111 -20.318055555555556) | 238562 | 2025-07-24 19:39:21 AEST | 2025-07-24 22:34:13 AEST | 18.0988 | 2025-07-24 | 04:15:40 | 4.1272 |  |  | -20.3181 | S | 118.5775 | E | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
9437d88a-97b7-40bd-8de8-48d754bf5b53 | c7246497-e015-445d-9194-a766b87aa3f8 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3181 | 118.5775 | POINT (118.5774611111111 -20.318055555555556) | 194218 | 2025-07-24 19:39:18 AEST | 2025-07-24 22:34:34 AEST | 18.0988 | 2025-07-24 | 04:15:40 | 4.1272 |  |  | -20.3181 | S | 118.5775 | E | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
015fa61f-b7ac-4bb1-bba1-81e56f27e289 | c7246497-e015-445d-9194-a766b87aa3f8 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 562719 | 2025-07-31 13:36:41 AEST | 2025-07-31 09:55:50 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
56bb517f-5714-4e34-a7e5-9cd72cb20e4b | f1740844-b413-4d1b-96cf-aecd4220af76 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 351403 | 2025-07-27 21:08:25 AEST | 2025-07-27 19:01:55 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
07ef5408-fed4-481d-8378-083e3d230d6c | f1740844-b413-4d1b-96cf-aecd4220af76 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 273380 | 2025-07-27 21:08:22 AEST | 2025-07-27 19:11:57 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
3b248b83-03f5-4872-9a87-45f418f0c28e | 5d16ced9-2080-44c0-8a39-84ba43464e74 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 179794 | 2025-07-24 13:54:26 AEST | 2025-07-24 18:44:45 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
19957fec-eb50-4ab0-803b-70d371148e85 | 5d16ced9-2080-44c0-8a39-84ba43464e74 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 180325 | 2025-07-24 13:54:24 AEST | 2025-07-24 18:45:02 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e7d12f43-43c0-43ac-975c-250179517e91 | 5d16ced9-2080-44c0-8a39-84ba43464e74 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 324302 | 2025-07-24 13:54:21 AEST | 2025-07-24 18:49:51 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
545a2d48-efdd-4fcf-aca2-8f26a242cf3b | 5d16ced9-2080-44c0-8a39-84ba43464e74 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 350759 | 2025-07-24 13:54:15 AEST | 2025-07-24 18:50:05 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
097396cd-71fa-4f50-b93b-09c5ae69795d | 52835ce1-9f6b-478a-bfc2-ea0fb49314d6 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 353304 | 2025-07-24 13:53:48 AEST | 2025-07-24 19:41:20 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
01dc7d8c-a8cf-4706-a26b-35492e80a333 | 52835ce1-9f6b-478a-bfc2-ea0fb49314d6 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 356302 | 2025-07-24 13:53:44 AEST | 2025-07-24 19:43:05 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
60094446-53aa-4d21-b4d1-3a7059b51c81 | 24b0f38f-edf9-4e95-a8ef-0008d5c0f173 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 391191 | 2025-07-24 13:52:37 AEST | 2025-07-24 20:51:22 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
38d411ad-5a15-4b9a-8ae8-496a16ff8ffe | 52f9cb96-c662-4449-a6ce-637c1a458c96 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3359 | 118.5913 | POINT (118.59134722222221 -20.33593611111111) | 366226 | 2025-07-24 19:36:30 AEST | 2025-07-25 03:07:27 AEST | 6.044 | 2025-07-24 | 09:07:28 | 3053.5743 | 219.465 | T | -20.3359 | S | 118.5913 | E | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
946dcbdc-530c-4f50-a7dd-3cafa3cb8a9f | 52f9cb96-c662-4449-a6ce-637c1a458c96 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3359 | 118.5913 | POINT (118.59134722222221 -20.33593611111111) | 462461 | 2025-07-24 19:36:26 AEST | 2025-07-25 03:07:50 AEST | 6.044 | 2025-07-24 | 09:07:28 | 3053.5743 | 16.8598 | T | -20.3359 | S | 118.5913 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
527a5ddf-e4a9-4030-9010-738548f1dfc2 | 0ecdf409-1778-42fa-b048-874adec21c74 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3177 | 118.5825 | POINT (118.58249444444444 -20.317691666666665) | 363689 | 2025-07-24 19:36:23 AEST | 2025-07-25 03:14:31 AEST | 6.044 | 2025-07-24 | 09:10:54 | 1414 | 238.1974 | T | -20.3177 | S | 118.5825 | E | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
93427d72-c697-426e-b5d2-b1ee4778fcde | 0ecdf409-1778-42fa-b048-874adec21c74 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3177 | 118.5825 | POINT (118.58249444444444 -20.317691666666665) | 423294 | 2025-07-24 19:36:20 AEST | 2025-07-25 03:14:50 AEST | 6.044 | 2025-07-24 | 09:10:54 | 1414 | 14.9749 | T | -20.3177 | S | 118.5825 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
4e267ca7-3736-4a38-b995-554c26934a28 | 99211911-a794-4510-a35e-fc79b29c502f | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3824 | 118.6076 | POINT (118.60760833333333 -20.38238611111111) | 399561 | 2025-07-24 19:36:16 AEST | 2025-07-25 03:18:57 AEST | 6.044 | 2025-07-24 | 09:17:00 | 9016.3909 |  |  | -20.3824 | S | 118.6076 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
4d13a672-0665-438b-bd37-735376a21758 | 8b5e9d67-7734-4262-80b6-cb54eb0c2648 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3277 | 118.5848 | POINT (118.58481388888889 -20.327694444444443) | 374189 | 2025-07-24 19:36:10 AEST | 2025-07-25 03:24:19 AEST | 6.044 | 2025-07-24 | 09:21:23 | 2836.9636 |  |  | -20.3277 | S | 118.5848 | E | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
a54b2046-7cb0-407e-9aa8-6c6e025b8f18 | 8b5e9d67-7734-4262-80b6-cb54eb0c2648 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3277 | 118.5848 | POINT (118.58481388888889 -20.327694444444443) | 442262 | 2025-07-24 19:36:05 AEST | 2025-07-25 03:24:32 AEST | 6.044 | 2025-07-24 | 09:21:23 | 2836.9636 |  |  | -20.3277 | S | 118.5848 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
9b760a84-758f-47b4-8d70-1c62e770f717 | 8b5e9d67-7734-4262-80b6-cb54eb0c2648 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3277 | 118.5848 | POINT (118.58481388888889 -20.327694444444443) | 414698 | 2025-07-24 19:36:02 AEST | 2025-07-25 03:24:41 AEST | 6.044 | 2025-07-24 | 09:21:23 | 2836.9636 |  |  | -20.3277 | S | 118.5848 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c0891d8f-55b5-4144-8230-1817a279f730 | 67758db5-619b-49af-af62-edd0d63537ff | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 327243 | 2025-07-27 21:09:36 AEST | 2025-07-27 18:02:31 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
23d8fa15-6854-4614-9185-e2d19f21864b | db6b7a25-e866-4c8e-8ed7-ade0c3d19641 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 402955 | 2025-07-27 21:09:33 AEST | 2025-07-27 18:03:22 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c2783fad-1161-49d5-a994-a6489035b305 | db6b7a25-e866-4c8e-8ed7-ade0c3d19641 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 399246 | 2025-07-27 21:09:30 AEST | 2025-07-27 18:03:39 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
76509de0-ec14-4698-b747-9a50c20cce57 | db6b7a25-e866-4c8e-8ed7-ade0c3d19641 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 426237 | 2025-07-27 21:09:27 AEST | 2025-07-27 18:03:49 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
48cd6ed3-edf9-4907-a1b2-322d8c963320 | e016950b-fc3b-46f1-8ec5-25de4831dad6 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 347571 | 2025-07-27 21:09:25 AEST | 2025-07-27 18:10:26 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
6e781fc1-0ebc-4f25-b6ba-c3373bec7671 | e016950b-fc3b-46f1-8ec5-25de4831dad6 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 370277 | 2025-07-27 21:09:22 AEST | 2025-07-27 18:10:38 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
47773162-ebe4-4f16-a7ca-63a87a981db4 | e016950b-fc3b-46f1-8ec5-25de4831dad6 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.318 | 118.5775 | POINT (118.57747777777777 -20.317977777777777) | 398755 | 2025-07-27 21:09:20 AEST | 2025-07-27 18:10:44 AEST | 32.0599 | 2025-07-26 | 23:43:53 | 14 |  |  | -20.318 | S | 118.5775 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
98ffc14d-42e5-4b7a-b490-e2322fc19524 | 145e8573-63b1-43d4-adac-d27f236808fd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 330265 | 2025-07-27 21:09:14 AEST | 2025-07-27 18:16:51 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
4d3e5032-d9be-4889-9941-1f97a1de8915 | 145e8573-63b1-43d4-adac-d27f236808fd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 362867 | 2025-07-27 21:09:12 AEST | 2025-07-27 18:16:58 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
04c13aec-2179-47f4-80be-f0d91377866a | 145e8573-63b1-43d4-adac-d27f236808fd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 311175 | 2025-07-27 21:09:09 AEST | 2025-07-27 18:17:05 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
8fba2f53-10af-486d-b8d7-bc8dc28df1ad | 145e8573-63b1-43d4-adac-d27f236808fd | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 233424 | 2025-07-27 21:09:06 AEST | 2025-07-27 18:17:18 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
91793c2b-ea31-49a9-8b04-a58e60f9e7cf | 261a1084-9b65-4201-ac6b-0c0758f128f2 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 387660 | 2025-07-27 21:09:04 AEST | 2025-07-27 18:24:24 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
959982cc-234d-47a9-8451-03f9506ab7ef | 261a1084-9b65-4201-ac6b-0c0758f128f2 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 307015 | 2025-07-27 21:09:01 AEST | 2025-07-27 18:24:46 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a2828155-9c62-4c55-bb7f-6b48e0ac0ed4 | f2090ec0-b174-450f-9862-d007dc996b66 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 323128 | 2025-07-27 21:08:38 AEST | 2025-07-27 18:47:36 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
2a529fe5-b4f4-48bb-a035-20f815b06974 | f2090ec0-b174-450f-9862-d007dc996b66 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 285057 | 2025-07-27 21:08:35 AEST | 2025-07-27 18:47:54 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e502f0bf-53c2-4cb1-a50b-77dc4cb59cbb | a795ab06-9bb5-42eb-a3fb-d27a7627965c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 339231 | 2025-07-27 21:08:33 AEST | 2025-07-27 18:54:11 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
f75d2e9a-b41e-4754-a71a-d8200d9b0ebe | a795ab06-9bb5-42eb-a3fb-d27a7627965c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 370381 | 2025-07-27 21:08:30 AEST | 2025-07-27 18:54:25 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
844078b0-8358-4377-971f-ac0836610139 | a795ab06-9bb5-42eb-a3fb-d27a7627965c | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | 0 | 0 | POINT (0.0 0.0) | 366564 | 2025-07-27 21:08:27 AEST | 2025-07-27 18:54:42 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e10cf5c7-dc80-44c0-88b7-84733e33947e | e94d5682-40db-4bbd-b8af-25897f458f62 | 8b7848f5-ea70-441e-9cab-b4cf7767517e | 1 |  | -20.3188 | 118.5844 | POINT (118.58442222222222 -20.31876388888889) | 232606 | 2025-07-27 10:04:57 AEST | 2025-07-27 18:04:22 AEST | 0 | 2025-07-27 | 00:01:18 | 1414 | 290.9374 | T | -20.3188 | S | 118.5844 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
17ecac67-9f2c-4626-8312-fe2b1ca3961f | 7fbfc3d9-efaf-4b5d-9b73-03d86c53982b | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 600371 | 2025-07-30 07:21:44 AEST | 2025-07-30 13:48:11 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
216c1312-6328-4933-8e87-de87eee37aaf | 7fbfc3d9-efaf-4b5d-9b73-03d86c53982b | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 542083 | 2025-07-30 07:21:46 AEST | 2025-07-30 13:48:11 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
567a6403-454e-4860-ad56-d42c98f8c972 | 1710c6d4-61e0-4c8a-a7ed-19479dfba14e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 563870 | 2025-07-31 13:36:55 AEST | 2025-07-31 10:01:46 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
594689d4-5983-44c1-8d1c-7f6d0d07aa1e | 1710c6d4-61e0-4c8a-a7ed-19479dfba14e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 378369 | 2025-07-31 13:36:53 AEST | 2025-07-31 10:01:46 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
147dbef6-359c-43c4-badd-5812b8d2dabb | 42f1d22b-f753-4f54-8291-c5813db7c249 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 291183 | 2025-07-27 18:51:40 AEST | 2025-07-27 19:45:19 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
3f42379c-0473-47ed-99d9-2ee726575e3b | 42f1d22b-f753-4f54-8291-c5813db7c249 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 248779 | 2025-07-27 18:51:43 AEST | 2025-07-27 19:45:54 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
a4e79f0f-a22d-432c-8aca-41b9f9b5e44e | 32e472ef-d0fe-4665-a056-a1128d2c943e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 586078 | 2025-07-31 13:36:58 AEST | 2025-07-31 10:07:25 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b9161e4d-aa96-47a5-b175-7a23b85150c5 | 32e472ef-d0fe-4665-a056-a1128d2c943e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 437873 | 2025-07-31 13:36:57 AEST | 2025-07-31 10:07:25 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b68f5104-6016-4a87-8373-da558181fe70 | e0d42ab3-f475-4964-a511-03c62b182c63 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3459 | 118.5931 | POINT (118.59311944444444 -20.34588611111111) | 406514 | 2025-07-25 13:07:46 AEST | 2025-07-25 17:53:11 AEST | 5.8245 | 2025-07-24 | 23:49:36 | 3871.4019 |  |  | -20.3459 | S | 118.5931 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5e1e81b1-0573-4855-91b6-dda82f664aa8 | e0d42ab3-f475-4964-a511-03c62b182c63 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3459 | 118.5931 | POINT (118.59311944444444 -20.34588611111111) | 558423 | 2025-07-25 13:07:42 AEST | 2025-07-25 17:53:19 AEST | 5.8245 | 2025-07-24 | 23:49:36 | 3871.4019 |  |  | -20.3459 | S | 118.5931 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
0ceadfff-8b82-45ba-90eb-6ca6982cbb15 | d3186fe8-24a0-4760-8484-dbb066413850 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 324333 | 2025-07-27 21:08:04 AEST | 2025-07-27 19:50:22 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d0090442-116a-45e1-8de5-394873aab1b8 | d3186fe8-24a0-4760-8484-dbb066413850 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 359507 | 2025-07-27 21:08:02 AEST | 2025-07-27 19:50:33 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
08aae027-4327-4a4c-9201-f348976270e5 | d3186fe8-24a0-4760-8484-dbb066413850 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 358880 | 2025-07-27 21:07:59 AEST | 2025-07-27 19:50:40 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c17e1768-1cd2-4586-a6c0-cab8388ffa43 | 96b06505-3f42-4a94-94be-8eae1678b3de | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 494657 | 2025-07-31 13:37:00 AEST | 2025-07-31 10:13:24 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
90e45305-359a-446e-8165-b03d791c811a | 96b06505-3f42-4a94-94be-8eae1678b3de | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 471366 | 2025-07-31 13:37:01 AEST | 2025-07-31 10:13:24 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2ed79450-3592-46c3-b109-d5fd5d509b48 | f2261ef7-ab7b-4cb7-b6ed-3be2136d7242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 365924 | 2025-07-24 19:39:00 AEST | 2025-07-24 23:00:45 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
bfc851af-aeb5-4ae3-9090-4a6ac9bd3d07 | f2261ef7-ab7b-4cb7-b6ed-3be2136d7242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 370376 | 2025-07-24 19:38:54 AEST | 2025-07-24 23:00:50 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e09099f4-96af-4e21-b13e-ccd619954aa0 | a84fe528-8a52-4fb2-8cdc-a7c2ab1579c8 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 382970 | 2025-07-24 19:39:06 AEST | 2025-07-24 22:57:12 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
980af16f-ffb4-4903-b932-f4973a1052fe | a84fe528-8a52-4fb2-8cdc-a7c2ab1579c8 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 431360 | 2025-07-31 13:37:03 AEST | 2025-07-31 10:14:29 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3fe707fe-b895-42fb-813c-23c54f349cc2 | 944aa3dc-3761-4f16-8bdf-36e9299ced31 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 347662 | 2025-07-24 19:38:47 AEST | 2025-07-24 23:03:56 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
009e8891-71a2-4c2d-9057-cece436eab37 | 944aa3dc-3761-4f16-8bdf-36e9299ced31 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 335240 | 2025-07-24 19:38:43 AEST | 2025-07-24 23:04:15 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
4bdc9ec1-04ce-464a-b4d1-13801d8ad6fe | 944aa3dc-3761-4f16-8bdf-36e9299ced31 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 446391 | 2025-07-31 13:37:05 AEST | 2025-07-31 10:16:25 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
aa695c81-7d5d-4684-b584-83ad4a01cd09 | 944aa3dc-3761-4f16-8bdf-36e9299ced31 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 512429 | 2025-07-31 13:37:06 AEST | 2025-07-31 10:16:25 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
851cf4cb-b0e6-404a-865e-c41583d71788 | d926d0e6-cf18-4e37-99ed-76a3a87ff7dd | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 353907 | 2025-07-25 13:07:21 AEST | 2025-07-25 18:09:50 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c759d1e6-5767-449f-85ab-6ae795f47275 | d926d0e6-cf18-4e37-99ed-76a3a87ff7dd | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 404464 | 2025-07-25 13:07:15 AEST | 2025-07-25 18:10:04 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
51bd2c66-7b34-47f5-aafd-0bd7ff2237e3 | ff91313f-39b8-4589-9a7a-ed54db9a9db9 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 320973 | 2025-07-27 21:07:51 AEST | 2025-07-27 20:25:32 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
08e3cf9c-feb2-463d-8a40-3c32a9f838e8 | ff91313f-39b8-4589-9a7a-ed54db9a9db9 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 252583 | 2025-07-27 21:07:48 AEST | 2025-07-27 20:25:41 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
8883205d-1ea2-4640-956d-0b703a792b81 | 16753271-57e9-4d5c-8f31-9edca63f0118 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 333664 | 2025-07-24 19:38:39 AEST | 2025-07-24 23:13:17 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
6f7afc6d-77f4-4ab0-814d-2ee08a3a2003 | 16753271-57e9-4d5c-8f31-9edca63f0118 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 403055 | 2025-07-24 19:38:36 AEST | 2025-07-24 23:13:59 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c69ac7e5-4fe6-4eb5-bf39-13564b5d3e17 | 115b0a2b-d1fb-4d9f-84e9-499d97f8f539 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 328588 | 2025-07-27 21:07:46 AEST | 2025-07-27 20:26:45 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
66013d1d-477b-4f76-80ba-3a1e2ec79552 | bc04c14e-29c7-4203-88ba-7ed1b83884cd | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 522164 | 2025-07-31 13:37:10 AEST | 2025-07-31 10:21:03 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c2d1521f-3322-4387-aa63-52addeb30542 | bc04c14e-29c7-4203-88ba-7ed1b83884cd | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 539407 | 2025-07-31 13:37:08 AEST | 2025-07-31 10:21:03 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
45b2a4da-8c19-4ff4-933e-999a7999a018 | a3b1601f-0f5a-48de-b90b-0d84fce6e195 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 522047 | 2025-07-24 19:38:21 AEST | 2025-07-24 23:18:17 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c17e32ff-ea48-45bc-9b0d-4215c49d8733 | a3b1601f-0f5a-48de-b90b-0d84fce6e195 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 555503 | 2025-07-30 07:21:49 AEST | 2025-07-30 13:54:42 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
83d13c09-ab64-4b15-872b-e84fe58a08fe | af2c465b-8e65-446d-9137-5e7bb38ac640 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 662485 | 2025-07-31 13:37:15 AEST | 2025-07-31 10:24:31 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
18756f34-5407-4618-9db1-6ba735354a39 | af2c465b-8e65-446d-9137-5e7bb38ac640 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 630641 | 2025-07-31 13:37:13 AEST | 2025-07-31 10:24:31 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4c9e4591-108b-4bd4-812b-59afd1d10b36 | af2c465b-8e65-446d-9137-5e7bb38ac640 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 530645 | 2025-07-31 13:37:11 AEST | 2025-07-31 10:24:31 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6b179a76-c691-4fd5-b800-5ad76e7b1598 | 143f5c06-9626-434c-9cd9-3e1f660d8373 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3166 | 118.5818 | POINT (118.58184444444444 -20.316594444444444) | 239682 | 2025-07-27 18:51:48 AEST | 2025-07-27 20:35:22 AEST | 0 | 2025-07-27 | 02:31:22 | 1414 |  |  | -20.3166 | S | 118.5818 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
efd1e213-2e9d-46a2-9cc4-f69f9cfa3c66 | 0fe2650e-2584-4b90-a5e3-1cf57fe70c8f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 356224 | 2025-07-25 13:07:00 AEST | 2025-07-25 18:32:20 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
181de8d8-c7eb-4fc4-8a37-1cb1094858de | 0fe2650e-2584-4b90-a5e3-1cf57fe70c8f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 364996 | 2025-07-25 13:06:56 AEST | 2025-07-25 18:32:28 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5d0a197c-4aa0-40db-b3db-d0eb05ba8de1 | 0fe2650e-2584-4b90-a5e3-1cf57fe70c8f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 310089 | 2025-07-25 13:06:49 AEST | 2025-07-25 18:32:34 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
4d30c096-b648-428d-8d62-e08d740f278c | 0fe2650e-2584-4b90-a5e3-1cf57fe70c8f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 335037 | 2025-07-25 13:06:44 AEST | 2025-07-25 18:32:56 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
a2eac470-bcce-4779-bb14-2ec8b1ddfa48 | 28316751-8de6-4c86-91c9-bd4e7c968072 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 424674 | 2025-07-24 19:38:15 AEST | 2025-07-24 23:27:24 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d24ab333-0cff-43b8-973a-bfa16a23bb97 | d36b435e-176a-4318-afe2-704509881880 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 441630 | 2025-07-25 13:06:40 AEST | 2025-07-25 18:40:18 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
bb2122d9-92e7-4ccb-b7d0-9943ea437e2a | d36b435e-176a-4318-afe2-704509881880 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 482337 | 2025-07-25 13:06:36 AEST | 2025-07-25 18:40:26 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c1766210-0a1e-4109-ae1d-df32805cfeda | d36b435e-176a-4318-afe2-704509881880 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 629556 | 2025-07-31 13:37:17 AEST | 2025-07-31 10:31:43 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
642c2038-d25a-4b63-b6a9-0ec6b991e8cd | d36b435e-176a-4318-afe2-704509881880 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 690766 | 2025-07-31 13:37:19 AEST | 2025-07-31 10:31:43 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
197380bb-f5cc-46ed-8db3-41c07e41a919 | ca0be67e-038b-483c-8e0a-22b9064ac50d | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3168 | 118.5676 | POINT (118.56757859999752 -20.3167924) | 455621 | 2025-07-30 03:28:18 AEST | 2025-07-30 11:08:35 AEST |  |  |  | 2400 |  |  | -20.3168 | S | 118.5676 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ce4f9743-107d-47d5-9a27-25593b68de39 | ca0be67e-038b-483c-8e0a-22b9064ac50d | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3168 | 118.5676 | POINT (118.56757859999752 -20.3167924) | 473450 | 2025-07-30 03:28:09 AEST | 2025-07-30 11:08:35 AEST |  |  |  | 2400 |  |  | -20.3168 | S | 118.5676 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d391c50f-1aef-4bd0-9c5f-45ed2b40fb78 | 615b9232-d5a9-46c0-bb03-35440f368438 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 555271 | 2025-07-30 07:21:51 AEST | 2025-07-30 13:59:09 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b92e3758-2851-4fab-9ba7-accdf753165c | 615b9232-d5a9-46c0-bb03-35440f368438 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 632736 | 2025-07-30 07:21:53 AEST | 2025-07-30 13:59:09 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
02ddb68a-93ad-44e9-95c2-ae5f12a59c44 | 1879fef6-78c2-4a05-9d19-abdc343b9c25 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3169 | 118.5822 | POINT (118.58219722222222 -20.316908333333334) | 252711 | 2025-07-27 18:51:50 AEST | 2025-07-27 20:40:33 AEST | 0 | 2025-07-27 | 02:39:37 | 1414 | 132.7013 | T | -20.3169 | S | 118.5822 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
1035e897-6b73-435b-a916-8cc335ee600f | 1879fef6-78c2-4a05-9d19-abdc343b9c25 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3169 | 118.5822 | POINT (118.58219722222222 -20.316908333333334) | 252256 | 2025-07-27 18:51:53 AEST | 2025-07-27 20:41:02 AEST | 0 | 2025-07-27 | 02:39:37 | 1414 | 132.7013 | T | -20.3169 | S | 118.5822 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
ae678730-1ae3-4224-a520-202bbc72ec60 | 3b4147b3-654f-4372-8e6e-da43f89584a7 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 602875 | 2025-07-31 13:37:28 AEST | 2025-07-31 10:52:56 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
da5e99ee-6cab-47e7-80b9-9d7e1d19ba09 | 3b4147b3-654f-4372-8e6e-da43f89584a7 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 486606 | 2025-07-31 13:37:26 AEST | 2025-07-31 10:52:56 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e07a30fc-3e05-44b1-893f-64c285db46c5 | 3b4147b3-654f-4372-8e6e-da43f89584a7 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 574013 | 2025-07-31 13:37:23 AEST | 2025-07-31 10:52:56 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
389062cf-68e8-4422-b641-1f4bac9222cb | dbb410b4-4a19-44e5-b3ba-2a6d39793e3f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 459132 | 2025-07-31 13:37:20 AEST | 2025-07-31 10:48:07 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
172c90a0-6ce5-453b-8d26-4fe14492efce | dbb410b4-4a19-44e5-b3ba-2a6d39793e3f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 568149 | 2025-07-31 13:37:22 AEST | 2025-07-31 10:48:07 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b63ddcf9-d835-4d21-a5a3-47001ac7b236 | 88db7b21-6975-4182-b85a-a687d013620a | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 604812 | 2025-07-30 07:21:56 AEST | 2025-07-30 14:01:18 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6be264c3-869b-4c1f-919f-2fea14a4064f | 88db7b21-6975-4182-b85a-a687d013620a | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 529970 | 2025-07-30 07:21:58 AEST | 2025-07-30 14:01:18 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5287e053-161c-48c1-b58f-7ecfefe8f097 | 0487282e-bf88-4339-8fc5-19b893d61a30 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 535290 | 2025-07-30 07:22:01 AEST | 2025-07-30 14:02:19 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b02c9e11-506e-40b6-bf31-a397ba75f97f | 0487282e-bf88-4339-8fc5-19b893d61a30 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 533224 | 2025-07-30 07:22:03 AEST | 2025-07-30 14:02:19 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6cf73877-517a-4d7a-b230-fd10f522a7d5 | 0487282e-bf88-4339-8fc5-19b893d61a30 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 638992 | 2025-07-31 03:49:29 AEST | 2025-07-31 11:01:06 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
4347583f-11eb-4884-8a00-767f5baa24a6 | c657af51-ae9f-4877-bc6b-f30f9f77ec4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 580509 | 2025-07-30 07:22:12 AEST | 2025-07-30 14:04:54 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c48f76c1-7ef6-4e9a-b1e8-321d23ade35c | c657af51-ae9f-4877-bc6b-f30f9f77ec4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 632885 | 2025-07-30 07:22:05 AEST | 2025-07-30 14:04:53 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
505a4432-210f-462f-a497-8510d2c59145 | c657af51-ae9f-4877-bc6b-f30f9f77ec4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 583954 | 2025-07-30 07:22:10 AEST | 2025-07-30 14:04:53 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b1d80fb0-f43b-4a13-8cf8-998046819e71 | c657af51-ae9f-4877-bc6b-f30f9f77ec4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 589531 | 2025-07-30 07:22:08 AEST | 2025-07-30 14:04:53 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
aa239e71-34f0-4977-9c77-3572d4876692 | 1dc02521-fc42-4fb5-b212-f62ae80aad1a | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 311520 | 2025-07-25 13:06:19 AEST | 2025-07-25 19:06:26 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
030c2f33-bfac-431b-bec6-281f2f9cca8f | 1d491ce6-3b3f-46f2-88ea-8358a606337a | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 374295 | 2025-07-27 21:07:36 AEST | 2025-07-27 20:40:45 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
cf242fb2-0cee-47b6-b9b1-06311aa9a4d6 | 1d491ce6-3b3f-46f2-88ea-8358a606337a | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 398923 | 2025-07-27 21:07:33 AEST | 2025-07-27 20:40:53 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
408fc1e5-abe7-478d-ad25-d28f2594d622 | 8b323d24-707d-4a58-905b-753f200f867f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 383690 | 2025-07-27 21:07:30 AEST | 2025-07-27 20:41:18 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
bd11729b-be76-4cfb-8515-568ef53ffa10 | 8b323d24-707d-4a58-905b-753f200f867f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 319188 | 2025-07-27 21:07:27 AEST | 2025-07-27 20:41:31 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
2bf42020-8525-40ce-b728-01a22d75952c | 7bbdcf2a-3e3c-4288-8d7a-cccc48a0968e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 364504 | 2025-07-24 19:37:49 AEST | 2025-07-24 23:49:05 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b3d75579-8b4c-4cc2-a290-1ea68e35df4d | fc6cb12c-3abf-42fb-84fe-e169992ac18f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 584715 | 2025-07-30 07:22:31 AEST | 2025-07-30 14:24:45 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
53ea838f-1b3e-46a4-a54d-04ebbdd27ea2 | fc6cb12c-3abf-42fb-84fe-e169992ac18f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 619483 | 2025-07-30 07:22:34 AEST | 2025-07-30 14:24:45 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4b6ed047-8f2d-4842-b554-1a467d3c9be7 | fc6cb12c-3abf-42fb-84fe-e169992ac18f | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 553324 | 2025-07-30 07:22:36 AEST | 2025-07-30 14:25:02 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1f383807-dda2-44bf-990e-70fe2d5a1c16 | 4ed6c3fb-51b0-4889-87c4-866c20047c14 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 304499 | 2025-07-27 21:07:21 AEST | 2025-07-27 20:46:46 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e087ab60-0124-496c-b357-fc17ccfe3b5c | 4ed6c3fb-51b0-4889-87c4-866c20047c14 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 319536 | 2025-07-27 21:07:19 AEST | 2025-07-27 20:46:54 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
51ddb580-d73d-4656-9add-5d590c8ce026 | b6b04f72-f84b-404c-b7d4-9fb2c0fdd347 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 568134 | 2025-07-30 07:22:38 AEST | 2025-07-30 14:26:25 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6ce506eb-d1bd-466f-adf0-ba47322aa89a | b6b04f72-f84b-404c-b7d4-9fb2c0fdd347 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 525164 | 2025-07-30 07:22:40 AEST | 2025-07-30 14:26:25 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
77eb2c02-36e8-4795-bd3f-e870c948599d | 2a1a4c83-8ea4-4dd0-842e-5c33ce02a242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 367168 | 2025-07-24 19:37:45 AEST | 2025-07-24 23:56:32 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
0991c975-a5f4-4f7d-b4b3-a3bae0fcbbb1 | 2a1a4c83-8ea4-4dd0-842e-5c33ce02a242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 434404 | 2025-07-24 19:37:41 AEST | 2025-07-24 23:56:45 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
034376b1-2ac6-4e8f-b9f6-c8f5a054efae | 2a1a4c83-8ea4-4dd0-842e-5c33ce02a242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 246624 | 2025-07-25 13:06:12 AEST | 2025-07-25 19:12:06 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7e194fef-3452-4d52-b3e8-5c35d4a5c19a | 2a1a4c83-8ea4-4dd0-842e-5c33ce02a242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 347277 | 2025-07-25 13:06:09 AEST | 2025-07-25 19:12:29 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7f8326c3-a552-43e0-aeac-9825c5f8d662 | 2a1a4c83-8ea4-4dd0-842e-5c33ce02a242 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 290997 | 2025-07-25 13:06:05 AEST | 2025-07-25 19:12:54 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
054fe918-8bcf-4ace-8091-9d3fa2321c85 | dc42b6e6-d96c-47fa-9872-69dd8e367d1d | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 850500 | 2025-07-30 04:11:55 AEST | 2025-07-30 11:44:44 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
15598619-cfe3-4def-a8a6-b39c79736847 | dc42b6e6-d96c-47fa-9872-69dd8e367d1d | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 712615 | 2025-07-30 04:11:52 AEST | 2025-07-30 11:44:44 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
68ff2951-be1c-4b47-90c3-43af9ae5d261 | fb38130e-79ad-4e0c-9634-5c5416702491 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 839063 | 2025-07-30 07:04:13 AEST | 2025-07-30 14:43:31 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
fcecca29-1e4d-4756-9b98-fb4c04f0ed8f | fb38130e-79ad-4e0c-9634-5c5416702491 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 775651 | 2025-07-30 07:04:10 AEST | 2025-07-30 14:43:31 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7c684ccd-1e9e-45bd-9da8-86f28806cbb3 | fb38130e-79ad-4e0c-9634-5c5416702491 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 642665 | 2025-07-30 07:04:07 AEST | 2025-07-30 14:43:31 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
f6b4bdae-9826-4a64-9953-1d527b2547f9 | fb38130e-79ad-4e0c-9634-5c5416702491 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 702298 | 2025-07-30 07:04:12 AEST | 2025-07-30 14:43:31 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
362e8b67-3148-4797-9922-a8df70b20429 | 7c684d64-27c3-45fe-8055-604ab7d0efad | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3166 | 118.5819 | POINT (118.58186944444444 -20.316613888888888) | 244757 | 2025-07-27 18:51:55 AEST | 2025-07-27 20:55:06 AEST | 0 | 2025-07-27 | 02:53:55 | 1414 |  |  | -20.3166 | S | 118.5819 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
f27f1438-08c6-4c9c-a4cf-88a659f63301 | 81fa51db-e471-48a1-b849-ddb41b2dde63 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 416359 | 2025-07-25 13:05:54 AEST | 2025-07-25 19:26:46 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
bc6fc61f-e969-45a5-98d9-e6966a6cb02a | 81fa51db-e471-48a1-b849-ddb41b2dde63 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 358214 | 2025-07-25 13:05:48 AEST | 2025-07-25 19:26:53 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
d0640ba1-4fc0-48ff-835c-2b436768794b | 81fa51db-e471-48a1-b849-ddb41b2dde63 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 359624 | 2025-07-25 13:05:13 AEST | 2025-07-25 19:27:02 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5dfd43a5-a7c9-4a8a-8edc-a6a9644438df | 8473e6e7-a930-43d7-9eda-59a2181c7150 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 673664 | 2025-07-31 13:37:29 AEST | 2025-07-31 11:17:13 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
94baee6d-104e-4d9e-9fc5-0de7dbabf30b | 8b35cc0f-b2c2-455e-97f2-4a3e3872e4d2 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 838283 | 2025-07-30 04:11:50 AEST | 2025-07-30 11:42:07 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
538018ee-16c0-4b90-af69-28df727d3cb8 | 8b35cc0f-b2c2-455e-97f2-4a3e3872e4d2 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 733000 | 2025-07-30 04:11:48 AEST | 2025-07-30 11:42:07 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
13b28973-ea6e-4042-9151-a10477849ec8 | ea55fece-29e8-49ff-a09f-2d07fd6e8093 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 422294 | 2025-07-25 13:04:55 AEST | 2025-07-25 19:32:52 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
8dc9cf0d-e027-4e15-9410-5dd6b56b2762 | ea55fece-29e8-49ff-a09f-2d07fd6e8093 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 414386 | 2025-07-25 13:04:50 AEST | 2025-07-25 19:33:10 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
27180985-7d73-4a4f-bbbf-b18964caf6f3 | cc192bcb-d96b-426e-93f1-c7aec99b401b | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 378474 | 2025-07-27 14:17:53 AEST | 2025-07-27 21:03:04 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
0814d7ca-1173-43b5-838e-9e49ff0fe9f9 | cc192bcb-d96b-426e-93f1-c7aec99b401b | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 412782 | 2025-07-27 14:17:45 AEST | 2025-07-27 21:03:13 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
9b3e4028-918c-41ff-97d8-854fa8686f63 | e39fbf86-3347-460e-9cad-7bf875633957 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 341001 | 2025-07-24 19:39:15 AEST | 2025-07-24 22:48:13 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d6a01c22-aa13-49e1-afe7-0763ddbb3450 | e39fbf86-3347-460e-9cad-7bf875633957 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 302378 | 2025-07-24 19:39:11 AEST | 2025-07-24 22:49:09 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a8c7fefb-76f0-4161-8aca-e68eb5749111 | 69848ba7-5067-473c-a0a6-aabde7f63f4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 387727 | 2025-07-25 13:07:53 AEST | 2025-07-25 17:38:29 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7a214d0c-f375-48d8-bc5a-ac29dd2f9e7e | 69848ba7-5067-473c-a0a6-aabde7f63f4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 316444 | 2025-07-25 13:07:49 AEST | 2025-07-25 17:39:24 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
77b1a188-ea20-4d55-90d8-19873545b021 | eb004917-0346-4551-bfbc-d374593080f4 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.364 | 118.6007 | POINT (118.60071666666666 -20.363991666666667) | 460716 | 2025-07-25 13:07:38 AEST | 2025-07-25 17:54:21 AEST | 5.8245 | 2025-07-24 | 23:53:45 | 5436.6683 |  |  | -20.364 | S | 118.6007 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7d84c3e0-f369-4ecf-971d-bf55b96ff3de | eb004917-0346-4551-bfbc-d374593080f4 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.364 | 118.6007 | POINT (118.60071666666666 -20.363991666666667) | 478467 | 2025-07-25 13:07:34 AEST | 2025-07-25 17:54:32 AEST | 5.8245 | 2025-07-24 | 23:53:45 | 5436.6683 |  |  | -20.364 | S | 118.6007 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
96a34f6b-d623-4bed-9ece-902cb40af92b | 77df86a5-4baf-4488-a554-e60750e3e57c | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 473631 | 2025-07-25 13:07:31 AEST | 2025-07-25 18:07:08 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
bdfb55ee-93b0-4296-8822-4218600a001e | 77df86a5-4baf-4488-a554-e60750e3e57c | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 508987 | 2025-07-25 13:07:27 AEST | 2025-07-25 18:07:30 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5d6add77-90a8-4780-bf44-bcacb468db92 | 77df86a5-4baf-4488-a554-e60750e3e57c | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 477966 | 2025-07-25 13:07:24 AEST | 2025-07-25 18:08:06 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
d4ae3a4e-8c26-4106-9dc5-890fa085df98 | a0f66257-212e-40cf-9beb-1edc3c3a43f0 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 473778 | 2025-07-25 13:06:00 AEST | 2025-07-25 19:20:54 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
42b3e9ab-005a-470e-b470-2247ba4baae1 | 5ab12c32-9958-4b96-adad-45aeb42722da | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 397383 | 2025-07-25 13:04:45 AEST | 2025-07-25 19:45:31 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
b6c5d5e7-3f85-4ac7-bd98-f783c67075b5 | 5ab12c32-9958-4b96-adad-45aeb42722da | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 480105 | 2025-07-25 13:04:41 AEST | 2025-07-25 19:45:58 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
81bbac93-4a1a-455b-ad29-2fd0372dd571 | 5ab12c32-9958-4b96-adad-45aeb42722da | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 470193 | 2025-07-25 13:04:37 AEST | 2025-07-25 19:46:08 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c2781dea-f321-4bf1-8d5f-b00e75ffe143 | 5ab12c32-9958-4b96-adad-45aeb42722da | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 445259 | 2025-07-25 13:04:32 AEST | 2025-07-25 19:46:56 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
37349411-f718-4e21-b757-b97b1eec81c2 | ba77adb3-6653-4e15-b56e-d41422bdd498 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 314863 | 2025-07-27 21:07:56 AEST | 2025-07-27 19:58:10 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d607b358-ec33-4f3e-bc14-58e56a689996 | ba77adb3-6653-4e15-b56e-d41422bdd498 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 409661 | 2025-07-27 21:07:54 AEST | 2025-07-27 19:58:22 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b6e34c9a-8871-4772-9aed-013e3a8ef475 | c0fd50df-219d-4d7c-8425-89746419eb7c | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 319954 | 2025-07-27 21:07:41 AEST | 2025-07-27 20:36:05 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
01c35591-18c0-44be-9023-e3946953064d | c0fd50df-219d-4d7c-8425-89746419eb7c | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 174863 | 2025-07-27 21:07:38 AEST | 2025-07-27 20:36:18 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
257fd7cc-a7bd-4107-b777-34e83de675d8 | 63bed447-87fe-41b6-a9fd-208ffd627a4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 262138 | 2025-07-27 21:07:16 AEST | 2025-07-27 20:54:59 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
fbb6f71b-f1ab-403b-8f9b-b5535db1b5ec | 63bed447-87fe-41b6-a9fd-208ffd627a4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 289664 | 2025-07-27 21:07:13 AEST | 2025-07-27 20:55:06 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
4670f672-a78b-4f87-a363-99c9199daf73 | 63bed447-87fe-41b6-a9fd-208ffd627a4e | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 379471 | 2025-07-27 21:07:10 AEST | 2025-07-27 20:55:17 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
98b7576d-ff49-4b59-8b32-95549e6cf4a5 | b717d79f-a2a2-492f-8c6f-df933bde5096 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3168 | 118.5821 | POINT (118.58210555555556 -20.316805555555554) | 313367 | 2025-07-27 18:51:45 AEST | 2025-07-27 20:28:40 AEST | 0 | 2025-07-27 | 02:25:17 | 1414 |  |  | -20.3168 | S | 118.5821 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
fa62baac-6192-4964-8099-c5b35728e9e7 | be4b2b48-d06e-479b-a1d2-7fb7b0058785 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3169 | 118.5822 | POINT (118.58216388888889 -20.316855555555556) | 288276 | 2025-07-27 18:51:58 AEST | 2025-07-27 20:58:15 AEST | 0 | 2025-07-27 | 02:55:37 | 1414 |  |  | -20.3169 | S | 118.5822 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
767fc84c-ecad-4ac0-a45d-33d8cb502346 | be4b2b48-d06e-479b-a1d2-7fb7b0058785 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3169 | 118.5822 | POINT (118.58216388888889 -20.316855555555556) | 215634 | 2025-07-27 18:52:00 AEST | 2025-07-27 20:58:39 AEST | 0 | 2025-07-27 | 02:55:37 | 1414 |  |  | -20.3169 | S | 118.5822 | E | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
e53136b1-bb5f-4bce-9dc3-02e1b4a87c2b | b354854a-efe7-4519-be31-f153b68d4f62 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 553363 | 2025-07-30 07:22:26 AEST | 2025-07-30 14:07:23 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
46569f63-4078-4a43-bdda-cef44db6f9ae | b354854a-efe7-4519-be31-f153b68d4f62 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 584180 | 2025-07-30 07:22:16 AEST | 2025-07-30 14:07:23 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a011678b-7c1d-46f6-87ce-c42555051c5c | b354854a-efe7-4519-be31-f153b68d4f62 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 641328 | 2025-07-30 07:22:14 AEST | 2025-07-30 14:07:23 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cec2a071-4cd0-4066-9dec-f48a8efb52de | b354854a-efe7-4519-be31-f153b68d4f62 | 17a3e0ee-6c5c-400c-9a82-bbf1db7fa495 | 1 |  | -20.3216 | 118.5854 | POINT (118.58540070000112 -20.321648699997933) | 623773 | 2025-07-30 07:22:29 AEST | 2025-07-30 14:07:23 AEST | 12.0696 |  |  | 21.3333 |  |  | -20.3216 | S | 118.5854 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a17b6967-5c44-48fd-8071-24df65b5dee9 | 3614605b-06e6-4abf-a23d-107639bf00dc | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 875754 | 2025-07-30 04:11:39 AEST | 2025-07-30 11:28:49 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
b1e0b785-e055-446d-b2e1-cc6fd45e9da4 | 3614605b-06e6-4abf-a23d-107639bf00dc | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 799190 | 2025-07-30 04:11:41 AEST | 2025-07-30 11:28:50 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
94a2063b-9289-4925-b635-6018c1b7b674 | 9590f0e5-2a88-466a-96b6-49c1cc334fc3 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 667578 | 2025-07-30 04:11:36 AEST | 2025-07-30 11:24:56 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
77154d75-8f3b-4f51-9466-537520b4ff79 | 9590f0e5-2a88-466a-96b6-49c1cc334fc3 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 687557 | 2025-07-30 04:11:34 AEST | 2025-07-30 11:24:56 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
3a5d6bf9-646f-4be6-8e5b-417581d0fed6 | 5ab0ed21-50c8-4fc2-8234-b6df798bb7a4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 801317 | 2025-07-30 04:11:32 AEST | 2025-07-30 11:22:47 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
2f071e7c-afde-4362-80ad-d761f2d4d373 | 5ab0ed21-50c8-4fc2-8234-b6df798bb7a4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 801317 | 2025-07-30 04:11:30 AEST | 2025-07-30 11:22:47 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7c964bc2-fcbc-4940-a124-a9a3162fb133 | 77b78753-0980-44c7-a372-e275a87c8c75 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 670666 | 2025-07-30 04:11:28 AEST | 2025-07-30 11:21:29 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
316909f7-4fcf-4713-94d2-b18f34dbc0c7 | b7f279d0-68d9-4d1b-847f-e57a109679f2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 650647 | 2025-07-30 04:10:13 AEST | 2025-07-30 11:41:21 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
80a0e5d1-407f-4028-a98c-4598d53261e3 | b7f279d0-68d9-4d1b-847f-e57a109679f2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 556774 | 2025-07-30 04:10:11 AEST | 2025-07-30 11:41:21 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
3654a9b3-f661-4d8a-b526-3a31756d6b2f | b7f279d0-68d9-4d1b-847f-e57a109679f2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 741435 | 2025-07-30 04:10:09 AEST | 2025-07-30 11:41:21 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
981e88ee-fe34-40b5-b40c-3d38a2309f69 | 3b68fd28-61e9-43d5-bc1c-6f23fd9c3d88 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 445997 | 2025-07-30 04:10:15 AEST | 2025-07-30 11:42:34 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
f3101b5f-417a-4003-8751-3ea45124ccdf | 3b68fd28-61e9-43d5-bc1c-6f23fd9c3d88 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 748271 | 2025-07-30 04:10:21 AEST | 2025-07-30 11:42:34 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
2bc8a569-7846-468c-a8ec-f6f1d06cb0f5 | 3b68fd28-61e9-43d5-bc1c-6f23fd9c3d88 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 576589 | 2025-07-30 04:10:24 AEST | 2025-07-30 11:42:34 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
d8707eed-2adc-4f8b-bee9-8dc7542c648b | f5a381ff-a308-4462-beb9-4e508b2d0b44 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 377816 | 2025-07-27 14:17:36 AEST | 2025-07-27 21:08:44 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
44a188c4-c34e-4219-9031-ff5fe8fa5c28 | f5a381ff-a308-4462-beb9-4e508b2d0b44 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 412146 | 2025-07-27 14:17:31 AEST | 2025-07-27 21:08:58 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
330c65c2-79d1-479f-a87b-786517480fea | 00003620-32b7-4ab2-a9b1-77e071e2f41b | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 781647 | 2025-07-30 04:11:26 AEST | 2025-07-30 11:16:12 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
76cf9420-1481-46e2-ab2c-0d1f59e71c16 | 4d28d489-954d-4658-a12d-8478861e2d0d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 530304 | 2025-07-30 04:10:29 AEST | 2025-07-30 11:45:26 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
27af9173-6fcb-4dac-88bc-16c48d9d20ce | 4d28d489-954d-4658-a12d-8478861e2d0d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 660431 | 2025-07-30 04:10:31 AEST | 2025-07-30 11:45:26 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
5b5a73ea-c583-416e-9d6d-b02e67debeb3 | e4a6536d-d9d1-4016-bcdb-adae304d3241 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 519067 | 2025-07-30 04:10:27 AEST | 2025-07-30 11:44:31 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
bddcb216-fade-49f5-a827-308b8df71126 | 005e5ec3-2f94-4a7b-922e-1e465fb8555d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 317986 | 2025-07-24 19:37:38 AEST | 2025-07-25 00:15:03 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d4a2e6e5-9b55-4bf9-b98e-6f20b83c1f75 | 005e5ec3-2f94-4a7b-922e-1e465fb8555d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 427672 | 2025-07-25 13:04:27 AEST | 2025-07-25 19:56:51 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
ba974a09-b0ff-4d7d-851d-4c547d9090f3 | 5bb7cd8b-5db7-4e59-b416-ee4807339fb5 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 563879 | 2025-07-30 04:10:34 AEST | 2025-07-30 11:48:45 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
4a53f3bc-01ae-4d70-8811-14c0a1e169cc | e8f3124e-9dc8-4b41-88aa-630ab7a34f82 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 586058 | 2025-07-30 04:10:07 AEST | 2025-07-30 11:26:36 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
a5d8cf3b-c42a-442b-a6cc-8c555944b793 | 02d065b8-b9b8-4ee9-bcd3-95cf99d10f0f | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 663784 | 2025-07-31 03:49:27 AEST | 2025-07-31 10:56:11 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
915b0e52-8414-4ac1-9024-85860751faf8 | ddeb89ca-5bc0-4d9d-81fa-25404a34053c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 231881 | 2025-07-27 14:17:20 AEST | 2025-07-27 21:24:27 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a5f72209-47f2-413e-8672-ff651cfd472e | ddeb89ca-5bc0-4d9d-81fa-25404a34053c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 248014 | 2025-07-27 14:17:15 AEST | 2025-07-27 21:24:37 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c6a989e2-5c82-4fcc-bd4b-38fcb741c153 | ddeb89ca-5bc0-4d9d-81fa-25404a34053c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 214113 | 2025-07-27 14:17:11 AEST | 2025-07-27 21:24:49 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
0a5983a9-e0ea-4eee-b15b-afe377cc09da | a06bda5e-15f7-49c3-b953-cc8b29ccd026 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 543208 | 2025-07-31 13:37:31 AEST | 2025-07-31 11:24:10 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
35a249d1-3055-4603-87c5-eff07fa81ee3 | a06bda5e-15f7-49c3-b953-cc8b29ccd026 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 503601 | 2025-07-31 13:37:33 AEST | 2025-07-31 11:24:10 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e8739648-0a67-4be9-8c24-9a518780e869 | 0ac8ca3c-5076-44bc-9108-cebf85a86b6d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 511074 | 2025-07-31 13:37:34 AEST | 2025-07-31 11:25:26 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9b1fedd2-b956-47a8-bda2-addb5a9471e4 | 0ac8ca3c-5076-44bc-9108-cebf85a86b6d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 485823 | 2025-07-31 13:37:38 AEST | 2025-07-31 11:25:26 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0a6701b3-eafd-4d16-9b6f-eeca00131a43 | bc2a137e-6bf1-4f6a-88b8-efac3b7e46a4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 780071 | 2025-07-30 04:10:04 AEST | 2025-07-30 11:24:54 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
ab45abe2-0ce9-42ad-8b1e-0e9882925441 | 3b27e960-8f9e-4ed8-9dc0-c529d6d4e011 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 790463 | 2025-07-30 04:11:21 AEST | 2025-07-30 11:12:25 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
3fe33895-0fc6-42db-8c41-e89edbaca186 | 3b27e960-8f9e-4ed8-9dc0-c529d6d4e011 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 738394 | 2025-07-30 04:11:23 AEST | 2025-07-30 11:12:25 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
a1a423d8-18c6-4f08-b879-e98e3b81cb89 | 4fdc513b-555b-4bf7-ad8a-ce9155f23838 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3187 | 118.5741 | POINT (118.5741444 -20.31867670000237) | 692403 | 2025-07-30 04:10:02 AEST | 2025-07-30 11:23:03 AEST |  |  |  | 900 |  |  | -20.3187 | S | 118.5741 | E | samsung | SM-S931B |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
ad50e967-5b3f-410f-9b98-d4c254dd22a2 | ee24910c-9d83-4f70-b028-22f055381942 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 624136 | 2025-07-31 13:37:40 AEST | 2025-07-31 11:30:35 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3053491c-356c-4153-b35a-9fffdd386b73 | ee24910c-9d83-4f70-b028-22f055381942 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 537730 | 2025-07-31 13:37:42 AEST | 2025-07-31 11:30:35 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bd3bad28-f8e6-44f8-99cc-200c886a65c0 | a10d714b-4a0f-4204-b0d6-5a6c51a36eb3 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 262870 | 2025-07-24 19:37:33 AEST | 2025-07-25 00:20:54 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
e194082a-bc77-4685-bf81-f3ff2967cfb3 | 95d9acd4-ca32-4708-859a-c6c5ea4feabf | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 602028 | 2025-07-31 03:49:25 AEST | 2025-07-31 10:53:19 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
4693a01f-aa99-4581-9a03-90fc7496e81f | 95d9acd4-ca32-4708-859a-c6c5ea4feabf | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 621047 | 2025-07-31 03:49:21 AEST | 2025-07-31 10:53:19 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
614ebf1e-1fb8-4c33-b3bc-da5660251ff2 | 95d9acd4-ca32-4708-859a-c6c5ea4feabf | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 650689 | 2025-07-31 03:49:22 AEST | 2025-07-31 10:53:19 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
1de1b3a4-7aff-473d-b94f-e094543bf72b | 3e2bd8bd-34b5-454c-a55c-81a4fce088dc | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 386425 | 2025-07-27 19:23:10 AEST | 2025-07-27 23:24:06 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
dbb97b65-dc54-448f-9c38-4436cb172127 | 3e2bd8bd-34b5-454c-a55c-81a4fce088dc | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 453294 | 2025-07-27 19:23:07 AEST | 2025-07-27 23:24:24 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
fc5c7df4-89a5-49f5-b5e4-90a0b5b22445 | 3e2bd8bd-34b5-454c-a55c-81a4fce088dc | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 211967 | 2025-07-27 19:23:04 AEST | 2025-07-27 23:24:38 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
4a45e58f-1050-483b-96a7-7f10a4cb67ef | ba100246-93c0-4a66-bd51-4423e51cc3b3 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 438224 | 2025-07-25 13:03:20 AEST | 2025-07-25 20:24:14 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
55edaa7c-9a71-43a5-85e7-bcacb3658f90 | ad226626-52b9-4240-af60-a8d928d73b23 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 512711 | 2025-07-31 03:49:19 AEST | 2025-07-31 10:50:20 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
710cfc1c-83cd-4c13-a3f9-33fd22f0ae90 | fe7cdc63-af5a-496d-8842-14decef4a4e6 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 311346 | 2025-07-27 19:22:56 AEST | 2025-07-27 23:29:37 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a21901ce-64f9-4810-8b8b-34cbcc1fea25 | c07bb033-e031-457c-9bf9-f11cea753d12 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 203342 | 2025-07-27 19:22:50 AEST | 2025-07-27 23:31:01 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
4308772a-8197-4b9c-8ea5-5f21fc3911de | 41122991-0c54-4235-a468-59aaa2b0c103 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 658671 | 2025-07-31 13:37:45 AEST | 2025-07-31 11:38:01 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
64946e7c-0af9-4a3f-a462-ddfb4b96fcda | 41122991-0c54-4235-a468-59aaa2b0c103 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 472499 | 2025-07-31 13:37:44 AEST | 2025-07-31 11:38:01 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2954673d-eace-4c41-b136-1c781c923284 | 74ac026b-ef94-4abd-b9c7-420b5bbfc62c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 220712 | 2025-07-27 19:22:48 AEST | 2025-07-27 23:34:51 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
4d79f1c3-51cf-41dc-a924-c27702744c26 | 74ac026b-ef94-4abd-b9c7-420b5bbfc62c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 301681 | 2025-07-27 19:22:44 AEST | 2025-07-27 23:35:06 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
fba76c48-3af7-44c9-92c4-7fd6b120e2d6 | 74ac026b-ef94-4abd-b9c7-420b5bbfc62c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 310536 | 2025-07-27 19:22:40 AEST | 2025-07-27 23:35:14 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
7666fdb9-e651-4db1-a35d-18d4bc78c9f6 | 74ac026b-ef94-4abd-b9c7-420b5bbfc62c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 239603 | 2025-07-27 19:22:37 AEST | 2025-07-27 23:35:25 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
21d61cf7-09bf-4963-a7f5-e0d940cf2a8a | 707eb0f9-e2f9-44d3-8b95-175715a8326e | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 277830 | 2025-07-27 19:22:34 AEST | 2025-07-27 23:37:17 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
aad23c8e-8883-4178-803b-a4f506db302a | 707eb0f9-e2f9-44d3-8b95-175715a8326e | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 298763 | 2025-07-27 19:22:31 AEST | 2025-07-27 23:37:42 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
ec4b3993-353e-4ae1-ba6b-2a84edbdea9f | 985df64f-ea7a-49ec-b113-483e76576f17 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 466487 | 2025-07-31 03:49:15 AEST | 2025-07-31 10:47:22 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
84c40f07-05cc-4c58-a9ff-39a6db6477a9 | 985df64f-ea7a-49ec-b113-483e76576f17 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 712389 | 2025-07-31 03:49:17 AEST | 2025-07-31 10:47:22 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
e7441cca-2d76-4c80-bb71-7db0c88090a6 | e0bcc0c6-cf27-441e-b14f-0e9681344f07 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 273841 | 2025-07-27 19:22:29 AEST | 2025-07-27 23:40:38 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
46ae2fd8-2f47-435b-a92d-9575939e89e6 | e0bcc0c6-cf27-441e-b14f-0e9681344f07 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 280675 | 2025-07-27 19:22:26 AEST | 2025-07-27 23:40:58 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d3cb4bd5-5868-4bfc-a565-06c9960f2704 | e0bcc0c6-cf27-441e-b14f-0e9681344f07 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 | Showing inactive leak - DR Inspection | 0 | 0 | POINT (0.0 0.0) | 643420 | 2025-07-31 06:31:12 AEST | 2025-07-31 10:44:06 AEST | [10 empty] | samsung | Galaxy S25 |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B | 72 | 72
7272ba37-86bb-49d0-9422-308f964401b6 | 1e06ff48-fc6d-4ae7-8afa-2d8f4b5cc898 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 326550 | 2025-07-27 19:22:22 AEST | 2025-07-27 23:42:45 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c8357f59-15b7-4282-a9a7-c8c0e232edc9 | 1e06ff48-fc6d-4ae7-8afa-2d8f4b5cc898 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 392881 | 2025-07-27 19:22:20 AEST | 2025-07-27 23:42:55 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
2b1cf63b-fb8f-493d-ad32-75dae462bbac | 1e06ff48-fc6d-4ae7-8afa-2d8f4b5cc898 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 343147 | 2025-07-27 19:22:16 AEST | 2025-07-27 23:43:03 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
8b673589-a690-42c1-9c1d-bbbf9b1d34f5 | 1e06ff48-fc6d-4ae7-8afa-2d8f4b5cc898 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 279420 | 2025-07-27 19:22:13 AEST | 2025-07-27 23:43:16 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
123ac819-cae1-43f1-96f2-7ba263f026ba | 380ada28-3c38-458f-b9d8-5dcb475ae5c4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 686769 | 2025-07-31 13:37:50 AEST | 2025-07-31 11:45:57 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
04acf598-8b11-428d-a8ec-3167b542290c | 380ada28-3c38-458f-b9d8-5dcb475ae5c4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 692599 | 2025-07-31 13:38:04 AEST | 2025-07-31 11:45:57 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2eb3c3a5-6c14-46dc-8568-a4db6cffb0bd | 380ada28-3c38-458f-b9d8-5dcb475ae5c4 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 746628 | 2025-07-31 13:38:06 AEST | 2025-07-31 11:45:57 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7e8251e6-87e5-4ce4-86ba-04e33ab73e75 | 258caafe-7a8b-4681-9b4d-8e4578b47ec1 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 253221 | 2025-07-27 19:22:10 AEST | 2025-07-27 23:46:32 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
3b5b08cf-8a93-471b-ba91-314f4ff4435f | 258caafe-7a8b-4681-9b4d-8e4578b47ec1 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 221115 | 2025-07-27 19:22:08 AEST | 2025-07-27 23:46:41 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
5a5c5a2e-4e3c-4e0a-85b9-35291ac0189c | 258caafe-7a8b-4681-9b4d-8e4578b47ec1 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3176 | 118.5767 | POINT (118.57668055555555 -20.317577777777778) | 270102 | 2025-07-27 19:22:05 AEST | 2025-07-27 23:46:45 AEST | 8.3036 | 2025-07-27 | 05:18:22 | 88.6994 |  |  | -20.3176 | S | 118.5767 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
6961a882-bbc5-4270-ac13-29e40ce59acf | 7f03e994-c6dc-4b6a-9dca-fccaac294783 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 602533 | 2025-07-31 03:49:13 AEST | 2025-07-31 10:41:27 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
da42329a-a2e0-41cf-b056-1546778bfa8d | 7f03e994-c6dc-4b6a-9dca-fccaac294783 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 627815 | 2025-07-31 03:49:11 AEST | 2025-07-31 10:41:27 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
0df4aaf0-de28-46d6-a062-85e0dcadd17b | fa61d76c-273f-437f-b1f5-394b29789a30 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 489568 | 2025-07-31 13:38:07 AEST | 2025-07-31 13:20:20 AEST | 15.66 |  |  | 16 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3a5fe652-1aa8-4173-bf98-6d45cf794acc | fa61d76c-273f-437f-b1f5-394b29789a30 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 492651 | 2025-07-31 13:38:09 AEST | 2025-07-31 13:20:20 AEST | 15.66 |  |  | 16 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e3d8bcf0-b73c-4ab7-83f1-abb60cfe8534 | 2b63443e-886b-40d3-97fd-a5c8b67ddea0 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 412924 | 2025-07-24 19:37:27 AEST | 2025-07-25 00:30:35 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
60031727-da63-4418-bd9b-d03a06f1ec5e | 2b63443e-886b-40d3-97fd-a5c8b67ddea0 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 468018 | 2025-07-24 19:37:24 AEST | 2025-07-25 00:30:43 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
991220a0-8186-42e8-a674-7d4ec0cb53a7 | 2b63443e-886b-40d3-97fd-a5c8b67ddea0 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 609456 | 2025-07-31 13:38:11 AEST | 2025-07-31 13:22:13 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
894b18c6-e3e9-4e94-88a3-c8e6acf7fe39 | affb4306-b9de-4db5-bdee-7d24d76da238 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.318 | 118.5774 | POINT (118.5774484 -20.317955400001907) | 616605 | 2025-07-30 03:14:31 AEST | 2025-07-30 10:58:19 AEST | 5 |  |  | 4.02 |  |  | -20.318 | S | 118.5774 | E | samsung | SM-S931B |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
2668f58f-dfbc-4ec6-934d-f96b693a60be | b0b94646-274b-4277-806f-4bcf8a0a58d7 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 339311 | 2025-07-24 19:37:20 AEST | 2025-07-25 00:34:59 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
ac7a4e4a-807a-4ebf-ae7d-2b05bdde0d22 | b0b94646-274b-4277-806f-4bcf8a0a58d7 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 672683 | 2025-07-31 13:38:13 AEST | 2025-07-31 13:25:24 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a0ab0085-1710-4a93-90a2-d42ca16e65b1 | b0b94646-274b-4277-806f-4bcf8a0a58d7 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 664572 | 2025-07-31 13:38:14 AEST | 2025-07-31 13:25:24 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f1189a67-cac0-4306-97d6-18b7b073caef | b08ee475-129f-48f8-9ab9-a0dc56322312 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 235989 | 2025-07-25 15:43:35 AEST | 2025-07-25 22:20:05 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
858d611b-2158-438e-8684-0e71b3e42611 | b08ee475-129f-48f8-9ab9-a0dc56322312 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 592195 | 2025-07-25 15:43:31 AEST | 2025-07-25 22:21:55 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
29bbec17-69e5-4b3c-b0a3-3366e837bc0c | 8fd3eb96-e4cd-4f84-bba2-d87621e23544 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 401940 | 2025-07-24 19:37:16 AEST | 2025-07-25 00:36:06 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
62e0f68d-06d7-4685-81c6-eb0688966d18 | 8fd3eb96-e4cd-4f84-bba2-d87621e23544 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3179 | 118.5773 | POINT (118.57730555555555 -20.317880555555554) | 470610 | 2025-07-25 15:43:38 AEST | 2025-07-25 22:15:36 AEST | 6.2893 | 2025-07-25 | 03:43:49 | 14 |  |  | -20.3179 | S | 118.5773 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
24dfde67-d8ee-462a-a12a-58b3369e2a88 | 8be4d72c-20da-40ff-bda2-526014cf98aa | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 400223 | 2025-07-24 19:37:09 AEST | 2025-07-25 00:36:41 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
ff4d20ee-d0e9-425e-9f77-3ccea8d06094 | 8be4d72c-20da-40ff-bda2-526014cf98aa | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 657414 | 2025-07-31 13:38:16 AEST | 2025-07-31 13:27:09 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fd1f36d2-7c66-4c10-bc0f-1d3d23c73273 | 3a512fa5-951f-4bf6-b2be-2a96b94b4804 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 321871 | 2025-07-24 19:37:03 AEST | 2025-07-25 00:37:42 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
92ecabfe-4199-42b2-a6e9-46ae56bb206f | 3e0952db-3d46-4e73-b883-a48049f431e2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 298008 | 2025-07-27 19:12:58 AEST | 2025-07-27 23:57:15 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
37f61845-17b3-4cb0-a359-fdb7a8c89b5b | 3e0952db-3d46-4e73-b883-a48049f431e2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 337330 | 2025-07-27 19:12:55 AEST | 2025-07-27 23:57:23 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
478f454e-b22c-4320-93f8-35dacb65ca3c | 3e0952db-3d46-4e73-b883-a48049f431e2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 320807 | 2025-07-27 19:12:52 AEST | 2025-07-27 23:57:30 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
2f3fade0-9fbf-490a-9edb-9b4182611725 | 3e0952db-3d46-4e73-b883-a48049f431e2 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 193241 | 2025-07-27 19:12:49 AEST | 2025-07-27 23:57:37 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
44d5dd54-9d7b-4e82-b86b-70eee5b63955 | dc819757-1470-43e5-9176-bd5c29f3a51d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3877 | 118.6106 | POINT (118.61064166666667 -20.38765) | 445971 | 2025-07-25 15:43:07 AEST | 2025-07-25 22:35:10 AEST | 0 | 2025-07-25 | 04:32:09 | 15000 |  |  | -20.3877 | S | 118.6106 | E | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
bc9e5027-f339-4ab9-ac1f-562eacb46fa2 | dc819757-1470-43e5-9176-bd5c29f3a51d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 441250 | 2025-07-31 13:38:19 AEST | 2025-07-31 13:31:19 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c26f8e4b-2b60-4e46-9637-3e4f5d338617 | 4b082ff0-05cc-4c5f-a465-e9ec486380d6 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 703433 | 2025-07-31 03:49:09 AEST | 2025-07-31 10:37:32 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
bac5d138-f37d-4d35-822c-e2af35e78ebf | 88e61ec3-36ce-4041-8ffe-f2fef5b66dfa | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 676192 | 2025-07-31 13:38:23 AEST | 2025-07-31 13:35:11 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4205ec03-6c1e-4714-bba8-a42269e0d641 | 88e61ec3-36ce-4041-8ffe-f2fef5b66dfa | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 582158 | 2025-07-31 13:38:21 AEST | 2025-07-31 13:35:11 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
19151176-65d4-40b2-bd4a-5469d0511958 | 5a6ea2ec-9c75-4ea9-bc0c-284c190a3e90 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 687584 | 2025-07-31 13:38:25 AEST | 2025-07-31 13:42:02 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cb1fceed-91a5-4572-995c-a67e75d10475 | 34083916-4222-4916-be17-23d9f9c84d3e | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 280658 | 2025-07-27 19:12:45 AEST | 2025-07-28 00:00:44 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
6f6da7d7-46b4-4292-804c-b1a64f9532cd | 34083916-4222-4916-be17-23d9f9c84d3e | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 274155 | 2025-07-27 19:12:41 AEST | 2025-07-28 00:01:02 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
73489de6-59d8-4580-93b3-dd4702536dcf | 09d617df-8167-4993-b954-2691aa4f69d7 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 292087 | 2025-07-27 19:12:37 AEST | 2025-07-28 00:03:04 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b6668be0-a3e0-4daa-a381-a92f0f4bfeda | 09d617df-8167-4993-b954-2691aa4f69d7 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 277299 | 2025-07-27 19:12:33 AEST | 2025-07-28 00:03:10 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
6ee4113d-03cb-4892-b841-b1b5aba8d781 | ef48afaa-6662-42c7-93fd-13ef95f97d36 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 781631 | 2025-07-30 04:11:19 AEST | 2025-07-30 11:04:52 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
956eb3e1-dea0-4af0-ab24-6863eb0c2836 | ee4e6832-e015-44c7-9075-f6f7322dcaa8 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.318 | 118.5774 | POINT (118.5774484 -20.317955400001907) | 764804 | 2025-07-30 03:14:28 AEST | 2025-07-30 10:54:14 AEST | 5 |  |  | 4.02 |  |  | -20.318 | S | 118.5774 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
664545b0-6d24-48b3-a59f-562b9070c4ae | 3fe8c8e2-3735-4d0a-9a35-dc55742ddff1 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 304865 | 2025-07-24 19:36:59 AEST | 2025-07-25 00:46:06 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a5f734b1-87a4-40d2-879e-01b57469bc21 | 3fe8c8e2-3735-4d0a-9a35-dc55742ddff1 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 182569 | 2025-07-24 19:36:56 AEST | 2025-07-25 00:48:09 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b36cc6ad-b9ab-431b-b8c4-6aa2e1e0aa7c | 007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 436730 | 2025-07-25 13:04:15 AEST | 2025-07-25 20:12:54 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
1643b668-8405-4c81-885a-b88048ddfd9a | 007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 486124 | 2025-07-25 13:04:10 AEST | 2025-07-25 20:13:03 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
0479752a-c369-4344-9f89-b5f3047abc06 | 007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 361601 | 2025-07-25 13:04:04 AEST | 2025-07-25 20:13:26 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
68767106-de3b-4fae-ab1f-a05ab0f78f9b | 007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 448019 | 2025-07-25 13:03:59 AEST | 2025-07-25 20:13:34 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
273ee17a-139d-46c8-9a33-711de2ac1174 | 007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 482259 | 2025-07-25 13:03:55 AEST | 2025-07-25 20:13:41 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
97054597-cfdd-4621-8713-871d6227a54e | 007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 454683 | 2025-07-25 13:03:51 AEST | 2025-07-25 20:15:30 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
aaf9e908-8bbd-4fb1-95c6-6ff9d350db30 | 007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 497929 | 2025-07-25 13:03:40 AEST | 2025-07-25 20:15:36 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
2c7f37ca-cc40-4433-8122-f0de30df49cc | 007e3e44-d6b5-459e-bd3f-ffcd4c11344c | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 490423 | 2025-07-25 13:03:28 AEST | 2025-07-25 20:15:47 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7c98c354-066b-4739-8145-b45b899c9530 | fd439ff8-fde2-4f54-a60c-53caf48f5183 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 331651 | 2025-07-25 13:03:08 AEST | 2025-07-25 20:33:40 AEST | [10 empty] | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
deb75ad4-8cbd-48b7-9bf9-450aa66047c9 | fd439ff8-fde2-4f54-a60c-53caf48f5183 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 458574 | 2025-07-25 13:03:04 AEST | 2025-07-25 20:38:36 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
8e7d2911-e216-4edc-befc-6f75d4dcf376 | fd439ff8-fde2-4f54-a60c-53caf48f5183 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 414530 | 2025-07-25 13:02:59 AEST | 2025-07-25 20:38:47 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
b00e6920-3335-4e38-a563-9ad719b1cf79 | fd439ff8-fde2-4f54-a60c-53caf48f5183 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 434784 | 2025-07-25 13:02:55 AEST | 2025-07-25 20:38:58 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
1d7e90ab-7df6-4aa2-8932-a80e76877e43 | fd439ff8-fde2-4f54-a60c-53caf48f5183 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 381416 | 2025-07-25 13:02:51 AEST | 2025-07-25 20:39:06 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
a9575dcc-3908-4802-8462-c6d607a6b82e | d6407af9-d9a0-4a53-9e32-2c7c40887929 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3179 | 118.5773 | POINT (118.57730555555555 -20.317880555555554) | 430317 | 2025-07-25 15:44:06 AEST | 2025-07-25 22:02:38 AEST | 6.2893 | 2025-07-25 | 03:43:49 | 14 |  |  | -20.3179 | S | 118.5773 | E | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
4ab8c7a7-a95b-40f8-9f2c-1299520585f2 | d6407af9-d9a0-4a53-9e32-2c7c40887929 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3179 | 118.5773 | POINT (118.57730555555555 -20.317880555555554) | 411061 | 2025-07-25 15:44:01 AEST | 2025-07-25 22:02:53 AEST | 6.2893 | 2025-07-25 | 03:43:49 | 14 |  |  | -20.3179 | S | 118.5773 | E | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
6ef0150c-3078-44ed-a216-09a74f782138 | 0a50d00d-423b-4bd1-b54f-6ea215daf809 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 535787 | 2025-07-25 15:43:26 AEST | 2025-07-25 22:22:45 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c81f3c0a-1565-4745-bd2f-9f5a7f88abb6 | 0a50d00d-423b-4bd1-b54f-6ea215daf809 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 413615 | 2025-07-25 15:43:23 AEST | 2025-07-25 22:22:52 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c9ad238a-ec38-4d9e-b2f1-00c9eeacfde7 | 0a50d00d-423b-4bd1-b54f-6ea215daf809 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 553891 | 2025-07-25 15:43:19 AEST | 2025-07-25 22:23:02 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
9d2b8b0d-4f94-405c-a164-c42e7df3fb3c | 0a50d00d-423b-4bd1-b54f-6ea215daf809 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 427913 | 2025-07-25 15:43:15 AEST | 2025-07-25 22:23:07 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
6e390dfe-72aa-40e2-aedb-fc71bfae1f8b | 0a50d00d-423b-4bd1-b54f-6ea215daf809 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 515196 | 2025-07-25 15:43:12 AEST | 2025-07-25 22:23:12 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5c804070-ad56-42fc-b65e-5548989d9b36 | d8c30d2c-2a2f-4e75-9ca3-7554b689c587 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 382232 | 2025-07-25 15:43:03 AEST | 2025-07-25 22:46:31 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
70e08e43-f8f9-416c-8752-caa6d48844e9 | d8c30d2c-2a2f-4e75-9ca3-7554b689c587 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 362442 | 2025-07-25 15:42:59 AEST | 2025-07-25 22:46:53 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
65f49dfb-4953-4b3d-82c5-eddc68803208 | d8c30d2c-2a2f-4e75-9ca3-7554b689c587 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 372300 | 2025-07-25 15:42:54 AEST | 2025-07-25 22:47:00 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7ffe7a8a-55b6-4c63-8c87-8dca6004367b | bdfdebe4-160d-4851-a9a3-b527a6a8414d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 448946 | 2025-07-25 15:42:51 AEST | 2025-07-25 22:52:02 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
931d877f-799a-4a20-8f59-962d0bc5f010 | bdfdebe4-160d-4851-a9a3-b527a6a8414d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 453630 | 2025-07-25 15:42:48 AEST | 2025-07-25 22:52:10 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
4e951ae7-2a26-4834-acad-58af057076f7 | bdfdebe4-160d-4851-a9a3-b527a6a8414d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 384779 | 2025-07-25 15:42:45 AEST | 2025-07-25 22:52:26 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
717f859d-caa0-4924-8301-1a07012eb82c | bdfdebe4-160d-4851-a9a3-b527a6a8414d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 403380 | 2025-07-25 15:42:40 AEST | 2025-07-25 22:52:39 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
3ad33a0a-b51e-4412-a153-5254d93ca4d3 | bdfdebe4-160d-4851-a9a3-b527a6a8414d | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 359881 | 2025-07-25 15:42:37 AEST | 2025-07-25 22:52:47 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
8328cf07-43cc-4478-a658-e3ae7b07bd63 | eda90375-414c-4158-94c5-197a4b51a23a | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 342879 | 2025-07-27 19:13:08 AEST | 2025-07-27 23:49:58 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
8eb9921e-364e-4d3d-a93b-6cb87b8a1fed | eda90375-414c-4158-94c5-197a4b51a23a | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 253062 | 2025-07-27 19:13:05 AEST | 2025-07-27 23:50:07 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
aa84f9e1-d0fd-40ce-b49e-3451a8a815b3 | eda90375-414c-4158-94c5-197a4b51a23a | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 256310 | 2025-07-27 19:13:01 AEST | 2025-07-27 23:50:50 AEST | [10 empty] | Apple | iPhone 13 mini | RightTop | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
d9ddc125-ac1e-4312-828f-c0dc0252e403 | 8701b36c-8640-4406-a685-2ddb4fd3cfed | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 795708 | 2025-07-30 04:11:45 AEST | 2025-07-30 11:39:03 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
64f15765-eb90-4d3e-bc86-a8d7866ccaa2 | 8701b36c-8640-4406-a685-2ddb4fd3cfed | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | 0 | 0 | POINT (0.0 0.0) | 774691 | 2025-07-30 04:11:43 AEST | 2025-07-30 11:39:03 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
facf4c3d-19b0-485f-8866-8e323e769b30 | 3246a177-2b50-484c-89aa-12e9f0939204 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 478380 | 2025-07-31 13:37:47 AEST | 2025-07-31 11:40:34 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e1e22c10-7937-4e0b-93ea-b882df233c20 | 3246a177-2b50-484c-89aa-12e9f0939204 | dc9f9beb-67e1-4ec8-aa4e-7cbc707a6fcd | 1 |  | -20.3165 | 118.5847 | POINT (118.58472222222221 -20.316461700002208) | 499786 | 2025-07-31 13:37:49 AEST | 2025-07-31 11:40:34 AEST |  |  |  | 1900 |  |  | -20.3165 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cff40b20-41e7-4dcf-9e4e-63ad4e1f3a67 | f585d567-5b17-4dde-9822-c61fe24778eb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 760367 | 2025-07-30 04:11:17 AEST | 2025-07-30 11:02:37 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
5f2d38bb-f3b9-46f1-99fd-3ca4cd1e2b0c | f585d567-5b17-4dde-9822-c61fe24778eb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 786673 | 2025-07-30 04:11:15 AEST | 2025-07-30 11:02:37 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
1f51cce4-342c-4e4b-9a9f-c1cdd452669f | 4a51f523-68e6-4e5d-9a0e-cdf6108aacca | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 803775 | 2025-07-30 04:11:12 AEST | 2025-07-30 11:00:50 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
48094c54-fd9a-4dce-a6fd-0e91feccd159 | 7a07d732-8c7f-4a3e-9e92-16dc629a8b17 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.318 | 118.5774 | POINT (118.5774484 -20.317955400001907) | 659231 | 2025-07-30 03:14:12 AEST | 2025-07-30 10:45:15 AEST | 5 |  |  | 4.02 |  |  | -20.318 | S | 118.5774 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
5dd18618-1bc8-4072-a186-b39286c0f373 | 7a07d732-8c7f-4a3e-9e92-16dc629a8b17 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.318 | 118.5774 | POINT (118.5774484 -20.317955400001907) | 676802 | 2025-07-30 03:14:17 AEST | 2025-07-30 10:45:15 AEST | 5 |  |  | 4.02 |  |  | -20.318 | S | 118.5774 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
8524aee4-1eaa-4ad9-876c-adece091aef9 | ab28569f-fb66-4b3a-aba2-37fef9b025fa | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 727603 | 2025-07-30 04:11:10 AEST | 2025-07-30 10:59:03 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
df9f393e-28bb-4d2b-bdd7-0440a3b5c669 | e8f6009c-d4f9-4ad7-8a6c-71a088190853 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 438068 | 2025-07-24 19:36:53 AEST | 2025-07-25 00:51:08 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
c63163a1-ed6e-483f-b8f4-d0184f50e26d | e8f6009c-d4f9-4ad7-8a6c-71a088190853 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 723293 | 2025-07-31 03:49:07 AEST | 2025-07-31 10:34:50 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
3f8425ef-e2fe-41fb-91a5-fdc4ea0addcd | e8f6009c-d4f9-4ad7-8a6c-71a088190853 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 752820 | 2025-07-31 03:49:05 AEST | 2025-07-31 10:34:50 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
eb5f5bd3-3eef-4fbf-9ce1-9490fb227df1 | d7e94c09-ea48-4667-9d93-e89d757005fd | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 768453 | 2025-07-30 04:11:08 AEST | 2025-07-30 10:57:18 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
d46b1c38-a98c-4385-b1a0-8e0df4511740 | 1565e672-3a2e-4584-9de4-f11c5b98afa4 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 732151 | 2025-07-30 04:11:06 AEST | 2025-07-30 10:55:49 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7575c9bb-2120-4162-a487-28b1a5f41106 | 1565e672-3a2e-4584-9de4-f11c5b98afa4 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 730137 | 2025-07-30 04:11:03 AEST | 2025-07-30 10:55:49 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c22b1cd9-582a-4722-b669-abd06c867c9e | 023ff6fc-aa04-4c6d-9266-88c3a8cf4044 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 697144 | 2025-07-31 03:48:58 AEST | 2025-07-31 10:33:37 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
47b2f3b9-b8df-431a-84da-b791e3c7b4eb | 023ff6fc-aa04-4c6d-9266-88c3a8cf4044 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 664112 | 2025-07-31 03:48:40 AEST | 2025-07-31 10:33:37 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
fb67957f-deb0-454a-a6c9-6d5752bde9d0 | 1109abae-6780-44f2-8540-cc5b2d86f5a2 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 837866 | 2025-07-30 04:11:02 AEST | 2025-07-30 10:52:38 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
250ab6c0-c194-4503-89a9-f999b94dc316 | a3b6f204-de42-4f92-abb4-0589bf29ead7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.318 | 118.5774 | POINT (118.5774484 -20.317955400001907) | 572741 | 2025-07-30 03:14:24 AEST | 2025-07-30 10:47:37 AEST | 5 |  |  | 4.02 |  |  | -20.318 | S | 118.5774 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
81f8d7b1-93bb-419c-8e6a-0f4a94cf8149 | a3b6f204-de42-4f92-abb4-0589bf29ead7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.318 | 118.5774 | POINT (118.5774484 -20.317955400001907) | 664569 | 2025-07-30 03:14:21 AEST | 2025-07-30 10:47:37 AEST | 5 |  |  | 4.02 |  |  | -20.318 | S | 118.5774 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
f23884d2-efa4-41b8-8da4-81f8d67b68a7 | f21d4acd-6180-479e-aa7b-4823b4bfde88 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 753308 | 2025-07-30 04:11:00 AEST | 2025-07-30 10:49:15 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
dec9c789-c106-485e-bebb-83fe3eb728a8 | 23559c8c-23a5-4bec-8b9d-37f822954385 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 375051 | 2025-07-24 19:36:50 AEST | 2025-07-25 00:53:42 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
33227cf9-4d4a-4ccf-8076-abd2ca23c830 | 23559c8c-23a5-4bec-8b9d-37f822954385 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 660384 | 2025-07-31 03:48:31 AEST | 2025-07-31 10:31:23 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
48308045-2c21-4807-9249-4e348ac7ceb4 | 25c22f01-40ac-478d-bb81-a49008371a9d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 429284 | 2025-07-24 19:36:47 AEST | 2025-07-25 00:55:37 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
0d5fce2c-04ac-46f5-b38d-0980711626d9 | 09196aa1-2dc2-4592-8d86-00d6dc69ad49 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 463339 | 2025-07-25 15:42:27 AEST | 2025-07-25 23:01:43 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c4639101-1c5d-45c1-bdc6-53d5278cd74d | 09196aa1-2dc2-4592-8d86-00d6dc69ad49 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 593258 | 2025-07-25 15:42:24 AEST | 2025-07-25 23:01:59 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5d3e8ef6-237a-48ee-8247-d765d29f8c70 | 09196aa1-2dc2-4592-8d86-00d6dc69ad49 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 580853 | 2025-07-25 15:42:21 AEST | 2025-07-25 23:02:05 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
2fb74ed0-40ba-460c-9823-ab2eacd1bb6d | 09196aa1-2dc2-4592-8d86-00d6dc69ad49 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 543019 | 2025-07-25 15:42:17 AEST | 2025-07-25 23:02:11 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
f634ffe1-3956-4977-bb53-85a7346ff715 | 254bf200-cdf8-4fd3-9c8e-8419e79c75d4 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 720589 | 2025-07-30 04:10:58 AEST | 2025-07-30 10:46:46 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
affd646c-526a-4be1-b4d4-ba8329fc3dcb | 192c525a-6ea1-469f-ba8b-f81ba572f6b3 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 718449 | 2025-07-31 03:48:29 AEST | 2025-07-31 10:29:35 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
88679a70-4a9c-4738-9e5d-5ebc7df69262 | cada60e6-6146-4bc7-976a-1151f1bcb935 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 693597 | 2025-07-31 03:48:27 AEST | 2025-07-31 10:28:18 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
aac66373-9358-406e-9dd0-7bd626599964 | cada60e6-6146-4bc7-976a-1151f1bcb935 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 581619 | 2025-07-31 03:48:25 AEST | 2025-07-31 10:28:18 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
ce75da53-e9d9-4063-9d68-72d3946c006b | 7ee6e04a-09e0-41cd-a072-fda0e28c1290 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 215435 | 2025-07-27 18:52:05 AEST | 2025-07-28 00:40:29 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
276f3ca2-b707-4ac8-b25c-57c634740ade | b8fa9417-1c6d-4cce-b09c-7d539191d2cb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 253673 | 2025-07-27 18:52:03 AEST | 2025-07-28 00:36:07 AEST | [10 empty] | Apple | iPad mini | RightTop | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
66fb7d6f-9b19-47e7-b500-c1743ad5d854 | 5abac53a-ba55-42ea-8050-4befc17adc99 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 592710 | 2025-07-31 13:38:27 AEST | 2025-07-31 13:49:40 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bb3ba1d3-cf40-4ede-949e-9f765231269c | 5abac53a-ba55-42ea-8050-4befc17adc99 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 539879 | 2025-07-31 13:38:29 AEST | 2025-07-31 13:49:40 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9550c2aa-eb95-4828-b37f-0587fc42d7b7 | 69ff1d32-fad2-4113-8d56-685e72de294d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 366643 | 2025-07-25 15:42:14 AEST | 2025-07-25 23:07:46 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
4eb629cb-e16f-4608-967d-540dfb0d0351 | 69ff1d32-fad2-4113-8d56-685e72de294d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 432231 | 2025-07-25 15:42:10 AEST | 2025-07-25 23:07:57 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
1c1d9d15-01ab-40a5-8821-404114d6ed0e | 69ff1d32-fad2-4113-8d56-685e72de294d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 298019 | 2025-07-25 15:42:07 AEST | 2025-07-25 23:08:09 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
22516a6f-007a-4120-a5e2-a6a496b02166 | 69ff1d32-fad2-4113-8d56-685e72de294d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 385512 | 2025-07-25 15:42:03 AEST | 2025-07-25 23:08:14 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
a8c1cd91-43bb-476b-83a7-f8c22ddc3241 | 64e0d9be-b406-4f0c-a0c8-19f401786f11 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1
693a0c08-b7af-46f8-b082-ef91386c5eec | 64e0d9be-b406-4f0c-a0c8-19f401786f11 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1
2bb6be24-9dd6-4fbb-99f7-016ef00bb962 | 54180008-e9b0-4447-a7ad-8af2d8f75e01 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 574368 | 2025-07-31 13:38:32 AEST | 2025-07-31 13:53:47 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a94e88e9-2576-4e01-975d-11b77f9dbdc8 | 54180008-e9b0-4447-a7ad-8af2d8f75e01 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3846 | 118.5807 | POINT (118.58070991234854 -20.38457969999788) | 444864 | 2025-07-31 13:38:30 AEST | 2025-07-31 13:53:47 AEST |  |  |  | 3400 |  |  | -20.3846 | S | 118.5807 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
158ba375-bd0e-44fb-b984-9d35b3bb6822 | 0b822531-4759-4754-86c6-8ef5c7088368 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1
0413dee5-2902-4ec0-831b-d987428d1a42 | 0b822531-4759-4754-86c6-8ef5c7088368 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1
59d00c87-da41-4731-877d-ac6ab957fcbf | bd3f12bc-5f61-4200-805a-3ec89618e43c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 433513 | 2025-07-25 14:20:32 AEST | 2025-07-25 09:55:02 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ab7adf5a-b8b7-40e6-8b78-e9be4a38724c | bd3f12bc-5f61-4200-805a-3ec89618e43c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 496663 | 2025-07-25 14:20:37 AEST | 2025-07-25 09:55:02 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
83455c17-3157-40dc-9867-a508db52d6f9 | 15cf87f9-2579-41cf-89d4-ebd4df111e82 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 620882 | 2025-07-26 02:04:59 AEST | 2025-07-26 05:49:51 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
22add23c-91c5-4861-9c62-420c722496dd | 58c31518-6e73-43d5-a189-a82abaaaee48 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 687593 | 2025-07-26 02:04:55 AEST | 2025-07-26 05:46:19 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
9f7f3fa3-4a42-4b38-8e43-b387447b052e | 58c31518-6e73-43d5-a189-a82abaaaee48 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 698098 | 2025-07-26 02:04:45 AEST | 2025-07-26 05:46:19 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
3c11a802-9a87-4662-a58a-d2f990946723 | e0e48d05-8406-4832-b280-f4459dcefa6d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 546378 | 2025-07-25 14:16:49 AEST | 2025-07-25 06:09:24 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a84ad01e-d289-4e8c-a61a-ea0f2a16fbdf | e0e48d05-8406-4832-b280-f4459dcefa6d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 552886 | 2025-07-25 14:16:53 AEST | 2025-07-25 06:09:24 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c2cb1303-d661-48a6-8675-9a166a98a409 | e4b01d86-3aa8-4594-ac31-2db0ca30976b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 577560 | 2025-07-25 14:21:10 AEST | 2025-07-25 10:00:35 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
365d53ac-c7d4-49a9-a5ba-102ebd97f788 | e4b01d86-3aa8-4594-ac31-2db0ca30976b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 583600 | 2025-07-25 14:20:47 AEST | 2025-07-25 10:00:35 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
381a0dce-adc4-4aa7-8843-0b9185b01c62 | e4b01d86-3aa8-4594-ac31-2db0ca30976b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 578690 | 2025-07-25 14:20:58 AEST | 2025-07-25 10:00:35 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a4671207-03f5-4a37-856e-afc9d7668acb | 276515de-9364-4e64-a92e-2b3f8bda2c7b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 586387 | 2025-07-25 14:21:18 AEST | 2025-07-25 10:01:00 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
addfa2b6-f81e-470f-a804-4c4b27cd945f | 276515de-9364-4e64-a92e-2b3f8bda2c7b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 441706 | 2025-07-25 14:21:29 AEST | 2025-07-25 10:01:00 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6db5f3cb-25e3-44f8-b7b1-61e16d8f8e07 | 77a58cea-bda5-4674-bdc1-735aa328271f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 719195 | 2025-07-26 02:05:15 AEST | 2025-07-26 05:55:45 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
3a6dac32-6dae-4886-8c5a-7adfab4f98d5 | 77a58cea-bda5-4674-bdc1-735aa328271f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 752036 | 2025-07-26 02:05:20 AEST | 2025-07-26 05:55:45 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
acb9b2bf-c667-4ae7-85a0-80bd1a2b7874 | 041bf985-29e3-4873-94a6-f49bf1facb0c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 584653 | 2025-07-25 14:17:01 AEST | 2025-07-25 06:13:12 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
51f89a8a-2e7b-4546-9252-bb4debcb17ab | 041bf985-29e3-4873-94a6-f49bf1facb0c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 665425 | 2025-07-25 14:16:57 AEST | 2025-07-25 06:13:12 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
db772921-1c79-4ec5-8314-d7d4afbe91af | 6490e537-c966-4321-8341-c88dbdde3143 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 507267 | 2025-07-25 14:22:21 AEST | 2025-07-25 10:09:14 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fba05dc3-641f-4ea2-af85-3625137a3107 | 7ff59e32-27f2-45ce-8de1-710126df1edf | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 493526 | 2025-07-25 14:17:05 AEST | 2025-07-25 06:17:33 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
09b4dabe-0ca9-4f24-aa2e-3bd5f1a2e697 | 7ff59e32-27f2-45ce-8de1-710126df1edf | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 493978 | 2025-07-25 14:17:08 AEST | 2025-07-25 06:17:33 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
35b3944f-8d9a-45cc-8cc3-69b4e87a7811 | e014945b-6a89-427d-991b-b4d47f0ea96c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 633978 | 2025-07-25 14:23:05 AEST | 2025-07-25 10:16:42 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cf9456ef-9313-4054-81dc-db831db5646d | e014945b-6a89-427d-991b-b4d47f0ea96c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 716123 | 2025-07-25 14:23:17 AEST | 2025-07-25 10:16:42 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
568ed46b-6df6-4d2a-b5c6-a69dc8be2bea | 145e4d4d-5e21-42b3-abc8-da340e8f512b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 519028 | 2025-07-25 14:23:53 AEST | 2025-07-25 10:21:57 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9fba77ce-8929-4665-aca0-d7ebcf8f2665 | 145e4d4d-5e21-42b3-abc8-da340e8f512b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 592069 | 2025-07-25 14:23:25 AEST | 2025-07-25 10:21:57 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9f024ee7-8640-43bd-882c-2d13dca43901 | 145e4d4d-5e21-42b3-abc8-da340e8f512b | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 565928 | 2025-07-25 14:23:43 AEST | 2025-07-25 10:21:57 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
28fa947b-a352-478d-8604-5befdc8b6ccb | 05268615-feb3-43e9-b739-50332acf72c5 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 566081 | 2025-07-25 14:24:19 AEST | 2025-07-25 10:24:37 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
73281399-e29f-471c-a7fa-277d1baab506 | 05268615-feb3-43e9-b739-50332acf72c5 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 452508 | 2025-07-25 14:24:02 AEST | 2025-07-25 10:24:37 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8dc4ba39-54c3-4336-b461-fb8dae63179b | d0b26253-af43-48d2-b144-7b7d9f053803 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 668087 | 2025-07-26 02:06:20 AEST | 2025-07-26 06:26:10 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
211690af-fec9-4948-ae30-560ad92ac292 | d0b26253-af43-48d2-b144-7b7d9f053803 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 695870 | 2025-07-26 02:05:46 AEST | 2025-07-26 06:26:10 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
81d47b2b-37a5-4ba7-8ea9-475eee67581b | 4cb68d6d-bf07-4a0b-9517-4d1c0381129d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 658664 | 2025-07-25 14:25:30 AEST | 2025-07-25 10:34:01 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
61717f09-684a-4133-9181-72f96bed0b26 | 4cb68d6d-bf07-4a0b-9517-4d1c0381129d | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 478329 | 2025-07-25 14:25:41 AEST | 2025-07-25 10:34:01 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9d452316-468e-4a71-9dc7-984642187317 | d11c9401-4a69-49ec-a5ca-328cdc5a41c2 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 595129 | 2025-07-26 02:06:42 AEST | 2025-07-26 06:36:17 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
4b20c6c3-66b8-496b-b891-af24c547b9d1 | d11c9401-4a69-49ec-a5ca-328cdc5a41c2 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 557790 | 2025-07-26 02:06:46 AEST | 2025-07-26 06:36:17 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
2b3ae91d-599b-40b4-9b61-46c710092a93 | 328ce410-ef29-40c8-9664-72dff1be70cf | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 582284 | 2025-07-25 14:17:15 AEST | 2025-07-25 06:24:12 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c900594f-fe45-4fc2-9c23-1845f77712f9 | 328ce410-ef29-40c8-9664-72dff1be70cf | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 494887 | 2025-07-25 14:17:11 AEST | 2025-07-25 06:24:12 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8acc2044-4780-4a20-8694-6c96d8c750ae | 6f395f30-2eb5-459c-a89f-75765d53cf7f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 512403 | 2025-07-25 14:25:51 AEST | 2025-07-25 10:48:53 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f9c7f0e3-1b44-455d-8cb0-2378a01799fe | 6f395f30-2eb5-459c-a89f-75765d53cf7f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 535273 | 2025-07-25 14:25:45 AEST | 2025-07-25 10:48:53 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
15deaf45-a39b-46ba-a9e5-8ecd07c67966 | a06a5d7a-7bd6-4991-940d-e5617ffe6aaa | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 590121 | 2025-07-25 14:17:19 AEST | 2025-07-25 06:25:50 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
96d4cf03-61b6-4875-ba8b-ec563690f4d5 | d49a5fd9-282a-4c1d-8d9b-e1f65bfc724e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 513794 | 2025-07-25 14:25:58 AEST | 2025-07-25 10:53:17 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6cbdf6af-5be7-448f-8a35-85104f27a50a | 91f3d268-1281-42e5-a635-712518d1421a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 545781 | 2025-07-25 14:26:07 AEST | 2025-07-25 10:54:54 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
caa18863-af8c-4d8a-bf34-20e6bacef3dd | 91f3d268-1281-42e5-a635-712518d1421a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 498919 | 2025-07-25 14:26:03 AEST | 2025-07-25 10:54:54 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bc285c02-8a22-4f18-ba78-be78affe6cbc | 4bf81172-6050-48e6-8f58-3fe255b928f5 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 430457 | 2025-07-25 14:26:13 AEST | 2025-07-25 10:56:52 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a5c0284d-e45a-428d-aa9d-0c827cdaf913 | 4bf81172-6050-48e6-8f58-3fe255b928f5 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 406736 | 2025-07-25 14:26:18 AEST | 2025-07-25 10:57:16 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
047d538b-8ee2-4184-b4b8-81d6b348ff02 | 56e59c1d-183c-4e22-94a5-0172d0044077 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 409692 | 2025-07-25 14:17:21 AEST | 2025-07-25 06:30:13 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e1991a65-fdf5-434d-a5f0-4714615477fb | 904bcdb2-dad1-4e47-bd1d-a006ec73c5cb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 726119 | 2025-07-26 02:06:51 AEST | 2025-07-26 06:48:56 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
94be80ec-0423-4815-a5ed-33f3d4273cba | fa555486-8b77-455d-85dd-5140989728a0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 590981 | 2025-07-25 14:17:25 AEST | 2025-07-25 06:34:57 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
759b0c97-336a-492b-8c01-31108605aced | d36fe100-7fa1-4380-95e9-2272383ab645 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 580846 | 2025-07-25 14:17:35 AEST | 2025-07-25 06:45:05 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f2ce0f92-621d-462c-bffa-964cf29104dd | d36fe100-7fa1-4380-95e9-2272383ab645 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 405993 | 2025-07-25 14:17:28 AEST | 2025-07-25 06:45:05 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
52f2dfc9-6194-46ae-9770-75156bfe5ee3 | d36fe100-7fa1-4380-95e9-2272383ab645 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 523120 | 2025-07-25 14:17:31 AEST | 2025-07-25 06:45:05 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4824c29f-8953-4f99-be9e-3a69bfe88c9c | b8447522-8bf8-4966-8373-26c17414a5cb | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 673730 | 2025-07-26 02:07:44 AEST | 2025-07-26 06:58:19 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
6bc20d1a-a216-41f9-b9e7-f65daa906f05 | 5d321542-b9b9-4b60-99d2-e80254cf2cca | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 493151 | 2025-07-25 14:26:55 AEST | 2025-07-25 11:05:52 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
51acfbc6-22e2-4339-9d1a-6c71523f11eb | 5d321542-b9b9-4b60-99d2-e80254cf2cca | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 475252 | 2025-07-25 14:26:58 AEST | 2025-07-25 11:05:52 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d68040e8-628f-4ab8-ab40-3fee0c4f920f | 5bea52be-d472-490c-bed3-6265c743e552 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 677838 | 2025-07-26 02:07:48 AEST | 2025-07-26 07:04:50 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
085b5891-62cf-4d48-902b-4e5dbd034af1 | 5bea52be-d472-490c-bed3-6265c743e552 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 748937 | 2025-07-26 02:07:52 AEST | 2025-07-26 07:04:50 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
8559e52e-0689-4b6b-b847-2f88bd75e8b7 | 2696671a-fc1c-4f14-92b2-8ea78a5666a7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 762973 | 2025-07-26 02:08:00 AEST | 2025-07-26 07:13:09 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
f8fab306-d703-4e0b-bf40-ed88155bb797 | 2696671a-fc1c-4f14-92b2-8ea78a5666a7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 786479 | 2025-07-26 02:07:56 AEST | 2025-07-26 07:13:09 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c4398150-350e-44fa-942c-7fc43b6cddf4 | 2696671a-fc1c-4f14-92b2-8ea78a5666a7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 822665 | 2025-07-26 02:08:05 AEST | 2025-07-26 07:13:09 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
164c42db-4875-4db6-a9dc-9a4e9b84a96f | 2696671a-fc1c-4f14-92b2-8ea78a5666a7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 749491 | 2025-07-26 02:08:11 AEST | 2025-07-26 07:14:16 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
f5857d2a-ccc2-4df9-9260-0ce16a4875df | 2696671a-fc1c-4f14-92b2-8ea78a5666a7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 758085 | 2025-07-26 02:08:08 AEST | 2025-07-26 07:14:16 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
9ba48e91-858a-4bee-ab21-5dab1b0e6149 | 2696671a-fc1c-4f14-92b2-8ea78a5666a7 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 671121 | 2025-07-26 02:08:15 AEST | 2025-07-26 07:14:16 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7c571135-7c89-4ec1-92aa-6b4679d356fa | 7233e690-b6fe-4c61-a41d-b2f29d4f9c5a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 768316 | 2025-07-26 02:08:23 AEST | 2025-07-26 07:16:22 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
819b540d-3f64-496c-ad9f-fcbf1ce0e273 | 7233e690-b6fe-4c61-a41d-b2f29d4f9c5a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 804483 | 2025-07-26 02:08:26 AEST | 2025-07-26 07:16:22 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
45d5bab0-c25e-4271-a0e1-32e375a6c38a | 7233e690-b6fe-4c61-a41d-b2f29d4f9c5a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 786546 | 2025-07-26 02:08:19 AEST | 2025-07-26 07:16:22 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
32bb53ee-07b9-4acb-a43f-22d7f8b2c799 | 9a6892b7-2818-4434-8184-36b1e73bae39 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 448137 | 2025-07-25 14:17:41 AEST | 2025-07-25 06:47:48 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
61a9c2ed-5680-4531-8bc1-65717eea25ab | 9a6892b7-2818-4434-8184-36b1e73bae39 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 467780 | 2025-07-25 14:17:44 AEST | 2025-07-25 06:47:48 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
eac8f9de-3da9-4629-8ad1-3dfc1c0895ef | e2527e28-a3ed-4d61-8902-9d4f54e58b6c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 506402 | 2025-07-25 14:17:48 AEST | 2025-07-25 06:53:30 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9b87c113-72a0-4f86-8e67-cde89a176b62 | e2527e28-a3ed-4d61-8902-9d4f54e58b6c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 536171 | 2025-07-25 14:17:51 AEST | 2025-07-25 06:53:30 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
510057b8-8383-474a-9f13-20f5a8f0d2c1 | e2527e28-a3ed-4d61-8902-9d4f54e58b6c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 514849 | 2025-07-25 14:27:35 AEST | 2025-07-25 11:13:21 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9ceee7ca-833d-440b-9a20-efcdf5b4ddb4 | 610d1396-321b-49c7-90da-d0d79c730c9c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 543452 | 2025-07-25 14:27:38 AEST | 2025-07-25 11:14:27 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b7b16511-d2a6-4e28-8e3b-3c27cb359f74 | b8f1f68d-36f3-4bdb-a43a-a523b2ea945c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 593715 | 2025-07-25 14:17:55 AEST | 2025-07-25 07:01:51 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e70bcb6d-c19b-47c9-8d8c-45f56f197fef | b8f1f68d-36f3-4bdb-a43a-a523b2ea945c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 567921 | 2025-07-25 14:18:04 AEST | 2025-07-25 07:01:51 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5a63486b-12e7-4af7-bcb4-66ac0ee859e9 | b8f1f68d-36f3-4bdb-a43a-a523b2ea945c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 547776 | 2025-07-25 14:18:08 AEST | 2025-07-25 07:01:51 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3fa29915-e16b-43a7-b218-5dd14a5f8d14 | b8f1f68d-36f3-4bdb-a43a-a523b2ea945c | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 372413 | 2025-07-25 14:17:59 AEST | 2025-07-25 07:01:51 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2b268461-d53a-45fd-adac-98c18e5a5825 | 4aa09434-dcc4-481a-9c03-ebe6bfef5f0a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 677580 | 2025-07-29 19:25:41 AEST | 2025-07-29 06:49:34 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c42c0ec9-73ef-4c70-8dfa-813242dde071 | 4aa09434-dcc4-481a-9c03-ebe6bfef5f0a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 629091 | 2025-07-29 19:25:44 AEST | 2025-07-29 06:49:34 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
daa25e5c-2ff1-4544-a399-517623e169e0 | 4aa09434-dcc4-481a-9c03-ebe6bfef5f0a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 661094 | 2025-07-29 19:25:40 AEST | 2025-07-29 06:49:34 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bd3ff3a5-9c77-4b37-a62d-75446c36d17a | 4aa09434-dcc4-481a-9c03-ebe6bfef5f0a | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 515560 | 2025-07-29 19:25:37 AEST | 2025-07-29 06:49:34 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
08f328ba-e30f-4a29-986e-55ec1280f44a | a56850d9-4d9a-4228-b38d-af14f37fac77 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 416571 | 2025-07-25 15:41:59 AEST | 2025-07-25 23:19:44 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
fd72f3b5-59a9-405e-b5af-3beafb340c69 | a56850d9-4d9a-4228-b38d-af14f37fac77 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 441215 | 2025-07-25 15:41:56 AEST | 2025-07-25 23:20:14 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c116790a-d784-4051-9b91-cad37ee20c2c | a56850d9-4d9a-4228-b38d-af14f37fac77 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 498597 | 2025-07-25 15:41:53 AEST | 2025-07-25 23:20:27 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
8932b491-78cd-4b0a-bb28-10cdf1980ace | 6a6a5178-1717-419f-b658-8d430ee38c04 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 680445 | 2025-07-25 14:20:26 AEST | 2025-07-25 09:48:54 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fb63edd8-23ae-4dce-aa0b-4fcdf72b2bd9 | 6a6a5178-1717-419f-b658-8d430ee38c04 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 698424 | 2025-07-25 14:20:22 AEST | 2025-07-25 09:48:54 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2c9e84bb-a588-410c-857b-52406fe68acc | 6a6a5178-1717-419f-b658-8d430ee38c04 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 695943 | 2025-07-25 14:20:30 AEST | 2025-07-25 09:48:54 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e27b2bf7-2052-4868-bbcc-5f7fa52cc109 | 25274911-8d10-44f0-83a5-ae288150ae3e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 674830 | 2025-07-25 14:21:39 AEST | 2025-07-25 10:05:45 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fbe92043-bbf7-4e9f-8561-4bd12ddc2f62 | 25274911-8d10-44f0-83a5-ae288150ae3e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 623144 | 2025-07-25 14:21:51 AEST | 2025-07-25 10:05:45 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c54f7f22-0cd4-46b3-89ca-647bd772d4e7 | 25274911-8d10-44f0-83a5-ae288150ae3e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 599910 | 2025-07-25 14:22:12 AEST | 2025-07-25 10:05:45 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
691c5ba7-1157-45ed-865e-334afd9ed05a | 25274911-8d10-44f0-83a5-ae288150ae3e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 668977 | 2025-07-25 14:22:01 AEST | 2025-07-25 10:05:45 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d75142be-94a2-4f40-995b-d769c54da50f | 18880553-f173-4d94-8d7a-1f14c43afaa1 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 580241 | 2025-07-25 14:22:46 AEST | 2025-07-25 10:11:59 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
61b62bf2-b815-4662-bedd-47fe1a5a1505 | 18880553-f173-4d94-8d7a-1f14c43afaa1 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 685711 | 2025-07-25 14:22:38 AEST | 2025-07-25 10:11:59 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
00551810-d75e-466b-a77d-c2c28abbd958 | 18880553-f173-4d94-8d7a-1f14c43afaa1 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 642705 | 2025-07-25 14:22:29 AEST | 2025-07-25 10:11:59 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3e0ddd96-1fdb-4a2c-8b31-58ba60dff89f | 18880553-f173-4d94-8d7a-1f14c43afaa1 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 647801 | 2025-07-25 14:22:54 AEST | 2025-07-25 10:11:59 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d9bd0a33-b334-48d4-b04a-00de7f36b281 | 0cccf7dc-9437-40a1-b936-1d7e47ffe360 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 643099 | 2025-07-25 14:24:50 AEST | 2025-07-25 10:27:47 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a76148d8-28d5-4312-a977-bb0be475b4c3 | 0cccf7dc-9437-40a1-b936-1d7e47ffe360 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 670850 | 2025-07-25 14:24:31 AEST | 2025-07-25 10:27:47 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
afedf938-009c-44d9-97e3-e6e03376a0ce | 0cccf7dc-9437-40a1-b936-1d7e47ffe360 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 633510 | 2025-07-25 14:24:40 AEST | 2025-07-25 10:27:47 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7269c23a-3558-4308-9bed-4f9fc7d3f212 | 9ceb4475-61bc-4747-af8b-22478e9b0829 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 667340 | 2025-07-25 14:25:23 AEST | 2025-07-25 10:31:27 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1fa1b398-b07a-4a7a-9e3a-7f7a02d0e634 | 9ceb4475-61bc-4747-af8b-22478e9b0829 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 586214 | 2025-07-25 14:24:59 AEST | 2025-07-25 10:31:27 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
dd4ca900-0b95-4719-815f-6724ecc4976d | 9ceb4475-61bc-4747-af8b-22478e9b0829 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 540126 | 2025-07-25 14:25:10 AEST | 2025-07-25 10:31:27 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c13edc26-0c05-4ce5-9b6a-07d881c66279 | e15290ec-765f-4bfc-81f4-c3584afbdf0e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 474629 | 2025-07-25 14:26:42 AEST | 2025-07-25 11:00:05 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ca7a5165-1fbd-401f-a153-4bce2194a479 | e15290ec-765f-4bfc-81f4-c3584afbdf0e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 480951 | 2025-07-25 14:26:23 AEST | 2025-07-25 11:00:05 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9dc096fd-fa7c-4ea0-8d78-45f11ba37143 | e15290ec-765f-4bfc-81f4-c3584afbdf0e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 599633 | 2025-07-25 14:26:28 AEST | 2025-07-25 11:00:05 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e7ce7e5f-6853-4c02-a7a8-66c83c7c2034 | e6be1681-c409-4ed5-9baf-d2a50954b4fc | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 610556 | 2025-07-25 14:26:52 AEST | 2025-07-25 11:02:18 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f9982a42-bd64-4f8d-9ed0-8c28f2c467e2 | e6be1681-c409-4ed5-9baf-d2a50954b4fc | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 564375 | 2025-07-25 14:26:46 AEST | 2025-07-25 11:02:18 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0999fd44-e568-4fb4-adaa-330c431fdf06 | fb87fa48-7838-411e-8e0a-f0d1e4341905 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 597006 | 2025-07-25 14:27:08 AEST | 2025-07-25 11:09:05 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
02693db3-7415-48b7-b3b9-cc750bc46d77 | fb87fa48-7838-411e-8e0a-f0d1e4341905 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 625872 | 2025-07-25 14:27:02 AEST | 2025-07-25 11:09:05 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
42e529d3-d555-403f-a2b7-e38c0a2fa505 | fb87fa48-7838-411e-8e0a-f0d1e4341905 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 629760 | 2025-07-25 14:27:21 AEST | 2025-07-25 11:09:05 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fdacb9e5-593a-47ec-85b9-d296c7d954d3 | fb87fa48-7838-411e-8e0a-f0d1e4341905 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 536181 | 2025-07-25 14:27:04 AEST | 2025-07-25 11:09:05 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
12385793-69ad-4394-b67a-621cdb816cc4 | fb87fa48-7838-411e-8e0a-f0d1e4341905 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 701816 | 2025-07-25 14:27:11 AEST | 2025-07-25 11:09:05 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3a8c6564-e33c-45cf-832b-d0301d766aec | 5a55d9bd-fd19-440a-8279-72931323a28f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 610798 | 2025-07-25 14:27:31 AEST | 2025-07-25 11:11:23 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4605fc0f-3c17-4422-aedc-54052fff249e | 5a55d9bd-fd19-440a-8279-72931323a28f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 511416 | 2025-07-25 14:27:24 AEST | 2025-07-25 11:11:23 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d217e5b6-ba64-400c-9edb-35587caf9a14 | 5a55d9bd-fd19-440a-8279-72931323a28f | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 495453 | 2025-07-25 14:27:28 AEST | 2025-07-25 11:11:23 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a4c8ded8-2c98-4891-9032-603b3f7fff2d | 6cdef391-3e69-484c-b911-43f9a2e0534e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 614498 | 2025-07-25 14:27:41 AEST | 2025-07-25 11:18:41 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4ec1806c-f37f-45a1-8a1c-6ea7b9684cbf | 6cdef391-3e69-484c-b911-43f9a2e0534e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 678470 | 2025-07-25 14:27:44 AEST | 2025-07-25 11:18:41 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9de664d3-bea4-4757-aea4-78a552377f2e | 6cdef391-3e69-484c-b911-43f9a2e0534e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 668424 | 2025-07-25 14:27:48 AEST | 2025-07-25 11:18:41 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d746d1b6-b084-401a-a398-5f6386cbb51c | 6cdef391-3e69-484c-b911-43f9a2e0534e | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 690223 | 2025-07-29 19:25:46 AEST | 2025-07-29 06:50:16 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5ac5d44d-ad09-4fbc-95c6-c3a881537b0e | c2580cf6-2263-4416-b197-7be95c537753 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 543411 | 2025-07-25 14:27:54 AEST | 2025-07-25 11:21:11 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7a28c6ab-bee4-478c-a162-32ffeffc271a | c2580cf6-2263-4416-b197-7be95c537753 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 486971 | 2025-07-25 14:27:51 AEST | 2025-07-25 11:21:11 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8b4ddf7c-51cf-41e6-bbef-4f7b7ac12d0b | 126e9d83-4a1e-4a28-9133-c93ca90f4dea | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 621683 | 2025-07-26 02:05:27 AEST | 2025-07-26 06:10:27 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ad027e22-e547-4c99-ac2c-90aa32de5f40 | 126e9d83-4a1e-4a28-9133-c93ca90f4dea | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 472208 | 2025-07-26 02:05:23 AEST | 2025-07-26 06:10:27 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c1938aff-44c9-454e-b82f-317b484dfa4d | 09ca859e-88a7-4d22-a91a-011029eb48e0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 563958 | 2025-07-26 02:05:37 AEST | 2025-07-26 06:19:10 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
5e72411d-b0ef-474b-9142-213fd06fcfe9 | 09ca859e-88a7-4d22-a91a-011029eb48e0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 530952 | 2025-07-26 02:05:32 AEST | 2025-07-26 06:19:10 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
98101bea-c037-43fc-a216-3a0724f872ba | d220c843-6ad1-47ab-a1c7-91ee334627a0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 824032 | 2025-07-26 02:07:06 AEST | 2025-07-26 06:53:18 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ae42b3cd-04f1-4578-8b7c-7701004b6110 | d220c843-6ad1-47ab-a1c7-91ee334627a0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 865905 | 2025-07-26 02:07:35 AEST | 2025-07-26 06:53:18 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ccca4e7f-daf0-4e7a-af25-3eb421dcb0f1 | d220c843-6ad1-47ab-a1c7-91ee334627a0 | f045916c-72e6-4de6-aa3a-dde53a6e1ff3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 864113 | 2025-07-26 02:07:40 AEST | 2025-07-26 06:53:18 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7f3b4276-4c77-41bc-9a69-4f49c79667e5 | fbbe66f1-1266-4265-94ff-dd82f8f22bb1 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 498549 | 2025-07-25 14:18:16 AEST | 2025-07-25 07:08:38 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e336235f-e6d8-4c1b-aa76-632af068d7e6 | fbbe66f1-1266-4265-94ff-dd82f8f22bb1 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 459585 | 2025-07-25 14:18:12 AEST | 2025-07-25 07:08:38 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
382f08af-6bfe-4980-ba0c-28794d7019e1 | 88d987f9-7aeb-4349-995c-20a6fb8e2381 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 782588 | 2025-07-26 02:08:30 AEST | 2025-07-26 07:34:18 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
a63ac322-ff1b-4d1f-91d3-a09ecbcf07ee | 88d987f9-7aeb-4349-995c-20a6fb8e2381 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 845250 | 2025-07-26 02:08:45 AEST | 2025-07-26 07:34:18 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
5d7bcd33-15b8-4ab2-97fc-038921668f48 | 88d987f9-7aeb-4349-995c-20a6fb8e2381 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 785577 | 2025-07-26 02:08:40 AEST | 2025-07-26 07:34:18 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
dbd56ce4-18b5-481c-913a-ce467af82689 | 88d987f9-7aeb-4349-995c-20a6fb8e2381 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 686148 | 2025-07-26 02:08:49 AEST | 2025-07-26 07:34:51 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
d6cc6aa6-12f0-4c9d-8b07-c688d375b0ee | 0a4182c5-06a7-4bac-ba6f-074062100548 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 591827 | 2025-07-26 09:05:19 AEST | 2025-07-26 11:27:18 AEST | 4.2964 |  |  | 6 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a462fd7b-f0d4-4512-b998-36786580dbe8 | 0a4182c5-06a7-4bac-ba6f-074062100548 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 465201 | 2025-07-26 09:05:17 AEST | 2025-07-26 11:27:18 AEST | 4.2964 |  |  | 6 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
79dd1e57-5c48-4466-b828-fdcf8c48ae99 | 0a4182c5-06a7-4bac-ba6f-074062100548 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 609546 | 2025-07-26 02:08:58 AEST | 2025-07-26 07:40:09 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c565268b-8e54-4fe4-a49e-487a9081c425 | 0a4182c5-06a7-4bac-ba6f-074062100548 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 615135 | 2025-07-26 02:08:54 AEST | 2025-07-26 07:40:09 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
2fd1cf99-a2b9-473b-92c0-4cace26addc8 | 14098702-bacd-4afd-ba47-3448ae789704 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 717849 | 2025-07-26 02:09:11 AEST | 2025-07-26 07:45:28 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
4a0c1f2a-b5ff-450d-8d79-fbb2391bd3d4 | 14098702-bacd-4afd-ba47-3448ae789704 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 739763 | 2025-07-26 02:09:04 AEST | 2025-07-26 07:45:28 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
64cd2fc3-cef6-45d0-8319-8e177e774299 | b30ab65c-b157-43d1-8eff-b0305742978f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 522588 | 2025-07-26 09:05:21 AEST | 2025-07-26 11:32:01 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6bb8a031-1fb0-460a-855f-55d6cf0daed5 | b30ab65c-b157-43d1-8eff-b0305742978f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 651588 | 2025-07-26 02:09:18 AEST | 2025-07-26 07:50:13 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
3650e4da-e2f8-4d02-9c12-147601eefd47 | b30ab65c-b157-43d1-8eff-b0305742978f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 618821 | 2025-07-26 02:09:23 AEST | 2025-07-26 07:50:13 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c7f27b0d-e66a-4ce5-b06d-9ff5a06724b0 | 04617099-6add-4434-bd31-897631af60fe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 453689 | 2025-07-25 14:18:20 AEST | 2025-07-25 07:14:28 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4b2a2826-05a1-4b22-a2b0-81ca44d5e1e7 | 04617099-6add-4434-bd31-897631af60fe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 448151 | 2025-07-25 14:18:23 AEST | 2025-07-25 07:14:28 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9a22aa20-b83e-46af-8b48-4aa65791f33f | 04617099-6add-4434-bd31-897631af60fe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 450998 | 2025-07-25 14:18:28 AEST | 2025-07-25 07:14:28 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6ea4c951-30b9-4f5b-b23c-f99bcff70e7f | 8041e2c7-6e06-44bf-a228-95cc764587dd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 637282 | 2025-07-25 14:18:49 AEST | 2025-07-25 07:16:27 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
184741f7-6212-4904-b4a8-4e8c4b312917 | 8041e2c7-6e06-44bf-a228-95cc764587dd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 663288 | 2025-07-25 14:18:34 AEST | 2025-07-25 07:16:27 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8ca17581-6a6a-468d-8a43-336dbf106ab3 | 8041e2c7-6e06-44bf-a228-95cc764587dd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 613489 | 2025-07-25 14:18:41 AEST | 2025-07-25 07:16:27 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
21914ec9-2723-4bae-8aa9-7a0b8b0d573b | 5bdb797e-8807-4fc6-ad9c-11a460404243 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 410862 | 2025-07-25 14:18:53 AEST | 2025-07-25 07:19:26 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f4afc9fe-82d3-4be6-91b8-a5d92949a34e | 5bdb797e-8807-4fc6-ad9c-11a460404243 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 433739 | 2025-07-25 14:19:01 AEST | 2025-07-25 07:19:26 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9b989044-da70-4564-a637-5aac2f03a4f4 | 829ead90-e019-467c-a7d9-dc0992d98239 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 491203 | 2025-07-25 14:19:10 AEST | 2025-07-25 07:22:17 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4ad95e0c-eadb-4de8-8e70-ffd1e3961e04 | 829ead90-e019-467c-a7d9-dc0992d98239 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 494719 | 2025-07-25 14:19:22 AEST | 2025-07-25 07:22:17 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
67db41c0-4a25-4f40-abb8-7f538daf42c1 | 4c171f5c-be7d-41a2-9376-2d525b79eb6b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 478715 | 2025-07-25 14:19:36 AEST | 2025-07-25 07:26:11 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
147b2730-773d-4a0e-9fcb-80f394c12f03 | 4c171f5c-be7d-41a2-9376-2d525b79eb6b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 484584 | 2025-07-25 14:19:28 AEST | 2025-07-25 07:26:11 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2efe6f94-99dd-4d7f-91db-c3c3b503f73d | 764287d1-6f3b-4b09-9b51-3d40607bcb6c | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 561828 | 2025-07-26 09:05:23 AEST | 2025-07-26 11:37:11 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
28733385-5dc4-4ddc-9a2e-3be57506e86c | 764287d1-6f3b-4b09-9b51-3d40607bcb6c | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 588824 | 2025-07-26 09:05:25 AEST | 2025-07-26 11:37:11 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e030c1ec-bcdb-4c8f-a879-d1e853a46c14 | 8069b96b-5160-4b6e-bb54-d848cbf2d2c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 583507 | 2025-07-26 09:05:29 AEST | 2025-07-26 11:40:50 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ef592d81-9605-4cfd-b9e7-97518bf7662f | 8069b96b-5160-4b6e-bb54-d848cbf2d2c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 515840 | 2025-07-26 09:05:31 AEST | 2025-07-26 11:40:50 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
741bf341-d012-4b15-9618-fc10fb008ffa | 8069b96b-5160-4b6e-bb54-d848cbf2d2c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 513590 | 2025-07-26 09:05:33 AEST | 2025-07-26 11:40:50 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4afb64c1-f320-4b48-9f15-a4fb599c2805 | 8069b96b-5160-4b6e-bb54-d848cbf2d2c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 478365 | 2025-07-26 09:05:27 AEST | 2025-07-26 11:40:50 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
02158ce7-692d-418a-b92c-337ad141f258 | b99745a4-6c55-4c2d-a61f-61c711ec154f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 648196 | 2025-07-25 14:19:46 AEST | 2025-07-25 07:44:38 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
10b30c12-8143-4d5e-a6fc-a2ba9ba22249 | b99745a4-6c55-4c2d-a61f-61c711ec154f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 603258 | 2025-07-25 14:19:49 AEST | 2025-07-25 07:44:38 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
981dfbef-dab9-4686-b331-d993417897a5 | b99745a4-6c55-4c2d-a61f-61c711ec154f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 572709 | 2025-07-25 14:19:52 AEST | 2025-07-25 07:44:38 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
49455574-2f1c-4dfd-885c-5a2aa08b88ba | 36047a2f-ceec-41b9-bd16-fbc58f3d9bcf | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 743362 | 2025-07-26 02:09:35 AEST | 2025-07-26 08:01:11 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
67d6067d-4359-4f3f-a42a-8c096472d14d | 800101e1-12c7-438b-aae8-acf58c388170 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 765901 | 2025-07-26 02:09:49 AEST | 2025-07-26 08:05:57 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ce2f66ce-3d56-4c98-9611-d056136db93c | 800101e1-12c7-438b-aae8-acf58c388170 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 754470 | 2025-07-26 02:09:43 AEST | 2025-07-26 08:05:57 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
2c5c859e-3bf8-4846-aad9-8c4222b9cb51 | 98b0160a-e4d9-495e-a71e-7f4bd089e740 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 742877 | 2025-07-26 02:09:55 AEST | 2025-07-26 08:11:47 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
dfac495b-e0c5-448a-a396-81e8074fa85f | 910d3e2f-7f9c-4702-9a37-4bb93850ea69 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 477725 | 2025-07-25 14:19:43 AEST | 2025-07-25 07:37:47 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7ddc307c-38ee-4e1a-86d9-bd0cee161579 | 910d3e2f-7f9c-4702-9a37-4bb93850ea69 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 591485 | 2025-07-25 14:19:39 AEST | 2025-07-25 07:37:47 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fcf1c48f-7895-4a3c-80d9-6bc0bf0fdc8c | b4b874a0-b5c9-43ea-b4c5-d526140402d0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 546226 | 2025-07-26 09:05:35 AEST | 2025-07-26 11:44:30 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
dae4cce5-57b7-4ee3-a8b8-291a38ee938f | b4b874a0-b5c9-43ea-b4c5-d526140402d0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 392189 | 2025-07-26 09:05:37 AEST | 2025-07-26 11:44:30 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
00c9d8dd-9bfd-49a3-a596-38d8f0071138 | b4b874a0-b5c9-43ea-b4c5-d526140402d0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 699419 | 2025-07-26 02:10:17 AEST | 2025-07-26 08:22:27 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ad0a7959-c2b7-4f67-8720-7b24592ebe8f | b4b874a0-b5c9-43ea-b4c5-d526140402d0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 675446 | 2025-07-26 02:10:22 AEST | 2025-07-26 08:22:27 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
b8587a2b-d64e-4370-aea8-b27b61c3bd78 | e1774fb3-6f1f-4e6e-9937-98d24c610106 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 529299 | 2025-07-26 08:59:20 AEST | 2025-07-26 05:47:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9a3c301d-0ece-4df9-9c7d-661ddd03ccbe | e1774fb3-6f1f-4e6e-9937-98d24c610106 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 609343 | 2025-07-26 08:59:31 AEST | 2025-07-26 05:47:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
61227878-00ea-410e-b8cd-107af2f2ed48 | d2079d53-6fdf-4cee-a81a-fa7a082ebf1b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 549436 | 2025-07-26 08:59:53 AEST | 2025-07-26 05:52:28 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c1b4f27e-a2fe-4e7c-827e-8d484f25f65f | d2079d53-6fdf-4cee-a81a-fa7a082ebf1b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 596127 | 2025-07-26 08:59:57 AEST | 2025-07-26 05:52:28 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
02f8be54-c54f-4303-880a-d1fcdddfc3e1 | ed123515-e4dc-4358-9603-5a750cac4f72 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 553749 | 2025-07-26 08:59:43 AEST | 2025-07-26 05:51:24 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0e8d2a68-ccdd-4446-ba0e-749b56abd6da | ed123515-e4dc-4358-9603-5a750cac4f72 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 587640 | 2025-07-26 08:59:49 AEST | 2025-07-26 05:51:24 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a7c3c37b-4e8a-464f-93ac-c2957888b5fe | 9bb5a904-f8ce-4b79-9e01-ae1498d0cc9e | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 660328 | 2025-07-25 14:20:09 AEST | 2025-07-25 08:03:54 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a1acf176-6b73-48e1-83a4-def600cef99c | 9bb5a904-f8ce-4b79-9e01-ae1498d0cc9e | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 616423 | 2025-07-25 14:20:12 AEST | 2025-07-25 08:03:54 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
20ffd6bf-38f0-4263-9ea8-62498c64bf82 | 55fd7f21-049f-4ca5-adc4-9a61a9c1d5b7 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 527956 | 2025-07-25 14:19:56 AEST | 2025-07-25 07:51:28 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0b146d76-7340-47ec-bb06-1af2440b0aed | 55fd7f21-049f-4ca5-adc4-9a61a9c1d5b7 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 436340 | 2025-07-25 14:19:59 AEST | 2025-07-25 07:51:28 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a29e1750-79f7-4b77-b9f0-2837ee693a23 | 55fd7f21-049f-4ca5-adc4-9a61a9c1d5b7 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 605552 | 2025-07-25 14:20:06 AEST | 2025-07-25 07:53:05 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c2e9bf4b-c1da-4eb9-90aa-d08edcbf10a7 | 55fd7f21-049f-4ca5-adc4-9a61a9c1d5b7 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 577575 | 2025-07-25 14:20:03 AEST | 2025-07-25 07:53:05 AEST |  |  |  | 2100 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ed661ccd-3a9e-44ce-b612-d5902e117551 | 01d680a6-a0ad-44b5-94ff-74c2de606e60 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 564922 | 2025-07-26 09:01:02 AEST | 2025-07-26 06:00:25 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
20598274-a77f-4988-9cd2-9011564b8e55 | 01d680a6-a0ad-44b5-94ff-74c2de606e60 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 588271 | 2025-07-26 09:00:58 AEST | 2025-07-26 06:00:25 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d77c133a-53e2-4dd4-ba36-bee3907f5285 | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 595473 | 2025-07-25 14:32:22 AEST | 2025-07-25 13:35:18 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
edaf1aa8-7c72-4636-a99c-8b8ad1cd5496 | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 544324 | 2025-07-25 14:32:40 AEST | 2025-07-25 13:35:18 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2be78ddc-c48e-4b69-98d1-e1e2be196de6 | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 547201 | 2025-07-25 14:32:03 AEST | 2025-07-25 13:35:18 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cf3ffb0e-df2f-40b3-a53c-02e114f30297 | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 505366 | 2025-07-25 14:32:33 AEST | 2025-07-25 13:35:18 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fc7ecf2d-279d-4284-bb44-e094abaf936f | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 750829 | 2025-07-26 02:10:42 AEST | 2025-07-26 08:44:58 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
9888b100-0e3e-4f5d-96ed-26a878d29599 | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 778457 | 2025-07-26 02:10:51 AEST | 2025-07-26 08:44:58 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
f8998f8a-4346-45eb-ac89-2fa69500c9ba | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 799827 | 2025-07-26 02:10:38 AEST | 2025-07-26 08:44:58 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
810a9103-0137-459b-adf3-96244c180337 | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 715503 | 2025-07-26 02:10:47 AEST | 2025-07-26 08:44:58 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
5de84dd3-9b52-4462-8576-5dc02fedb22a | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 657021 | 2025-07-26 02:10:58 AEST | 2025-07-26 08:45:49 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
59a2f3d9-5ce7-4ca9-9a22-3d6b71cea106 | ffc35b89-5450-4bb2-ad80-7e5f33f4044d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 608302 | 2025-07-26 02:10:54 AEST | 2025-07-26 08:45:49 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7eb8636e-ef63-4358-9ba1-2126ab435a41 | 3563de4c-7e46-482f-a0ec-88aedcda4768 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 720168 | 2025-07-26 02:11:06 AEST | 2025-07-26 08:50:26 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
045a9432-13d5-4cbd-830c-624b07d61535 | aaec5a64-4502-4839-97e3-8e6c9cf7608b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 589101 | 2025-07-25 14:31:33 AEST | 2025-07-25 13:30:29 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ef0c5393-8379-42fc-8507-adb91d07feff | aaec5a64-4502-4839-97e3-8e6c9cf7608b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 563885 | 2025-07-25 14:31:57 AEST | 2025-07-25 13:30:29 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
eaf0e58f-4760-401f-9f0e-5cc1018f1328 | aaec5a64-4502-4839-97e3-8e6c9cf7608b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 535572 | 2025-07-25 14:31:53 AEST | 2025-07-25 13:30:29 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4542aca2-e18b-4872-9b43-158cc7d89e15 | aaec5a64-4502-4839-97e3-8e6c9cf7608b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 548562 | 2025-07-25 14:32:00 AEST | 2025-07-25 13:30:29 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0e573c0e-7550-41e3-a1fc-545ea5f985fb | 383d50f3-4531-4c3a-8d98-443b92af09c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 607936 | 2025-07-26 09:05:39 AEST | 2025-07-26 11:48:58 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e1e7357d-a140-4611-88b7-e6e201d31b05 | 383d50f3-4531-4c3a-8d98-443b92af09c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 655782 | 2025-07-26 02:11:17 AEST | 2025-07-26 09:04:44 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
cbf1391d-cc50-420a-be20-2b7a914c782d | 383d50f3-4531-4c3a-8d98-443b92af09c0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 605143 | 2025-07-26 02:11:09 AEST | 2025-07-26 09:04:44 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
15bd11f9-c8e0-42d1-9219-c0e018f08899 | 0e4daed3-c796-4773-847f-b8812ad8c5b8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 584747 | 2025-07-26 09:01:06 AEST | 2025-07-26 06:04:26 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
91951779-29e6-4712-b5d9-2c227b95dab6 | 0e4daed3-c796-4773-847f-b8812ad8c5b8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 585256 | 2025-07-26 09:01:10 AEST | 2025-07-26 06:04:26 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ccd05839-4d5f-400a-af0c-c8d336a9ad51 | eeaa2e67-c0ba-429f-a820-d1f3e04a9321 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 609943 | 2025-07-26 09:01:50 AEST | 2025-07-26 06:20:36 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
afd5ae55-9944-4f2c-b559-63f848d41bc4 | eeaa2e67-c0ba-429f-a820-d1f3e04a9321 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 488286 | 2025-07-26 09:01:45 AEST | 2025-07-26 06:20:36 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
518d6277-cbd5-4c00-8539-eb959eda7142 | 431f13f4-30a6-4a8a-9a63-84e1fda18faf | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 466639 | 2025-07-26 09:01:15 AEST | 2025-07-26 06:10:32 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b3db6445-d401-4eb8-962c-f0dbc02505f8 | 431f13f4-30a6-4a8a-9a63-84e1fda18faf | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 535947 | 2025-07-26 09:01:20 AEST | 2025-07-26 06:10:32 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1c211c47-e292-45ae-8ad8-daa1a5a7088a | 887f3e3a-e07b-4323-a4b8-306d4d05d7d8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 510915 | 2025-07-25 14:32:55 AEST | 2025-07-25 13:39:32 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4b3caefd-02ce-4c57-97fc-2a6cb7190cae | 887f3e3a-e07b-4323-a4b8-306d4d05d7d8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 517675 | 2025-07-25 14:32:47 AEST | 2025-07-25 13:39:32 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b92b7c1e-026e-4f31-bc04-671d0b06e110 | 887f3e3a-e07b-4323-a4b8-306d4d05d7d8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 506974 | 2025-07-25 14:32:59 AEST | 2025-07-25 13:39:32 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ba45b649-d69a-49d7-b6e2-bb0f584e0664 | 887f3e3a-e07b-4323-a4b8-306d4d05d7d8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 677847 | 2025-07-26 09:01:29 AEST | 2025-07-26 06:13:00 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1afad40b-15fb-43fd-9090-cd3063378110 | 887f3e3a-e07b-4323-a4b8-306d4d05d7d8 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 489380 | 2025-07-26 09:01:24 AEST | 2025-07-26 06:13:00 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
980010c5-5242-4b3e-9f43-969e836f8bf9 | 17067ec4-fc76-4013-a2c2-fb867d713246 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 603666 | 2025-07-26 09:01:38 AEST | 2025-07-26 06:18:29 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b8b537c4-4efd-4cb8-ad30-4f61e37cb3bf | 17067ec4-fc76-4013-a2c2-fb867d713246 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 611712 | 2025-07-26 09:01:33 AEST | 2025-07-26 06:18:29 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d382f388-3d14-4ed9-83fa-1f35b227fa7a | 17067ec4-fc76-4013-a2c2-fb867d713246 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 533007 | 2025-07-26 09:01:41 AEST | 2025-07-26 06:18:29 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d554bd2d-7cb1-4af7-8875-583bfca89b91 | 11197ffd-f03f-4ede-8dc1-18fde6e0a681 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 544317 | 2025-07-25 14:33:21 AEST | 2025-07-25 13:47:46 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
33bde6ca-4622-49fe-9d47-b684c3103611 | 11197ffd-f03f-4ede-8dc1-18fde6e0a681 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 561297 | 2025-07-25 14:33:14 AEST | 2025-07-25 13:47:46 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1276c4d9-eacb-4972-b5c0-eca7fb820a19 | 11197ffd-f03f-4ede-8dc1-18fde6e0a681 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 615150 | 2025-07-25 14:33:06 AEST | 2025-07-25 13:47:46 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
912557c6-6b72-4bfc-9695-f3fd6c918f22 | 11197ffd-f03f-4ede-8dc1-18fde6e0a681 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 546080 | 2025-07-25 14:33:30 AEST | 2025-07-25 13:48:17 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1673d7a4-6330-480b-8fe5-00b1e1c1909e | 11197ffd-f03f-4ede-8dc1-18fde6e0a681 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 809850 | 2025-07-26 02:11:33 AEST | 2025-07-26 09:21:13 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
03de7e87-38a1-426b-8c1a-10231cebc16c | 11197ffd-f03f-4ede-8dc1-18fde6e0a681 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 823546 | 2025-07-26 02:11:37 AEST | 2025-07-26 09:21:13 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
048f336c-331c-44ab-be48-a1d1e382f180 | d9fb836e-c6e3-4b9b-8f55-108196102b03 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 632416 | 2025-07-25 14:33:43 AEST | 2025-07-25 13:49:35 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0285259a-39db-470b-85c6-70732354b245 | d9fb836e-c6e3-4b9b-8f55-108196102b03 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 601090 | 2025-07-25 14:34:07 AEST | 2025-07-25 13:49:35 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
aae6bbad-32b0-47cf-bdde-de3776d87ca9 | d9fb836e-c6e3-4b9b-8f55-108196102b03 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 691180 | 2025-07-25 14:33:54 AEST | 2025-07-25 13:49:35 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d5d7338a-e7b7-45ab-b46c-feef257e158f | 222f749a-135e-41c6-b361-e6e484967b47 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 716122 | 2025-07-26 02:11:30 AEST | 2025-07-26 09:18:15 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
174558fe-8dd9-4fa7-af87-61f8c3859668 | 141e8104-0ec7-40da-bb04-54359c11178b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 552086 | 2025-07-26 09:05:49 AEST | 2025-07-26 11:56:06 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a0e7be45-4b32-43c8-85c9-ffbb68096833 | 141e8104-0ec7-40da-bb04-54359c11178b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 352900 | 2025-07-26 09:05:47 AEST | 2025-07-26 11:56:06 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
12bf45da-187b-4a55-a36b-b5cd9b811c3e | 141e8104-0ec7-40da-bb04-54359c11178b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 626162 | 2025-07-26 02:11:21 AEST | 2025-07-26 09:13:53 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
2926ca91-bc09-4e97-be33-34722a320eca | 141e8104-0ec7-40da-bb04-54359c11178b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 626576 | 2025-07-26 02:11:27 AEST | 2025-07-26 09:13:53 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
91dff720-7a11-4a7f-a930-6f991b6fa261 | 141e8104-0ec7-40da-bb04-54359c11178b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 673791 | 2025-07-26 02:11:23 AEST | 2025-07-26 09:13:53 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
02257ad4-c6f5-49c8-93c3-d5ac102459be | 6dcea904-d085-481d-8420-db3025fc0fbc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 513176 | 2025-07-26 09:02:19 AEST | 2025-07-26 06:29:08 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7a13b892-1f45-438d-ae36-10e573ac20f2 | 6dcea904-d085-481d-8420-db3025fc0fbc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 508623 | 2025-07-26 09:02:23 AEST | 2025-07-26 06:29:08 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cb84358a-1ee0-49fc-9240-a3a08dc12eb5 | 64fcdc3c-ea6e-4ebe-a6aa-fd339305c307 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 598586 | 2025-07-25 14:35:18 AEST | 2025-07-25 14:03:10 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b304ffc2-232a-4e99-84e0-e1dabbf84399 | 64fcdc3c-ea6e-4ebe-a6aa-fd339305c307 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 554064 | 2025-07-25 14:34:53 AEST | 2025-07-25 14:03:10 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
dafacd1f-a5d3-4602-95d0-56106186da11 | 64fcdc3c-ea6e-4ebe-a6aa-fd339305c307 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 503140 | 2025-07-25 14:36:06 AEST | 2025-07-25 14:03:10 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
56f77b31-ad97-4f9b-89f0-d2f4e38bd74b | 64fcdc3c-ea6e-4ebe-a6aa-fd339305c307 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 560762 | 2025-07-25 14:35:36 AEST | 2025-07-25 14:03:10 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
acb35c9a-dcc4-49f8-b174-d5d825eefb6b | 64fcdc3c-ea6e-4ebe-a6aa-fd339305c307 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 543812 | 2025-07-25 14:35:58 AEST | 2025-07-25 14:03:10 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
dfd37fc9-129e-4c3e-a4ae-4e512f136012 | 64fcdc3c-ea6e-4ebe-a6aa-fd339305c307 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 471374 | 2025-07-25 14:36:08 AEST | 2025-07-25 14:03:10 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
467debd4-4879-4375-958a-6600ba0842f2 | 46fc460e-a0ba-494c-8a96-54a0382bcd62 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 647754 | 2025-07-25 14:34:36 AEST | 2025-07-25 13:55:03 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
be2e32b1-d22b-422e-b74a-d3d89ff8410b | 46fc460e-a0ba-494c-8a96-54a0382bcd62 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 581529 | 2025-07-25 14:34:22 AEST | 2025-07-25 13:55:03 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d8fc9fbb-5979-4485-b878-bab943cfa177 | c2fa3dd4-43d2-4f5c-bdca-8fef9de54fb0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 592405 | 2025-07-25 14:36:32 AEST | 2025-07-25 14:05:30 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
64e24e0c-488f-4eaf-bbe9-da8d389bb2d8 | c2fa3dd4-43d2-4f5c-bdca-8fef9de54fb0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 548041 | 2025-07-25 14:36:12 AEST | 2025-07-25 14:05:30 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8053c45a-5309-4551-ab91-1698a3336ec0 | c2fa3dd4-43d2-4f5c-bdca-8fef9de54fb0 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 622087 | 2025-07-25 14:36:24 AEST | 2025-07-25 14:05:30 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f60dfe0e-7607-4515-b662-a6d685d4992a | 2fb4e483-6c33-4b3f-a375-3e85983f3dca | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 817524 | 2025-07-26 02:11:40 AEST | 2025-07-26 09:27:33 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
fe2af408-9d65-4d0c-afd9-b874ad7464ab | a8304509-aa85-4dd2-9281-f6ebaaa0269f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 548449 | 2025-07-26 09:05:53 AEST | 2025-07-26 11:59:17 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6f6ce16c-4a8e-44e2-805e-dc53e532aa87 | a8304509-aa85-4dd2-9281-f6ebaaa0269f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 556889 | 2025-07-26 09:05:51 AEST | 2025-07-26 11:59:17 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e5705c84-89d3-4628-8a81-81749b095600 | a8304509-aa85-4dd2-9281-f6ebaaa0269f | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 779418 | 2025-07-26 02:11:43 AEST | 2025-07-26 09:30:32 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
d17d2477-a793-487a-b840-2786fe87e4c5 | f023df65-b99b-4f4b-91d4-7d4dd711533d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 520647 | 2025-07-25 14:36:39 AEST | 2025-07-25 14:10:44 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a2a95716-88dc-4efd-b786-d28a6fa04a7a | 523633b6-00c8-4ad5-b66d-af28a7d82129 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 497498 | 2025-07-26 09:02:26 AEST | 2025-07-26 06:34:32 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ea05410b-ae70-4a0b-8e8c-9c3ecf520241 | 109f4bd5-c219-42a5-8b77-67d3f03950d3 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 474648 | 2025-07-25 14:37:19 AEST | 2025-07-25 14:27:20 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
84301d77-9a6c-4568-94b6-3d0846b6cfee | 109f4bd5-c219-42a5-8b77-67d3f03950d3 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 352039 | 2025-07-25 14:37:28 AEST | 2025-07-25 14:27:20 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ebe96420-4023-4f8c-a947-003aeb13bc1c | 109f4bd5-c219-42a5-8b77-67d3f03950d3 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 481400 | 2025-07-25 14:37:37 AEST | 2025-07-25 14:27:20 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e928c43b-a10d-4ccf-90fc-063cfdf12163 | 109f4bd5-c219-42a5-8b77-67d3f03950d3 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 469453 | 2025-07-25 14:37:54 AEST | 2025-07-25 14:27:20 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b95217c6-bd62-44d8-b5d9-89f6d4f240d7 | 90ceded3-5abc-4e24-ae89-53be65caf3f4 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 561311 | 2025-07-25 14:38:10 AEST | 2025-07-25 14:30:53 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4d158c83-df3c-432c-aef9-db3900320b13 | 90ceded3-5abc-4e24-ae89-53be65caf3f4 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 614152 | 2025-07-25 14:38:18 AEST | 2025-07-25 14:30:53 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a31084ca-49a9-47a1-9d25-c40b536b6fc5 | 9ab289f6-f7b4-498d-bdfc-58150311d0c5 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 554113 | 2025-07-26 09:02:45 AEST | 2025-07-26 06:47:19 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b61c16c9-9eab-47b7-8936-34063610a5f7 | 9ab289f6-f7b4-498d-bdfc-58150311d0c5 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 562562 | 2025-07-26 09:02:47 AEST | 2025-07-26 06:47:19 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1102c233-2efc-480a-926a-b699b899636e | 7ad72d98-d76b-411b-8cd1-de70d311b8dc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 473644 | 2025-07-26 09:02:50 AEST | 2025-07-26 06:54:25 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f9011d44-8021-4bd4-9b07-0b684d5dc098 | 7ad72d98-d76b-411b-8cd1-de70d311b8dc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 358267 | 2025-07-26 09:02:52 AEST | 2025-07-26 06:54:25 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a1f58cbf-26a8-4fb5-a7d2-d94822cf7aa7 | 072ede3b-db09-4382-b7ea-355ee456bfe9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 533936 | 2025-07-25 14:38:44 AEST | 2025-07-25 14:36:04 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8ef908c0-2712-4bd2-b46e-cda663dc170e | 072ede3b-db09-4382-b7ea-355ee456bfe9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 484244 | 2025-07-25 14:38:37 AEST | 2025-07-25 14:36:03 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5034d408-455e-4283-b547-4ca2d1d54a47 | 072ede3b-db09-4382-b7ea-355ee456bfe9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 530628 | 2025-07-25 14:38:27 AEST | 2025-07-25 14:36:03 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
62d61bc0-d1bc-43c5-9402-505d1db69135 | 1cade013-f352-47ee-b7d6-91559ef6d009 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 616460 | 2025-07-25 14:39:21 AEST | 2025-07-25 14:41:43 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
57af7c89-a9fc-4c99-859f-5ea8679ca412 | 1cade013-f352-47ee-b7d6-91559ef6d009 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 515014 | 2025-07-25 14:39:07 AEST | 2025-07-25 14:41:43 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
425ea099-b4d6-4634-bda2-fa3ccf914033 | 1cade013-f352-47ee-b7d6-91559ef6d009 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 542207 | 2025-07-25 14:38:56 AEST | 2025-07-25 14:41:43 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5882b3c1-70f8-4ad5-b81c-4015d09d9f38 | 1cade013-f352-47ee-b7d6-91559ef6d009 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 525849 | 2025-07-25 14:39:24 AEST | 2025-07-25 14:41:43 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
79fd18da-75a8-490e-9012-ec5067301f90 | 1cade013-f352-47ee-b7d6-91559ef6d009 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 677129 | 2025-07-26 06:49:06 AEST | 2025-07-26 11:29:00 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
43a78402-db86-4d45-ae37-88c3d9c138c3 | 3656cb31-58e3-485a-b23e-e5887d9d7326 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 464233 | 2025-07-25 14:39:29 AEST | 2025-07-25 14:44:24 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e029ac16-2fb5-4868-829c-2408e4677be5 | 3656cb31-58e3-485a-b23e-e5887d9d7326 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 559487 | 2025-07-25 14:39:39 AEST | 2025-07-25 14:44:24 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a2e722ef-9173-4534-9ec5-f63ce1adfbf0 | 3656cb31-58e3-485a-b23e-e5887d9d7326 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 644412 | 2025-07-25 14:39:49 AEST | 2025-07-25 14:44:24 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9796feb2-3719-48df-9f58-503f6238e97b | 99e5ab55-10c7-415f-b20e-ca8f8b62c0a6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 421375 | 2025-07-26 09:03:01 AEST | 2025-07-26 07:08:31 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7be9d910-b1af-4294-9347-d6239351d06e | a0c66409-2f0e-4a4c-a6cc-38609de9149d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 483643 | 2025-07-26 09:03:03 AEST | 2025-07-26 07:12:29 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6e7469eb-53bc-4e0d-8c4f-b83f43747be0 | a0c66409-2f0e-4a4c-a6cc-38609de9149d | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 469470 | 2025-07-26 09:03:05 AEST | 2025-07-26 07:12:29 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
55f5d44d-28cb-4716-8d41-314aaa741119 | f0dad168-e3c4-4a95-94ab-e924a4588988 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 637731 | 2025-07-25 14:40:43 AEST | 2025-07-25 14:48:21 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
17fcf3bc-05bd-4140-851a-cf228751a924 | f0dad168-e3c4-4a95-94ab-e924a4588988 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 606472 | 2025-07-25 14:40:08 AEST | 2025-07-25 14:48:21 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
faefdd16-2fa1-485d-8cc3-4efd445845bf | f0dad168-e3c4-4a95-94ab-e924a4588988 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 605314 | 2025-07-25 14:39:58 AEST | 2025-07-25 14:48:21 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bdae1384-5452-44ea-ad39-f592854049cb | f0dad168-e3c4-4a95-94ab-e924a4588988 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 577678 | 2025-07-25 14:40:19 AEST | 2025-07-25 14:48:21 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
48e93ab7-2d22-43d9-b93d-75bb1270dab8 | c4d1f892-b6b6-49a6-b3be-6445a5d1160b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 585490 | 2025-07-25 14:41:09 AEST | 2025-07-25 14:50:40 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ff296b50-e7e4-4595-87f9-70eeee027231 | c4d1f892-b6b6-49a6-b3be-6445a5d1160b | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 575431 | 2025-07-25 14:40:58 AEST | 2025-07-25 14:50:40 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e6426162-991f-4dcb-b299-9caca9228b36 | ebdae796-dab7-4f96-9bb9-ec01249d3233 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 547534 | 2025-07-26 09:03:13 AEST | 2025-07-26 07:20:26 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
77646e20-d50a-47e7-8447-25ce4ad22fc6 | ebdae796-dab7-4f96-9bb9-ec01249d3233 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 498585 | 2025-07-26 09:03:15 AEST | 2025-07-26 07:20:26 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bf90a6ee-3c6c-476c-a058-a9d57b9c52b8 | ebdae796-dab7-4f96-9bb9-ec01249d3233 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 707846 | 2025-07-26 06:49:09 AEST | 2025-07-26 11:33:38 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
41697202-670f-4eab-8e31-8ad651f35593 | d0ef7de2-ddff-4fda-88c0-de4574cb290a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 675669 | 2025-07-26 09:03:17 AEST | 2025-07-26 07:23:15 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bd6e5570-a951-4165-8491-620e396610e8 | d0ef7de2-ddff-4fda-88c0-de4574cb290a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 626586 | 2025-07-26 09:03:28 AEST | 2025-07-26 07:23:15 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6a7dd223-9a7b-470a-b2d0-f2adac02fe65 | d0ef7de2-ddff-4fda-88c0-de4574cb290a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 595941 | 2025-07-26 06:49:13 AEST | 2025-07-26 11:38:56 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
6c6ab83e-e8b3-4c39-9d27-f8cd1111d113 | 596e41a3-dbf5-4c85-97b4-4f9b2d5080c6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 682514 | 2025-07-25 14:43:53 AEST | 2025-07-25 15:00:25 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7b614505-dd8d-4422-b2bf-500c39b0ae07 | 596e41a3-dbf5-4c85-97b4-4f9b2d5080c6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 572523 | 2025-07-25 14:44:13 AEST | 2025-07-25 15:00:25 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f0e2389b-c9e0-442e-89b0-e54c96351401 | 596e41a3-dbf5-4c85-97b4-4f9b2d5080c6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 619131 | 2025-07-25 14:42:56 AEST | 2025-07-25 15:00:24 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
692a3c1b-4b72-4e74-9679-2e4dc0b6ea19 | 596e41a3-dbf5-4c85-97b4-4f9b2d5080c6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 682897 | 2025-07-25 14:44:08 AEST | 2025-07-25 15:00:25 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7e8864ee-1dbc-4c20-9006-808e80852081 | 596e41a3-dbf5-4c85-97b4-4f9b2d5080c6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 685274 | 2025-07-25 14:43:07 AEST | 2025-07-25 15:00:24 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
908e745d-fe13-4747-b83f-5b04446f6d56 | 596e41a3-dbf5-4c85-97b4-4f9b2d5080c6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 701296 | 2025-07-25 14:43:36 AEST | 2025-07-25 15:00:25 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1e838a62-fd4a-4fdc-a31a-c62a46b562c6 | 596e41a3-dbf5-4c85-97b4-4f9b2d5080c6 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 629202 | 2025-07-25 14:43:20 AEST | 2025-07-25 15:00:25 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8aec4480-5969-4434-8634-595bffbebfad | e3a83c78-ce48-49f7-9fae-36f7e5323dbe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 588421 | 2025-07-25 14:41:19 AEST | 2025-07-25 14:54:39 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2f93a6b0-54f3-4653-a477-8c53bd6744f6 | e3a83c78-ce48-49f7-9fae-36f7e5323dbe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 625610 | 2025-07-25 14:41:53 AEST | 2025-07-25 14:54:39 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f95e5914-6197-4658-9209-3b027d591d49 | e3a83c78-ce48-49f7-9fae-36f7e5323dbe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 656141 | 2025-07-25 14:41:36 AEST | 2025-07-25 14:54:39 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d6e2b017-96a7-46af-a258-91c766aa2b47 | e3a83c78-ce48-49f7-9fae-36f7e5323dbe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 689866 | 2025-07-25 14:42:08 AEST | 2025-07-25 14:54:39 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e7633f90-0897-4fc1-bf20-c6c32b258e30 | e3a83c78-ce48-49f7-9fae-36f7e5323dbe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 719295 | 2025-07-25 14:42:46 AEST | 2025-07-25 14:58:41 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4debb331-7b05-4dbd-86c7-ccdba12b1923 | e3a83c78-ce48-49f7-9fae-36f7e5323dbe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 611565 | 2025-07-25 14:42:19 AEST | 2025-07-25 14:58:41 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8dfa854c-5d84-40a2-b26d-bda905bb3d7e | e3a83c78-ce48-49f7-9fae-36f7e5323dbe | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 624548 | 2025-07-25 14:42:30 AEST | 2025-07-25 14:58:41 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
edc7189f-afd7-4d24-b285-6babe25d0647 | 5ef6d70d-561f-46a5-9580-934d19e7d80e | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 724070 | 2025-07-25 14:28:04 AEST | 2025-07-25 11:32:30 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
26755449-d00f-4f0e-b4e3-d3dd944342b6 | 5ef6d70d-561f-46a5-9580-934d19e7d80e | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 788560 | 2025-07-25 14:28:27 AEST | 2025-07-25 11:33:01 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
901030b5-5cdc-4bc0-b72c-4c633050158c | 5ef6d70d-561f-46a5-9580-934d19e7d80e | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 564228 | 2025-07-25 14:28:11 AEST | 2025-07-25 11:33:01 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0784df72-90e8-4482-8f61-a2b5a5dc29fe | 5ef6d70d-561f-46a5-9580-934d19e7d80e | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 652416 | 2025-07-25 14:28:19 AEST | 2025-07-25 11:33:01 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b64139f6-b7d0-45a7-849c-4efb48f5ca63 | 346e645c-2781-4628-a7c6-ca018732a962 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 677166 | 2025-07-25 14:28:40 AEST | 2025-07-25 11:35:49 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
43a08049-c750-44d8-8e7d-70eb4b6a4e9a | 346e645c-2781-4628-a7c6-ca018732a962 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 570717 | 2025-07-25 14:28:34 AEST | 2025-07-25 11:35:49 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4f91ea85-1f86-45ef-8a93-9d9fd436de3f | 346e645c-2781-4628-a7c6-ca018732a962 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 568080 | 2025-07-25 14:28:49 AEST | 2025-07-25 11:35:49 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c6c42ea1-1e33-46a4-9d2f-4147dea5f27c | 346e645c-2781-4628-a7c6-ca018732a962 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 599991 | 2025-07-25 14:29:03 AEST | 2025-07-25 11:35:49 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
52677a69-e488-4ba9-980f-8a271f393e95 | f84cada6-2f37-456c-b76f-3d2e852af1ba | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 708879 | 2025-07-25 14:29:46 AEST | 2025-07-25 11:42:14 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
67ea4000-8a43-431b-a416-e2d947965b3f | f84cada6-2f37-456c-b76f-3d2e852af1ba | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 690799 | 2025-07-25 14:30:09 AEST | 2025-07-25 11:42:14 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
09ef15ac-24db-4a62-b0d6-3f03663a86e3 | f84cada6-2f37-456c-b76f-3d2e852af1ba | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 710775 | 2025-07-25 14:30:13 AEST | 2025-07-25 11:42:14 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d8fb736f-d971-4b87-8a36-1ea2d61a5550 | 81cbcc23-02d5-476c-a144-e7541a7e800a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 576303 | 2025-07-25 14:31:10 AEST | 2025-07-25 11:43:22 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2b1b9226-cb65-466c-af27-3a00c58e51c8 | 81cbcc23-02d5-476c-a144-e7541a7e800a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 513028 | 2025-07-25 14:30:55 AEST | 2025-07-25 11:43:22 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
03c0b8a5-24a0-4306-8b85-8ea0abcbb079 | 81cbcc23-02d5-476c-a144-e7541a7e800a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3181 | 118.5773 | POINT (118.5772832 -20.3181078) | 543869 | 2025-07-25 14:30:41 AEST | 2025-07-25 11:43:22 AEST | 16.2466 |  |  | 16 |  |  | -20.3181 | S | 118.5773 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d1a6dc5e-f0ca-41f3-8b75-1cfaeed3c5e6 | aae40368-acd8-4e9c-942e-2325b18f8cfd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 550945 | 2025-07-25 14:36:47 AEST | 2025-07-25 14:19:38 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
62b115b1-b13a-40c0-af81-d412d607252f | aae40368-acd8-4e9c-942e-2325b18f8cfd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 547054 | 2025-07-25 14:36:56 AEST | 2025-07-25 14:19:39 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a4793948-2e45-4019-a6f3-3c340273dce7 | aae40368-acd8-4e9c-942e-2325b18f8cfd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 529690 | 2025-07-25 14:36:53 AEST | 2025-07-25 14:19:38 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
daa55799-ac26-448f-8f68-f7cb32bdd9e5 | aef5a7b8-bc4c-4984-92a6-e437e6826dcd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 607307 | 2025-07-25 14:37:10 AEST | 2025-07-25 14:20:50 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c135c50d-cd84-4780-bd23-2bf5963f4e6f | aef5a7b8-bc4c-4984-92a6-e437e6826dcd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 612093 | 2025-07-25 14:37:04 AEST | 2025-07-25 14:20:50 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
225b9ea0-68af-4aa9-98e9-c9a5a8061a39 | aef5a7b8-bc4c-4984-92a6-e437e6826dcd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3155 | 118.5803 | POINT (118.5803452 -20.3155446) | 546885 | 2025-07-25 14:36:59 AEST | 2025-07-25 14:20:50 AEST |  |  |  | 300 |  |  | -20.3155 | S | 118.5803 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a772dca6-2e94-4749-a3e1-855400b3fa19 | 8edc492f-440e-4a00-81f0-2f19fb6f97cb | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 773369 | 2025-07-26 09:00:20 AEST | 2025-07-26 05:57:52 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7b100185-72dd-4d46-8617-f78c6acb26e4 | 8edc492f-440e-4a00-81f0-2f19fb6f97cb | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 663482 | 2025-07-26 09:00:51 AEST | 2025-07-26 05:57:52 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6c510e4f-dc6b-4dea-a615-9c57e3b6da73 | 8edc492f-440e-4a00-81f0-2f19fb6f97cb | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 656816 | 2025-07-26 09:00:09 AEST | 2025-07-26 05:57:52 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
386950d3-d005-45a4-a87a-623bbd001819 | 8edc492f-440e-4a00-81f0-2f19fb6f97cb | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 651975 | 2025-07-26 09:00:23 AEST | 2025-07-26 05:57:52 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9a391b83-481a-4727-94c1-acc452f0d719 | 7b7b88c1-3dfc-47bc-bfca-059c31eade05 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 647129 | 2025-07-26 09:01:54 AEST | 2025-07-26 06:24:52 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b165d502-43de-4243-ba66-d66fcd00da26 | 7b7b88c1-3dfc-47bc-bfca-059c31eade05 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 705773 | 2025-07-26 09:02:03 AEST | 2025-07-26 06:24:52 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
090c8e29-f037-4750-825f-4b295f93d478 | 7b7b88c1-3dfc-47bc-bfca-059c31eade05 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 681943 | 2025-07-26 09:01:59 AEST | 2025-07-26 06:24:52 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
84fd8589-72e3-4f5f-8571-ceb2af2dd6be | 7b7b88c1-3dfc-47bc-bfca-059c31eade05 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 610828 | 2025-07-26 09:02:08 AEST | 2025-07-26 06:26:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
370ac7b9-1d76-4870-9ee1-88555e7f20cc | 7b7b88c1-3dfc-47bc-bfca-059c31eade05 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 599753 | 2025-07-26 09:02:12 AEST | 2025-07-26 06:26:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
91d54b45-3670-4f84-95e1-0073e5f0c8a1 | 7b7b88c1-3dfc-47bc-bfca-059c31eade05 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 607364 | 2025-07-26 09:02:16 AEST | 2025-07-26 06:26:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bff15338-136e-41f5-8877-9bb7ea8769f2 | e4dc191a-e47e-4fdf-bbdb-af15bcb43fd9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 573644 | 2025-07-26 09:02:28 AEST | 2025-07-26 06:40:13 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
32916502-f842-4dd2-b795-1f091a3121cc | e4dc191a-e47e-4fdf-bbdb-af15bcb43fd9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 630187 | 2025-07-26 09:02:33 AEST | 2025-07-26 06:40:13 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3a8d0fac-5565-4c3a-9d95-c1a5feb9d335 | e4dc191a-e47e-4fdf-bbdb-af15bcb43fd9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 632930 | 2025-07-26 09:02:30 AEST | 2025-07-26 06:40:13 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
61fd9046-19a6-4f10-af59-dc047020dc5e | e4dc191a-e47e-4fdf-bbdb-af15bcb43fd9 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 546863 | 2025-07-26 09:02:35 AEST | 2025-07-26 06:40:13 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
37ff5632-9c25-4c48-9f66-7fe75c20a820 | d2036d0c-4fc5-4cd3-80c8-24e517c99978 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 700224 | 2025-07-26 09:02:38 AEST | 2025-07-26 06:43:06 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cac25a3e-9fea-4175-b3f7-895298c0d862 | d2036d0c-4fc5-4cd3-80c8-24e517c99978 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 738631 | 2025-07-26 09:02:42 AEST | 2025-07-26 06:43:06 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6d8e5058-bc34-476b-b79f-1704a9cb6fae | d2036d0c-4fc5-4cd3-80c8-24e517c99978 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 720528 | 2025-07-26 09:02:40 AEST | 2025-07-26 06:43:06 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
10cf6696-9bbd-4e01-8c18-cb59796e9cf0 | 4545d5d4-4261-4c10-99d4-d55c3457b7dc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 803472 | 2025-07-26 09:02:57 AEST | 2025-07-26 06:58:04 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b36a0159-c164-4df3-b673-04cee0b07bfd | 4545d5d4-4261-4c10-99d4-d55c3457b7dc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 855498 | 2025-07-26 09:02:59 AEST | 2025-07-26 06:58:04 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
84670683-461b-4c6a-bbcd-4ea8717c85c9 | 4545d5d4-4261-4c10-99d4-d55c3457b7dc | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 796473 | 2025-07-26 09:02:55 AEST | 2025-07-26 06:58:04 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
602236ac-6e84-46d5-b1e8-03ff46d6e67d | f19aeb91-d25e-4824-8d63-e8dcdc15ee04 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 791413 | 2025-07-26 09:03:11 AEST | 2025-07-26 07:17:48 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cae8d23b-0e84-45a8-8fc5-a7ac5c898445 | f19aeb91-d25e-4824-8d63-e8dcdc15ee04 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 758907 | 2025-07-26 09:03:07 AEST | 2025-07-26 07:17:48 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
942b882e-0fa2-4c5b-b524-3112674a9ec0 | f19aeb91-d25e-4824-8d63-e8dcdc15ee04 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 740890 | 2025-07-26 09:03:09 AEST | 2025-07-26 07:17:48 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f5c7ec6d-9532-4ed8-94b8-2b93c6158425 | afa45073-e8c6-40dc-8de9-066f5c506b6a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 620056 | 2025-07-26 09:05:45 AEST | 2025-07-26 11:52:50 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2aa90147-ca84-4184-b054-938be39279e4 | afa45073-e8c6-40dc-8de9-066f5c506b6a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 505573 | 2025-07-26 09:05:41 AEST | 2025-07-26 11:52:50 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
dd6e1ffa-7d25-4b37-9cde-324d84846b79 | afa45073-e8c6-40dc-8de9-066f5c506b6a | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 614817 | 2025-07-26 09:05:43 AEST | 2025-07-26 11:52:50 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3c121795-1042-4e8e-8d95-a15784cded50 | 64540b4a-7839-4db1-8e19-457aa72832fa | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 772783 | 2025-07-26 02:10:06 AEST | 2025-07-26 08:14:25 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
17ed5f55-ca9c-48c8-b66f-8c77f5a74027 | 64540b4a-7839-4db1-8e19-457aa72832fa | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 796786 | 2025-07-26 02:10:00 AEST | 2025-07-26 08:14:25 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
9d0f658b-3f36-418d-892d-187850d72c71 | 64540b4a-7839-4db1-8e19-457aa72832fa | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 797130 | 2025-07-26 02:10:11 AEST | 2025-07-26 08:14:25 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c5c5c46c-e585-4edf-a2b5-482a7eaeb322 | 51bb57ab-a0a2-4254-a00e-1b00e3d114dd | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 729349 | 2025-07-26 02:10:26 AEST | 2025-07-26 08:25:51 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
da78caef-d92e-4c89-9b0c-dcc7a1539eac | e197d5f3-117b-4d73-a487-22df8187f956 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 780771 | 2025-07-26 02:10:34 AEST | 2025-07-26 08:30:13 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
fcee5589-c6f1-43f7-813a-516c26a62649 | e197d5f3-117b-4d73-a487-22df8187f956 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 836755 | 2025-07-26 02:10:31 AEST | 2025-07-26 08:30:13 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ddfb31d0-8fb4-4c25-8266-5e95de75f0e3 | 1617d1b3-9d83-460a-8a01-ee2eba215935 | a396a13f-fd7c-4b8f-8265-dbe7f1c1a200 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 694462 | 2025-07-26 06:49:18 AEST | 2025-07-26 11:44:14 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
b6f472ea-25b1-43b6-ac51-f63840424501 | 6bcb124f-7e46-41d8-9ede-92f496c0cf71 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 507939 | 2025-07-26 09:03:30 AEST | 2025-07-26 07:36:16 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
63071f1c-e0b4-45fe-97c3-310c353624e5 | 6bcb124f-7e46-41d8-9ede-92f496c0cf71 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 566047 | 2025-07-26 09:03:32 AEST | 2025-07-26 07:36:16 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7db07702-c633-46db-951a-4f3cff5b8170 | 98fd9997-c332-44fa-b796-5e644c245f9f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 554817 | 2025-07-26 09:03:37 AEST | 2025-07-26 07:37:48 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e4cfbdb7-5de3-4c8a-98c6-40fccfef81a0 | 98fd9997-c332-44fa-b796-5e644c245f9f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 534896 | 2025-07-26 09:03:34 AEST | 2025-07-26 07:37:48 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
996f316a-f350-4a40-b356-0220db4cd6be | 5ac89e87-82be-4a89-9d1b-174fdd457155 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 612398 | 2025-07-26 09:03:52 AEST | 2025-07-26 07:38:57 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4436e8f6-f2f7-4167-b7b0-bcd5f5d0f5ba | 5ac89e87-82be-4a89-9d1b-174fdd457155 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 630876 | 2025-07-26 09:03:48 AEST | 2025-07-26 07:38:57 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
75d58f15-8605-4e01-83db-475abd4cc269 | 5ac89e87-82be-4a89-9d1b-174fdd457155 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.318 | 118.5774 | POINT (118.57738055555555 -20.317991666666668) | 229067 | 2025-07-25 19:56:43 AEST | 2025-07-26 02:14:50 AEST | 7.3948 | 2025-07-25 | 07:57:23 | 4.7487 |  |  | -20.318 | S | 118.5774 | E | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
c8641fbe-d8fb-44bd-b6cf-edb960e0c5d2 | 5ac89e87-82be-4a89-9d1b-174fdd457155 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.318 | 118.5774 | POINT (118.57738055555555 -20.317991666666668) | 274858 | 2025-07-25 19:56:47 AEST | 2025-07-26 02:15:02 AEST | 7.3948 | 2025-07-25 | 07:57:23 | 4.7487 |  |  | -20.318 | S | 118.5774 | E | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5bad25e6-6a48-4405-a6e1-0e530521781f | 19c9ea78-d7fd-47b6-9c24-33a5eaaf171d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.318 | 118.5774 | POINT (118.57738055555555 -20.317991666666668) | 391845 | 2025-07-25 19:56:51 AEST | 2025-07-26 02:18:50 AEST | 7.3948 | 2025-07-25 | 07:57:23 | 4.7487 |  |  | -20.318 | S | 118.5774 | E | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
fd0d10f9-0971-4051-9fb1-c92193ad6246 | 19c9ea78-d7fd-47b6-9c24-33a5eaaf171d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.318 | 118.5774 | POINT (118.57738055555555 -20.317991666666668) | 343534 | 2025-07-25 19:56:55 AEST | 2025-07-26 02:19:06 AEST | 7.3948 | 2025-07-25 | 07:57:23 | 4.7487 |  |  | -20.318 | S | 118.5774 | E | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7c5bb5dd-7aa7-439f-bed3-1f8880fedbb7 | 1d205ac2-371c-481a-b10a-4045187437c2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 234936 | 2025-07-27 18:52:09 AEST | 2025-07-28 01:46:06 AEST | [10 empty] | Apple | iPad mini | TopLeft | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
fb0983a1-d3c9-4cbd-8c37-c934bc766f1d | 94a6f108-47de-4a25-b63f-a512a2e43730 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 716839 | 2025-07-30 07:04:06 AEST | 2025-07-30 13:53:27 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
0ae4cec9-0257-4cbe-98a4-5babb0f08cfc | 94a6f108-47de-4a25-b63f-a512a2e43730 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 786201 | 2025-07-30 07:04:04 AEST | 2025-07-30 13:53:27 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
dbbd3c00-0c7e-4653-bf6a-db16ce226e84 | 432fcdf4-7714-43ec-8423-b6fbb3786aad | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.318 | 118.5774 | POINT (118.57738055555555 -20.317991666666668) | 195020 | 2025-07-25 19:56:57 AEST | 2025-07-26 02:27:36 AEST | 7.3948 | 2025-07-25 | 07:57:23 | 4.7487 |  |  | -20.318 | S | 118.5774 | E | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
2b95e20f-e53d-4d53-966c-e4b2eb9160e0 | 1b8af2d8-2e9e-44f2-86ed-a88c087291cf | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3189 | 118.5749 | POINT (118.57487389999874 -20.318886001386) | 662715 | 2025-07-29 23:51:31 AEST | 2025-07-30 07:20:21 AEST | 11.1672 |  |  | 2400 |  |  | -20.3189 | S | 118.5749 | E | samsung | SM-S931B |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
73cebea0-3e74-4009-8092-fcefc0e41d18 | 1b8af2d8-2e9e-44f2-86ed-a88c087291cf | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3189 | 118.5749 | POINT (118.57487389999874 -20.318886001386) | 648356 | 2025-07-29 23:51:30 AEST | 2025-07-30 07:20:21 AEST | 11.1672 |  |  | 2400 |  |  | -20.3189 | S | 118.5749 | E | samsung | SM-S931B |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
f878161c-fb73-4167-82d3-f2a93625d8c9 | 2370748b-7ebb-4880-b009-9060da5f0c6d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 339804 | 2025-07-25 19:57:04 AEST | 2025-07-26 02:29:13 AEST | [10 empty] | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
a12b5c26-d698-49fd-a02f-5fe7c5f553fa | dcb9bc3b-96d3-46e0-a535-cdd5c055a9c9 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 652691 | 2025-07-31 03:48:23 AEST | 2025-07-31 10:09:44 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
893810e3-6f8b-4fb5-926f-de55de96f439 | dcb9bc3b-96d3-46e0-a535-cdd5c055a9c9 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 531532 | 2025-07-31 03:48:21 AEST | 2025-07-31 10:09:44 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
d0bf9f15-4cdf-4bd7-a13a-1f27f14cbe1d | 81923c34-5394-4c0d-9186-0c3fc765c9fe | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3189 | 118.5749 | POINT (118.57487389999874 -20.318886001386) | 653494 | 2025-07-29 23:51:28 AEST | 2025-07-30 07:16:28 AEST | 11.1672 |  |  | 2400 |  |  | -20.3189 | S | 118.5749 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
e9f5c6c4-3277-4a66-ab84-88d171e6baf3 | 31b29bee-2906-4fc9-95ec-f1bde1fac971 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 171930 | 2025-07-25 19:57:08 AEST | 2025-07-26 02:37:38 AEST | [10 empty] | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
1470dce5-4eb0-4791-876b-74db09b26f86 | 31b29bee-2906-4fc9-95ec-f1bde1fac971 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 272944 | 2025-07-26 19:14:09 AEST | 2025-07-27 00:26:10 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
02a51f70-b9b9-494c-9a2a-dfdfe3c52253 | 3ae9ee7d-8506-469e-955c-3bf208e59b2c | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 371995 | 2025-07-26 19:14:05 AEST | 2025-07-27 00:27:21 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
2acba1fe-9704-49ee-867d-c98ded834f68 | 69953d3d-ea1b-4242-8d81-fd4eb6c74339 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3189 | 118.5749 | POINT (118.57487389999874 -20.318886001386) | 599431 | 2025-07-29 23:51:26 AEST | 2025-07-30 07:15:00 AEST | 11.1672 |  |  | 2400 |  |  | -20.3189 | S | 118.5749 | E | samsung | SM-S931B |  | 1080 | 810 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
b97e26da-86da-4ef9-b632-9a3c64f57c7b | 08c262a7-1d05-4817-91a9-b231e4a1e81c | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 265195 | 2025-07-25 19:57:13 AEST | 2025-07-26 02:40:48 AEST | [10 empty] | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
13a94414-08dc-4211-93d3-419b2783ea62 | 5c4e3434-5a4e-43de-ad15-d202824b207a | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 318094 | 2025-07-25 19:57:17 AEST | 2025-07-26 02:49:05 AEST | [10 empty] | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
25e301d3-bb14-48c5-b1ee-24d0da511abc | 647adb88-42a8-439e-b69f-015b3203d437 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 694031 | 2025-07-31 03:48:08 AEST | 2025-07-31 09:25:58 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
558be3d2-fff7-44a8-a5b1-be645f15b46e | 647adb88-42a8-439e-b69f-015b3203d437 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 474780 | 2025-07-31 03:48:04 AEST | 2025-07-31 09:25:58 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
5baab012-a6c2-48eb-99df-df4306ce7014 | 6b0aae3a-692b-4c0d-ba17-1496d5b2bda2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 164479 | 2025-07-27 18:52:11 AEST | 2025-07-28 02:01:08 AEST | [10 empty] | Apple | iPad mini | BottomRight | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
bef5f32b-a413-40a9-bff9-15f3a38f41ef | 6b0aae3a-692b-4c0d-ba17-1496d5b2bda2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 162898 | 2025-07-27 18:52:14 AEST | 2025-07-28 02:01:19 AEST | [10 empty] | Apple | iPad mini | BottomRight | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
3f9fb810-1ff6-4c0b-91ef-553524ff2143 | 7459ed16-f586-4036-a277-cedae4c732f6 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 668096 | 2025-07-30 07:04:03 AEST | 2025-07-30 13:47:44 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
d3175c42-875d-43b5-b9f2-d70c7c8d135e | 7459ed16-f586-4036-a277-cedae4c732f6 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 712408 | 2025-07-30 07:04:00 AEST | 2025-07-30 13:47:43 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
8e39182b-61ee-4b09-9b91-f45043ad28ff | 4c643bd5-60f9-4b26-b67e-b5e854d79209 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 221406 | 2025-07-27 18:52:16 AEST | 2025-07-28 02:18:53 AEST | [10 empty] | Apple | iPad mini | TopLeft | 1080 | 810 | Fulcrum iOS 2504.0.0 (12301), iOS 18.5, Apple, iPad mini 6 | 72 | 72
e4ef72ed-ca0f-4261-bba3-0952c8d679a6 | 67fcc57b-c6cf-42fd-b8d9-9f4ef18a7ff3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 161575 | 2025-07-25 19:57:20 AEST | 2025-07-26 02:53:51 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
1c644a43-7e83-419b-a0c1-f813fd13d212 | 67fcc57b-c6cf-42fd-b8d9-9f4ef18a7ff3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 331600 | 2025-07-25 19:53:58 AEST | 2025-07-26 02:40:48 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
8ba0c055-3f91-4e24-aea6-16e9df08d301 | 19ec8717-8b46-4dd5-be1d-117e1ed24dc4 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 408310 | 2025-07-25 19:57:23 AEST | 2025-07-26 02:59:04 AEST | [10 empty] | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
78d6672d-facb-4877-baf3-f2d718eeefde | 19ec8717-8b46-4dd5-be1d-117e1ed24dc4 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 298590 | 2025-07-25 19:57:27 AEST | 2025-07-26 02:59:31 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
3a575d20-10f6-4265-a2b2-9f568e8fd700 | 3d18012e-a494-4f85-a0cd-93df985c2c06 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 316758 | 2025-07-25 19:57:30 AEST | 2025-07-26 03:07:06 AEST | [10 empty] | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
6a3d7906-b64f-4603-b19f-922426027e83 | 3d18012e-a494-4f85-a0cd-93df985c2c06 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 332145 | 2025-07-25 19:57:33 AEST | 2025-07-26 03:08:00 AEST | [10 empty] | Apple | iPhone 15 Pro Max | RightTop | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
d3bf7479-0c34-4d2f-b0b2-59f5156eed18 | 3d18012e-a494-4f85-a0cd-93df985c2c06 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 727194 | 2025-07-31 03:48:15 AEST | 2025-07-31 09:34:16 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
a8dda843-df2c-4e66-a807-c02066ef9c04 | ea0534b9-cad0-4c50-b906-c69b5ec18285 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 342976 | 2025-07-25 19:53:29 AEST | 2025-07-26 03:07:41 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
7db0e712-24aa-4dd5-9869-ad02cf68186e | 31436f12-35af-4702-a006-8e43c19ca6c8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 689432 | 2025-07-30 07:03:54 AEST | 2025-07-30 13:38:51 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ced6701c-5475-4d64-b201-b97bf1ecf2db | 31436f12-35af-4702-a006-8e43c19ca6c8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 714283 | 2025-07-30 07:03:52 AEST | 2025-07-30 13:38:51 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c9c8dc7d-7a6e-4907-8d70-12764e3d7d99 | 699226d9-b0e9-4918-a4a9-931eb3c4829c | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 714144 | 2025-07-30 07:03:50 AEST | 2025-07-30 13:36:55 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
b4ed148a-1497-40b4-b5e0-9401792fde60 | 699226d9-b0e9-4918-a4a9-931eb3c4829c | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 785751 | 2025-07-30 07:03:48 AEST | 2025-07-30 13:36:55 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
96a1226e-b339-4ae4-b1fb-d50f79da17bd | da6c09dc-7814-4644-aea6-f0a624552c0b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 597623 | 2025-07-29 19:25:28 AEST | 2025-07-29 06:30:25 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
286b394e-adfe-4376-8961-0637aa4401e2 | da6c09dc-7814-4644-aea6-f0a624552c0b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 606215 | 2025-07-29 19:25:30 AEST | 2025-07-29 06:30:25 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
42230faa-69ae-49bc-84d7-cbfec0d17830 | da6c09dc-7814-4644-aea6-f0a624552c0b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 493558 | 2025-07-29 19:25:35 AEST | 2025-07-29 06:30:25 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9e4abf42-ea23-414b-b5e3-f22b8a116da3 | a57a38d6-3e6f-4cc5-8356-a765bbfdb4d3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 341981 | 2025-07-25 19:57:37 AEST | 2025-07-26 03:15:23 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
9842bc5b-4824-4838-a49b-a499663f1a86 | a57a38d6-3e6f-4cc5-8356-a765bbfdb4d3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 298216 | 2025-07-25 19:57:41 AEST | 2025-07-26 03:15:57 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
09335eb5-f45a-4cd9-ab5e-499bf507eedf | 489cad8c-79bc-43a0-a8bb-f0465123a8ac | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 503959 | 2025-07-30 07:03:56 AEST | 2025-07-30 13:42:11 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
cff9977b-de5c-460c-a6f5-7979cc63cc9c | 489cad8c-79bc-43a0-a8bb-f0465123a8ac | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 623712 | 2025-07-30 07:03:58 AEST | 2025-07-30 13:42:11 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
b14ff9a1-9399-41b0-a28e-2f761c15bf91 | eea2f38e-1b46-4723-9e4f-06d484c110d5 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 669077 | 2025-07-29 19:25:26 AEST | 2025-07-29 06:28:08 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3b0e9f21-634d-4efc-9005-ca7eef06b114 | eea2f38e-1b46-4723-9e4f-06d484c110d5 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 451365 | 2025-07-29 19:25:24 AEST | 2025-07-29 06:28:08 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
188a1943-0138-41e5-9d48-9ac06fcad0c7 | 24427f18-17f9-4a42-8dc6-52d5ad88c70e | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 570050 | 2025-07-26 09:03:56 AEST | 2025-07-26 07:48:51 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c0efe520-1ba8-426e-803c-fb39524e81de | 24427f18-17f9-4a42-8dc6-52d5ad88c70e | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 566772 | 2025-07-26 09:03:58 AEST | 2025-07-26 07:48:51 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6f19513a-f1c8-42d0-bbfa-9d2d044f826c | 24427f18-17f9-4a42-8dc6-52d5ad88c70e | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 571937 | 2025-07-26 06:49:21 AEST | 2025-07-26 11:53:57 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
56fd2193-7cd9-4ba3-bed5-b9932714316a | 24427f18-17f9-4a42-8dc6-52d5ad88c70e | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 682680 | 2025-07-26 06:49:25 AEST | 2025-07-26 11:53:57 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
f681c0c1-c176-4d60-9b88-793fb4f74707 | ca634e3a-b151-4ae0-ae8a-96bc2204c01b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 557797 | 2025-07-26 09:04:03 AEST | 2025-07-26 07:54:14 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
320dc32d-dd2a-49db-9418-3ecb7f478f67 | ca634e3a-b151-4ae0-ae8a-96bc2204c01b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 605424 | 2025-07-26 09:04:00 AEST | 2025-07-26 07:54:14 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2ca8b5e1-3862-44ce-a753-168a9d1afed4 | ca634e3a-b151-4ae0-ae8a-96bc2204c01b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 638206 | 2025-07-26 06:49:29 AEST | 2025-07-26 12:00:22 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
3df17178-3975-4101-adb9-cc0f55aee2d2 | 33a85c96-52b5-4813-ae6e-a7bd1f160262 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 607990 | 2025-07-26 09:04:08 AEST | 2025-07-26 07:58:56 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5fef17d9-87ed-45b8-8b06-1b0aa56ea4b0 | 33a85c96-52b5-4813-ae6e-a7bd1f160262 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 590089 | 2025-07-26 09:04:06 AEST | 2025-07-26 07:58:56 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f7a65051-dfaf-44b8-9b78-e93035c71df5 | 33a85c96-52b5-4813-ae6e-a7bd1f160262 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 735453 | 2025-07-26 06:49:31 AEST | 2025-07-26 12:03:19 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
32114db7-1894-46f1-b332-8de9f1189dd8 | 33a85c96-52b5-4813-ae6e-a7bd1f160262 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 722900 | 2025-07-26 06:49:47 AEST | 2025-07-26 12:03:41 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
1c16af19-e8de-427d-b719-2e18e74592c5 | c0e1f8ef-5d7d-4593-b963-4a67438bc76b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 576895 | 2025-07-26 09:04:12 AEST | 2025-07-26 08:02:09 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a90d19aa-2f70-4c13-a69f-daecac57f197 | c0e1f8ef-5d7d-4593-b963-4a67438bc76b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 675496 | 2025-07-26 09:04:14 AEST | 2025-07-26 08:02:09 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f5c30318-bc78-4911-92b5-6b2799066bcc | c0e1f8ef-5d7d-4593-b963-4a67438bc76b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 539035 | 2025-07-26 06:49:54 AEST | 2025-07-26 12:12:22 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
80b346e7-13fd-45f1-ac0e-2752bf5a143b | c0e1f8ef-5d7d-4593-b963-4a67438bc76b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 603125 | 2025-07-26 06:49:50 AEST | 2025-07-26 12:12:22 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
e1a4d9ae-cbfc-4cb2-990d-57f8e3f3457a | f0c22191-2d91-455f-8615-987529213fe8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 393631 | 2025-07-26 09:04:51 AEST | 2025-07-26 09:08:42 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
16a77e9b-11a1-4429-8a49-39f92d469cd0 | f0c22191-2d91-455f-8615-987529213fe8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 408172 | 2025-07-26 09:04:52 AEST | 2025-07-26 09:08:42 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6bca8f70-1642-4da1-94d3-3f878de52b64 | 8927c9f5-4823-4295-8a0c-8771414689b8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 479365 | 2025-07-26 09:04:20 AEST | 2025-07-26 08:05:10 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c00f0636-d1bf-47ac-9e51-13d0ce897db4 | 8927c9f5-4823-4295-8a0c-8771414689b8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 444444 | 2025-07-26 09:04:16 AEST | 2025-07-26 08:05:10 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e9160bca-e8c4-4002-9f7b-5c1b8fccf454 | 8927c9f5-4823-4295-8a0c-8771414689b8 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 440479 | 2025-07-26 09:04:18 AEST | 2025-07-26 08:05:10 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d91677f0-c9f2-4352-87c7-ddf317fff271 | af41be2b-f4a9-4abd-ad6d-d8f78093ee04 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 527154 | 2025-07-26 09:04:56 AEST | 2025-07-26 09:11:17 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cdea7df3-064a-4e14-9665-6412460261c3 | af41be2b-f4a9-4abd-ad6d-d8f78093ee04 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 525460 | 2025-07-26 09:04:54 AEST | 2025-07-26 09:11:17 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ad10839b-344c-44a1-9b21-2961ef7c4345 | 5a44871e-7e77-4166-87ad-fb0b7ca1923d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 454976 | 2025-07-26 09:04:22 AEST | 2025-07-26 08:11:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f5d9bf49-2bbd-43bc-9373-99fa2c9cd726 | 5a44871e-7e77-4166-87ad-fb0b7ca1923d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 507423 | 2025-07-26 09:04:35 AEST | 2025-07-26 08:11:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
29be8e5e-49bd-4878-8a2c-ea2536d2ce4a | f52a8d49-51e7-4a19-9a90-bc3f1e2252bd | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 596497 | 2025-07-26 09:04:37 AEST | 2025-07-26 08:15:40 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
46e3e8ad-aabc-4f06-905f-5dd779ccb546 | f52a8d49-51e7-4a19-9a90-bc3f1e2252bd | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 578051 | 2025-07-26 09:04:39 AEST | 2025-07-26 08:15:40 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4903ae76-d063-43f7-8665-c7638f042673 | f52a8d49-51e7-4a19-9a90-bc3f1e2252bd | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 670522 | 2025-07-26 06:50:21 AEST | 2025-07-26 12:23:17 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
d146af81-4eae-481d-8c84-8922de3f4d42 | 78c61d64-7372-45ce-93f8-c1ce4c00a996 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 474493 | 2025-07-26 09:05:00 AEST | 2025-07-26 09:20:01 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
50e0b899-f296-417b-ba3f-2170052d5793 | 78c61d64-7372-45ce-93f8-c1ce4c00a996 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 434569 | 2025-07-26 09:04:58 AEST | 2025-07-26 09:20:01 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7ebf3e5b-3ddd-475d-8080-88bbe5bf37f3 | 44faeedd-988f-431e-84a5-834740232a2b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 769869 | 2025-07-26 06:50:26 AEST | 2025-07-26 12:29:43 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
83c81869-6bfc-42a0-8af0-56049e86d0bf | 44faeedd-988f-431e-84a5-834740232a2b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 730465 | 2025-07-26 06:50:34 AEST | 2025-07-26 12:29:43 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
26e1be60-6e81-4ead-83ed-be1fe40bc85d | 44faeedd-988f-431e-84a5-834740232a2b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 711976 | 2025-07-26 06:50:42 AEST | 2025-07-26 12:29:43 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
5fd99501-125a-4df0-8494-65104b34b3f6 | 44faeedd-988f-431e-84a5-834740232a2b | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 594725 | 2025-07-26 06:50:30 AEST | 2025-07-26 12:29:43 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
decb5df6-d2e0-4560-91ca-a438fb60d09c | 6a1704d0-cfaa-451b-bd15-1637ceae1191 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 483737 | 2025-07-26 09:05:04 AEST | 2025-07-26 09:29:44 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
febf67f9-7d91-49af-88a1-85e5da71e6e1 | 6a1704d0-cfaa-451b-bd15-1637ceae1191 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 483843 | 2025-07-26 09:05:02 AEST | 2025-07-26 09:29:44 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
18e56def-acea-489d-a835-f17ae2e55434 | 5a5b1b2a-b545-4e71-af0a-9923f39ec536 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 478736 | 2025-07-26 09:05:05 AEST | 2025-07-26 09:31:35 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
de45e1b8-21ad-4a41-a550-8cef8ed7bb08 | 5a5b1b2a-b545-4e71-af0a-9923f39ec536 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 455127 | 2025-07-26 09:05:07 AEST | 2025-07-26 09:31:35 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
60f8347a-83fb-4464-941d-2bd7deaf2795 | 9af9d80f-7446-4648-bce1-4d200be41d0d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3181 | 118.5773 | POINT (118.577325 -20.318105555555555) | 220003 | 2025-07-25 19:54:15 AEST | 2025-07-26 02:20:57 AEST | 5.6594 | 2025-07-25 | 08:05:25 | 66.5279 |  |  | -20.3181 | S | 118.5773 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
924f8d13-2f65-4961-937f-859b3cd5c2b7 | 9af9d80f-7446-4648-bce1-4d200be41d0d | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3181 | 118.5773 | POINT (118.577325 -20.318105555555555) | 288916 | 2025-07-25 19:54:12 AEST | 2025-07-26 02:21:18 AEST | 5.6594 | 2025-07-25 | 08:05:25 | 66.5279 |  |  | -20.3181 | S | 118.5773 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
eb348c84-346c-4b05-9585-17489195f91d | 6fc252c2-d129-44da-b6d4-6a67f25555e6 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3181 | 118.5773 | POINT (118.577325 -20.318105555555555) | 276895 | 2025-07-25 19:54:10 AEST | 2025-07-26 02:27:32 AEST | 5.6594 | 2025-07-25 | 08:05:25 | 66.5279 |  |  | -20.3181 | S | 118.5773 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
af775046-148a-4e95-89f1-61d9a07b50a1 | 6fc252c2-d129-44da-b6d4-6a67f25555e6 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3181 | 118.5773 | POINT (118.577325 -20.318105555555555) | 310380 | 2025-07-25 19:54:07 AEST | 2025-07-26 02:28:40 AEST | 5.6594 | 2025-07-25 | 08:05:25 | 66.5279 |  |  | -20.3181 | S | 118.5773 | E | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
a71ffa0c-989b-4c00-8226-7ad59bd7b496 | cbb4a87b-472c-47f1-bbdc-8699d34520f1 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3181 | 118.5773 | POINT (118.577325 -20.318105555555555) | 225717 | 2025-07-25 19:54:02 AEST | 2025-07-26 02:34:43 AEST | 5.6594 | 2025-07-25 | 08:05:25 | 66.5279 |  |  | -20.3181 | S | 118.5773 | E | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
2c020c18-db49-4b79-aa96-c77da162e00d | cbb4a87b-472c-47f1-bbdc-8699d34520f1 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 243940 | 2025-07-25 19:53:42 AEST | 2025-07-26 02:44:58 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
fae18fac-d352-4df7-9e9c-aae7e5522c89 | 8c5e4be6-b68c-4dea-a91e-b389bd198d6f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 244277 | 2025-07-25 19:53:39 AEST | 2025-07-26 02:54:05 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
f170f0af-5fd1-43b8-9665-32f945c0af88 | 8c5e4be6-b68c-4dea-a91e-b389bd198d6f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 336475 | 2025-07-25 19:53:36 AEST | 2025-07-26 02:54:15 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
87acaa45-4f8e-4882-bbe6-9ce61dc7ca13 | 3ad2a319-8f64-4798-b3e7-06278d5f7433 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 280092 | 2025-07-25 19:53:33 AEST | 2025-07-26 03:03:00 AEST | [10 empty] | Apple | iPhone 13 mini | BottomRight | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
b16279e0-99ab-45fe-b1d3-265037fbdf81 | 3ad2a319-8f64-4798-b3e7-06278d5f7433 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 649411 | 2025-07-31 03:48:13 AEST | 2025-07-31 09:33:11 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
607d8af8-14a6-47f6-8add-74e8c901ad80 | 3ad2a319-8f64-4798-b3e7-06278d5f7433 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 671412 | 2025-07-31 03:48:10 AEST | 2025-07-31 09:33:11 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
3a35f9e4-66ac-4d7e-832f-99f267af8e6a | aa616cca-d466-4197-ab7c-49c7a60d73e2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 407267 | 2025-07-25 19:53:26 AEST | 2025-07-26 03:17:27 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
96843638-0d29-42d1-9843-fdfe98f8eb9d | aa616cca-d466-4197-ab7c-49c7a60d73e2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 322409 | 2025-07-25 19:53:22 AEST | 2025-07-26 03:17:32 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
3977261f-cda5-4193-a4f6-8b07b00a4841 | aa616cca-d466-4197-ab7c-49c7a60d73e2 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 411183 | 2025-07-25 19:53:18 AEST | 2025-07-26 03:17:37 AEST | [10 empty] | Apple | iPhone 13 mini | TopLeft | 1080 | 810 | Fulcrum iOS 2507.1.1 (12327), iOS 18.5, Apple, iPhone 13 Mini | 72 | 72
5a254668-cb28-44ae-9ada-4160c751e681 | f3a25cb3-b411-47d3-95bf-b3c1d990703f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 728808 | 2025-07-26 06:49:58 AEST | 2025-07-26 12:18:04 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
33060705-d613-4ab3-910c-d130dd512b88 | f3a25cb3-b411-47d3-95bf-b3c1d990703f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 725810 | 2025-07-26 06:50:10 AEST | 2025-07-26 12:18:04 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
79e0bf4c-6632-4dfd-a5b2-d0d67bcc3b81 | f3a25cb3-b411-47d3-95bf-b3c1d990703f | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 567287 | 2025-07-26 06:50:16 AEST | 2025-07-26 12:19:30 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
36288dca-680d-4722-9613-123cd7a9efb8 | b0a974c3-0c88-4ed5-800f-f307b3df2a88 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 507341 | 2025-07-26 06:50:46 AEST | 2025-07-26 12:36:08 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
8d0d82e4-dbde-427b-9ee5-93da8ec06eb9 | b0a974c3-0c88-4ed5-800f-f307b3df2a88 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 566682 | 2025-07-26 06:51:05 AEST | 2025-07-26 12:36:08 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
bc534b78-b1e1-4a8b-a779-166f671b634c | b0a974c3-0c88-4ed5-800f-f307b3df2a88 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 511858 | 2025-07-26 06:51:00 AEST | 2025-07-26 12:36:08 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
48589e84-17bc-445a-8ed1-5763e7c83125 | b0ed1bcd-6a29-4105-a8eb-3835574708d3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 414404 | 2025-07-27 21:29:44 AEST | 2025-07-28 01:28:06 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
89054f45-b3dc-4646-b833-ffcd8c6dce03 | b0ed1bcd-6a29-4105-a8eb-3835574708d3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 475747 | 2025-07-27 21:29:42 AEST | 2025-07-28 01:28:16 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7f44bcf4-b273-4f9e-90a5-ba67b546c846 | b0ed1bcd-6a29-4105-a8eb-3835574708d3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 444436 | 2025-07-27 21:29:39 AEST | 2025-07-28 01:28:35 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
313a19aa-397a-4490-a0b0-917f637cd3d1 | b0ed1bcd-6a29-4105-a8eb-3835574708d3 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 434155 | 2025-07-27 21:29:36 AEST | 2025-07-28 01:28:42 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
27582b24-a06c-4df6-aaec-33bf94ccbe6b | 15c91b3d-cc04-4f83-a711-fc7326ffa96a | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 524622 | 2025-07-27 21:29:33 AEST | 2025-07-28 01:40:25 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
b9163fca-9d43-4c6c-adb5-910a02de5e55 | 15c91b3d-cc04-4f83-a711-fc7326ffa96a | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 523591 | 2025-07-27 21:29:30 AEST | 2025-07-28 01:40:29 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
02e2fe34-791f-40de-9abb-dd1f5f5b1347 | 15c91b3d-cc04-4f83-a711-fc7326ffa96a | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 577085 | 2025-07-27 21:29:28 AEST | 2025-07-28 01:40:40 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
a462c2f2-5b4c-4e0f-9307-90f81f8e4b9d | 15c91b3d-cc04-4f83-a711-fc7326ffa96a | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 474234 | 2025-07-27 21:29:25 AEST | 2025-07-28 01:41:17 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
536d71aa-01e4-4d7e-8087-b21798c5fe98 | 15c91b3d-cc04-4f83-a711-fc7326ffa96a | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 547740 | 2025-07-27 21:29:22 AEST | 2025-07-28 01:41:24 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
9fd81ded-41f6-4d60-88af-06407e08fbc7 | 8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 365366 | 2025-07-27 21:29:19 AEST | 2025-07-28 01:55:02 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
242d19ec-108b-4df4-8d67-b67d93a06b5e | 8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 353365 | 2025-07-27 21:29:16 AEST | 2025-07-28 01:55:09 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
0a12d4b1-13e5-4c5b-858f-a1eb910e8897 | 8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 577147 | 2025-07-27 21:29:13 AEST | 2025-07-28 01:55:37 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
482317cd-9ef3-4c76-947c-a5ada5db4879 | 8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 378165 | 2025-07-27 21:29:10 AEST | 2025-07-28 01:55:51 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
47255840-e77d-4cca-bf3c-d21e6877862d | 8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 375953 | 2025-07-27 21:29:07 AEST | 2025-07-28 01:56:04 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
7c5ac1e1-e10a-423b-950c-389f6e3022d7 | 8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 464244 | 2025-07-27 21:29:05 AEST | 2025-07-28 01:56:28 AEST | [10 empty] | Apple | iPhone 15 Pro Max | BottomRight | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
4140eecb-e554-44be-be64-e77e4572c51e | 8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 493856 | 2025-07-27 21:29:02 AEST | 2025-07-28 01:56:41 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
197fd34b-94b2-474f-92e4-0e97901c2130 | 8a5f5c3d-3279-4210-a57d-dec09baf9d18 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 422931 | 2025-07-27 21:28:59 AEST | 2025-07-28 01:56:50 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
b2078654-eff4-4c23-b4a0-8bee5b58a6fd | 2eb72ddf-1e7a-41a8-87c4-2b4ce4c17023 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 351770 | 2025-07-27 21:28:56 AEST | 2025-07-28 02:09:37 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5cbc1470-cf81-4172-ae8e-aea56089ec7b | 2eb72ddf-1e7a-41a8-87c4-2b4ce4c17023 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 382279 | 2025-07-27 21:28:53 AEST | 2025-07-28 02:09:43 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
9aef9aa4-dac6-42ff-8599-c88b596c7e6d | 2eb72ddf-1e7a-41a8-87c4-2b4ce4c17023 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 348849 | 2025-07-27 21:28:50 AEST | 2025-07-28 02:09:51 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
b101022a-228f-476d-b3e1-09c000445053 | 2eb72ddf-1e7a-41a8-87c4-2b4ce4c17023 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 288660 | 2025-07-27 21:28:48 AEST | 2025-07-28 02:09:58 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
e5b44645-43dd-44f6-a2a0-4caf78009f1d | 2eb72ddf-1e7a-41a8-87c4-2b4ce4c17023 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 484252 | 2025-07-27 21:28:45 AEST | 2025-07-28 02:10:12 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
f524da60-b1b9-4ba3-8503-16f608e99eaf | 2eb72ddf-1e7a-41a8-87c4-2b4ce4c17023 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 438161 | 2025-07-27 21:28:42 AEST | 2025-07-28 02:10:28 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
468c9287-5f19-4f4f-a753-19ddd5886261 | 2eb72ddf-1e7a-41a8-87c4-2b4ce4c17023 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 427526 | 2025-07-27 21:28:39 AEST | 2025-07-28 02:10:33 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
653ccb87-b1e6-4f31-bd18-02d14b22ee3c | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 435825 | 2025-07-27 21:28:37 AEST | 2025-07-28 02:26:55 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
8eb42811-e70d-4a7e-bac8-ed03656a87b9 | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 395774 | 2025-07-27 21:28:34 AEST | 2025-07-28 02:27:09 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
a30c3873-731d-4e67-8a5b-b90cfc5edaae | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 453416 | 2025-07-27 21:28:31 AEST | 2025-07-28 02:27:13 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
e8beef56-28bc-44e6-8838-d11688e54afe | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 430083 | 2025-07-27 21:28:29 AEST | 2025-07-28 02:27:18 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
60ef6a0d-c41f-4561-a0d7-99124e996421 | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 438417 | 2025-07-27 21:28:26 AEST | 2025-07-28 02:27:34 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
5cfb6008-84d5-42aa-ab7f-32a7773563ca | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 648844 | 2025-07-27 21:28:20 AEST | 2025-07-28 02:27:56 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
bb8ad476-2d21-415a-8910-26533b49f01f | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 456337 | 2025-07-27 21:28:17 AEST | 2025-07-28 02:28:12 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
ac61be30-0f9f-4b87-8de9-4a6563f69620 | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 373584 | 2025-07-27 21:28:14 AEST | 2025-07-28 02:28:18 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
6c2d0af1-98ea-439b-a0d6-555758a0477e | b43a8ede-4737-4005-8445-8bf145e53745 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 545345 | 2025-07-27 21:28:12 AEST | 2025-07-28 02:28:27 AEST | [10 empty] | Apple | iPhone 15 Pro Max | TopLeft | 1080 | 810 | Fulcrum iOS 2507.0.0 (12324), iOS 18.5, Apple, iPhone 15 Pro Max | 72 | 72
eceb3dac-54d5-445e-9a84-4f3e0c495349 | d071eaac-c3b4-4760-b9fe-d30a62169fd7 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 506606 | 2025-07-31 03:48:17 AEST | 2025-07-31 09:40:58 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
82ebea5e-3e29-46d2-9ccb-85c66057c571 | d071eaac-c3b4-4760-b9fe-d30a62169fd7 | 53c90c8e-d66b-4c57-ad37-dc9e9557e549 | 1 |  | -20.3212 | 118.5712 | POINT (118.57122629999904 -20.321226499999998) | 572574 | 2025-07-31 03:48:19 AEST | 2025-07-31 09:40:58 AEST |  |  |  | 2700 |  |  | -20.3212 | S | 118.5712 | E | samsung | SM-S931B |  | 810 | 1080 | Fulcrum Android 2507.2.0 (19260), Android 15, samsung, SM-S931B
c97e762f-685d-45e0-bcaa-70dab5511709 | a338411d-8ae9-455f-bdae-92df22461a07 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 605932 | 2025-07-26 09:05:56 AEST | 2025-07-26 12:09:44 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9c856b51-2ee4-459a-b732-1372b4361ab9 | a338411d-8ae9-455f-bdae-92df22461a07 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 493041 | 2025-07-26 09:05:54 AEST | 2025-07-26 12:09:44 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cb5fee15-5645-4fa6-994f-68c60a747aae | a338411d-8ae9-455f-bdae-92df22461a07 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 649464 | 2025-07-26 06:51:08 AEST | 2025-07-26 12:48:30 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
8497055c-d2da-42cb-87cd-be19caca0efb | d214fb78-1147-4156-880b-c11a6cfa6215 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 442871 | 2025-07-26 09:05:11 AEST | 2025-07-26 09:37:31 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
59e94bd5-ab11-4998-b3bd-4c6b242bfe86 | d214fb78-1147-4156-880b-c11a6cfa6215 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 440050 | 2025-07-26 09:05:09 AEST | 2025-07-26 09:37:31 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1b577c59-9e2d-4a79-877d-7597dcda63ac | 27d6a4c5-36e7-4308-a89f-d330fc865ca5 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 622941 | 2025-07-26 06:51:10 AEST | 2025-07-26 12:59:43 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
773bfe7f-96f8-44cf-9401-120d60bea85e | 27d6a4c5-36e7-4308-a89f-d330fc865ca5 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 536835 | 2025-07-26 06:51:12 AEST | 2025-07-26 12:59:43 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c5d957e4-560e-4b82-b943-bfb8dc7f5a34 | 270472c6-7e0a-4275-848f-0d773e3535eb | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 465845 | 2025-07-26 09:04:41 AEST | 2025-07-26 08:40:13 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c6ea20b7-8fa8-4013-9f47-80201dc96398 | 270472c6-7e0a-4275-848f-0d773e3535eb | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 499174 | 2025-07-26 09:04:43 AEST | 2025-07-26 08:40:13 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
16d0fb60-2015-4840-ac13-0577403f5613 | 7cb9cfa1-954a-411b-9e3c-fca334c82d0f | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 519217 | 2025-07-26 09:04:49 AEST | 2025-07-26 08:44:05 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
fa5594a0-665d-4590-80fc-1be1e789e72e | 7cb9cfa1-954a-411b-9e3c-fca334c82d0f | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 505612 | 2025-07-26 09:04:45 AEST | 2025-07-26 08:44:05 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
afcd54e6-9a78-4eea-a11d-8bdd919d58f6 | 1f80372c-75cd-493c-a4e9-b7cca5546697 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 436002 | 2025-07-26 09:05:15 AEST | 2025-07-26 09:44:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
536721a4-e5c5-4f32-a3e8-4b6e55e94c39 | 1f80372c-75cd-493c-a4e9-b7cca5546697 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3161 | 118.5847 | POINT (118.58472222222221 -20.316123) | 484795 | 2025-07-26 09:05:13 AEST | 2025-07-26 09:44:49 AEST |  |  |  | 1900 |  |  | -20.3161 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
beb95b15-3ec1-4d96-bd89-15aa27fafe92 | 81a93a60-d465-46ab-a3b9-c5f99e32dad3 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 693859 | 2025-07-26 06:51:17 AEST | 2025-07-26 13:13:16 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
4f11066d-2757-4186-9103-01da55289861 | 81a93a60-d465-46ab-a3b9-c5f99e32dad3 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 679781 | 2025-07-26 06:51:15 AEST | 2025-07-26 13:13:16 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
e6d9322a-c28c-4289-b022-0bd362bb9ded | 017f40ad-59c8-4a10-a358-6c86d87960b9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 650867 | 2025-07-29 19:25:16 AEST | 2025-07-29 06:21:24 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
58025fff-b9ca-4f95-9fa6-14f9fb9fd53f | 017f40ad-59c8-4a10-a358-6c86d87960b9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 652095 | 2025-07-29 19:25:20 AEST | 2025-07-29 06:21:24 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
43380d83-68ac-45ce-a08a-71350fd71beb | 017f40ad-59c8-4a10-a358-6c86d87960b9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3188 | 118.5865 | POINT (118.58654569999733 -20.318847599999998) | 552289 | 2025-07-29 19:25:22 AEST | 2025-07-29 06:21:24 AEST |  |  |  | 2000 |  |  | -20.3188 | S | 118.5865 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d2bd7954-2d90-4b26-87a6-aad6acbf06ab | c512451e-e937-47f3-8d22-6261806679f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 652892 | 2025-07-26 09:06:29 AEST | 2025-07-26 13:03:54 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a49af9e4-1a0d-42aa-93b3-0c8d011bd949 | c512451e-e937-47f3-8d22-6261806679f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 629917 | 2025-07-26 09:06:27 AEST | 2025-07-26 13:03:54 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ac85b826-77e8-442c-b808-da200144c2c3 | c512451e-e937-47f3-8d22-6261806679f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 742107 | 2025-07-26 06:51:20 AEST | 2025-07-26 13:16:17 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
e3a4c912-9057-4b72-b931-dd127eaa5ffc | c512451e-e937-47f3-8d22-6261806679f9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 804266 | 2025-07-26 06:51:23 AEST | 2025-07-26 13:16:17 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7123f25f-c6ea-470a-9e19-6275d4e2c72c | 02f780c9-d25b-4d9d-a11e-0cc2b16db819 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 456340 | 2025-07-26 09:06:31 AEST | 2025-07-26 13:09:30 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c0c85201-b328-47ce-b77c-72205eb22568 | 02f780c9-d25b-4d9d-a11e-0cc2b16db819 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 511798 | 2025-07-26 09:06:33 AEST | 2025-07-26 13:09:30 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b6a91509-36c1-4840-bd88-e72fc7ba74eb | 02f780c9-d25b-4d9d-a11e-0cc2b16db819 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3741 | 118.634 | POINT (118.633954 -20.3740844) | 625662 | 2025-07-28 06:23:32 AEST | 2025-07-28 10:05:44 AEST |  |  |  | 2200 |  |  | -20.3741 | S | 118.634 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
faeb5ce7-e710-41c4-b1c2-b8b2f9a60dc1 | 02f780c9-d25b-4d9d-a11e-0cc2b16db819 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3741 | 118.634 | POINT (118.633954 -20.3740844) | 584544 | 2025-07-28 06:23:35 AEST | 2025-07-28 10:05:44 AEST |  |  |  | 2200 |  |  | -20.3741 | S | 118.634 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7d8ed08f-fde6-4d6f-818f-ccb97f2db5de | d9a82046-dcd7-4e70-a70e-996d1b093e3c | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 589007 | 2025-07-26 09:06:37 AEST | 2025-07-26 13:15:15 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a9692007-05e3-4f26-8978-31cad190fe8c | d9a82046-dcd7-4e70-a70e-996d1b093e3c | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 575200 | 2025-07-26 09:06:35 AEST | 2025-07-26 13:15:15 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
92fa0871-8f87-455b-8a5d-9706311187d7 | d9a82046-dcd7-4e70-a70e-996d1b093e3c | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 709958 | 2025-07-26 06:51:36 AEST | 2025-07-26 13:20:40 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
36a42707-f68f-4b6d-9e32-27d5674d354d | d9a82046-dcd7-4e70-a70e-996d1b093e3c | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 748636 | 2025-07-26 06:51:40 AEST | 2025-07-26 13:20:55 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
0cfd2133-f9f7-4b17-bef7-260d06932062 | cc778594-9985-441e-810e-283d8d080f26 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 513885 | 2025-07-26 09:06:41 AEST | 2025-07-26 13:17:08 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d0521566-6155-472f-9506-807c5b6f7c5f | cc778594-9985-441e-810e-283d8d080f26 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 558524 | 2025-07-26 09:06:39 AEST | 2025-07-26 13:17:08 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cdcbde5b-85cc-4791-a47e-5e5075955e34 | 0e199566-4862-4afc-a285-8a34c659352b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 566126 | 2025-07-26 09:06:45 AEST | 2025-07-26 13:19:52 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
101173bb-fe61-4ace-819f-3c95abd5eabc | 0e199566-4862-4afc-a285-8a34c659352b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 526464 | 2025-07-26 09:06:43 AEST | 2025-07-26 13:19:52 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b7a4d2de-f1cb-47fa-8702-6e8ca841b6e7 | 34ee6bef-3510-4e27-bc83-3fc80bc6a2d6 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 568866 | 2025-07-26 09:06:47 AEST | 2025-07-26 13:22:41 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
15852746-fd6d-42cd-a210-050b22a5734d | 34ee6bef-3510-4e27-bc83-3fc80bc6a2d6 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 568258 | 2025-07-26 09:06:49 AEST | 2025-07-26 13:22:41 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d6d4d991-8359-49be-b5f7-52567f38c954 | 2410be29-0702-4415-9daf-910f04ce85ff | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 598055 | 2025-07-26 09:06:55 AEST | 2025-07-26 13:28:39 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
52c48b67-1c32-40e6-b814-63d4170db06b | 2410be29-0702-4415-9daf-910f04ce85ff | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 422908 | 2025-07-26 09:06:51 AEST | 2025-07-26 13:28:39 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
be9ed26a-b125-47fd-a1a2-abf36bbea5d7 | 2410be29-0702-4415-9daf-910f04ce85ff | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 596406 | 2025-07-26 09:06:53 AEST | 2025-07-26 13:28:39 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6d8a9eb2-bfa6-4714-8dc6-5b43ab0140b8 | 2410be29-0702-4415-9daf-910f04ce85ff | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 488614 | 2025-07-26 09:06:57 AEST | 2025-07-26 13:28:39 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
65e691be-5d55-4f10-b392-b0e4dc25e5c9 | a829edc5-3dcc-42be-8bba-b4105265a37c | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 689077 | 2025-07-26 06:51:43 AEST | 2025-07-26 13:28:55 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
97240d9e-338f-4ff0-9771-50d1e7bd751e | a829edc5-3dcc-42be-8bba-b4105265a37c | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 713130 | 2025-07-26 06:51:45 AEST | 2025-07-26 13:28:55 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ad77c5a3-d77d-4b83-980f-ec93bdf8fbf8 | 71edfa7e-2c02-491d-83ec-30c3f3213b15 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 619880 | 2025-07-26 06:51:53 AEST | 2025-07-26 13:31:36 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
b6887a25-2a28-4c0c-ac8c-49317c1f8240 | 6e8b5bec-98fc-4f46-a29c-c1719e333220 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 537106 | 2025-07-26 09:07:00 AEST | 2025-07-26 13:32:44 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2bd87b22-fc41-42be-a208-3cab029364ec | 6e8b5bec-98fc-4f46-a29c-c1719e333220 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 550961 | 2025-07-26 09:06:59 AEST | 2025-07-26 13:32:44 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0d19978e-e46c-47c6-bc51-f71512bf3813 | 3c2232eb-6d5b-4824-857b-57513c1f2c01 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 629593 | 2025-07-26 06:51:56 AEST | 2025-07-26 13:34:58 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
447a1181-e665-4672-8cef-b49f6f1470e1 | 2bc0340a-817a-4db4-98f0-8e0d7536e249 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 615401 | 2025-07-26 09:07:02 AEST | 2025-07-26 13:35:49 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
16e223d6-1f32-4be5-8fa0-88e60537830b | 2bc0340a-817a-4db4-98f0-8e0d7536e249 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 538271 | 2025-07-26 09:07:05 AEST | 2025-07-26 13:35:49 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
507c6e2e-76a2-4880-8700-e16aa7d9e378 | 2bc0340a-817a-4db4-98f0-8e0d7536e249 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 671282 | 2025-07-26 06:51:58 AEST | 2025-07-26 13:36:44 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
4611e8e7-9cc2-4349-9705-bdb13fd7b2ac | a9f1fb92-4ed9-4d18-ae32-8bffa4d69f27 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 563249 | 2025-07-26 09:07:09 AEST | 2025-07-26 13:38:26 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c1e075c0-37d1-4b34-9d00-f529551fde0d | a9f1fb92-4ed9-4d18-ae32-8bffa4d69f27 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 514340 | 2025-07-26 09:07:07 AEST | 2025-07-26 13:38:26 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f58108d5-946f-42b2-a57c-7ee2b951297d | 54501af9-0bda-4705-9d39-0ca6a8da45fb | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 473434 | 2025-07-27 07:15:11 AEST | 2025-07-27 10:40:54 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1722d5d3-396e-4f9d-8df3-a49c238a3132 | 54501af9-0bda-4705-9d39-0ca6a8da45fb | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 473331 | 2025-07-27 07:15:13 AEST | 2025-07-27 10:40:54 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
33b49317-ff2e-4eea-a409-4d794d427fe4 | 637d1053-41f7-4019-8d2c-e2098b9408c2 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 745426 | 2025-07-26 06:52:17 AEST | 2025-07-26 13:40:09 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
df40629d-4eef-4d7e-8f83-5093b232fa4c | 637d1053-41f7-4019-8d2c-e2098b9408c2 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 585895 | 2025-07-26 06:52:11 AEST | 2025-07-26 13:40:09 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
dd3631d5-2d8a-4029-8671-3c4b25e91cae | 637d1053-41f7-4019-8d2c-e2098b9408c2 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 618589 | 2025-07-26 06:52:33 AEST | 2025-07-26 13:40:09 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
0650f97b-4b20-4a51-9982-42df4f971b54 | 637d1053-41f7-4019-8d2c-e2098b9408c2 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 588147 | 2025-07-26 06:52:31 AEST | 2025-07-26 13:40:09 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
065e7610-d0cb-4879-82b6-f7ad1ac194ab | 637d1053-41f7-4019-8d2c-e2098b9408c2 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 578498 | 2025-07-26 06:52:27 AEST | 2025-07-26 13:40:09 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
ba7ccb1d-c6a8-4c87-b73b-131dfcabc1a2 | 5dfff68a-4a4b-4efa-9e74-488bb68cac10 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 520106 | 2025-07-26 06:52:41 AEST | 2025-07-26 13:44:15 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
170ca34b-5245-4250-9699-f54ed7b169ee | 5dfff68a-4a4b-4efa-9e74-488bb68cac10 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 554085 | 2025-07-26 06:52:38 AEST | 2025-07-26 13:44:15 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
deea7e52-ac80-4ff2-9523-2906d5ba6250 | 7e07a1cb-c3bf-41e7-9ff9-bb3992422a15 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 639472 | 2025-07-26 06:52:43 AEST | 2025-07-26 13:46:04 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
57ed5fc2-3c1f-4c41-9bd0-6b96b57f2fe0 | 7e07a1cb-c3bf-41e7-9ff9-bb3992422a15 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 719969 | 2025-07-26 06:53:18 AEST | 2025-07-26 13:46:04 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
849dc715-c163-4db3-b901-5b7816cdb713 | 7e07a1cb-c3bf-41e7-9ff9-bb3992422a15 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 642404 | 2025-07-26 06:53:05 AEST | 2025-07-26 13:46:04 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
540743f7-4fcd-4ff4-a9a5-b982af7ea4bd | 7e07a1cb-c3bf-41e7-9ff9-bb3992422a15 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 614109 | 2025-07-26 06:52:51 AEST | 2025-07-26 13:46:04 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
c12527bc-7d6c-4bd6-901c-89d415df2a89 | a5170fe8-62c6-4894-9b44-044af6967863 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 448895 | 2025-07-26 09:07:13 AEST | 2025-07-26 13:45:32 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e8332fc1-8a44-4347-bdb1-e36e0c72ef67 | a5170fe8-62c6-4894-9b44-044af6967863 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 479710 | 2025-07-26 09:07:11 AEST | 2025-07-26 13:45:32 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f06c80e3-5682-495f-a885-501cd811ac7d | a5170fe8-62c6-4894-9b44-044af6967863 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 585483 | 2025-07-27 07:15:15 AEST | 2025-07-27 10:42:01 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4aae738d-1c8d-4122-93e3-550d463f3cbb | d534a6c5-4f87-4707-86bc-dd77618644d4 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 620866 | 2025-07-26 09:07:17 AEST | 2025-07-26 13:48:14 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
4092a1a8-fb11-4986-9b7f-8e34f35ef8c0 | d534a6c5-4f87-4707-86bc-dd77618644d4 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 580576 | 2025-07-26 09:07:15 AEST | 2025-07-26 13:48:14 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
bde00f29-2e4c-44c3-8450-ec7d05dad9c1 | 39146f9b-283b-48ba-9de0-0b6a9435c55b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 686066 | 2025-07-26 06:53:24 AEST | 2025-07-26 13:48:01 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
19f46361-2f3e-4f06-bf9a-c9dde6678179 | 676f1d11-79a8-4b0b-97b5-24c841a5535f | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 694878 | 2025-07-26 06:53:31 AEST | 2025-07-26 13:49:25 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7f3f891f-f18b-44ce-bc84-6c56912e9e3e | 676f1d11-79a8-4b0b-97b5-24c841a5535f | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 713192 | 2025-07-26 06:53:36 AEST | 2025-07-26 13:49:25 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
869bb8f7-e3da-451f-98eb-d07ac38bb49d | c496cdd2-e787-4706-bd67-6a9cd7e49954 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 476172 | 2025-07-27 07:15:19 AEST | 2025-07-27 10:45:56 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e10b51ed-426a-4616-95be-3a0103f33b83 | c496cdd2-e787-4706-bd67-6a9cd7e49954 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 374071 | 2025-07-27 07:15:17 AEST | 2025-07-27 10:45:56 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3cd2bf35-51ee-4a8d-af3c-9e2020c9eb9b | 8e813717-e903-4ed6-92c6-b85bbe8cc8e3 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 441473 | 2025-07-27 07:15:21 AEST | 2025-07-27 10:48:07 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f0ec4ea3-a3af-4c7f-9d92-06d4ace9b11b | 8e813717-e903-4ed6-92c6-b85bbe8cc8e3 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 409845 | 2025-07-27 07:15:23 AEST | 2025-07-27 10:48:07 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5030fb7b-daf7-41c5-982d-577ac7055b01 | 0a73665d-593e-4226-afc9-3b3eee38aed6 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 480052 | 2025-07-26 09:07:21 AEST | 2025-07-26 13:51:59 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
64cfe7e4-5379-4279-bcd5-d50c32d21ff5 | 0a73665d-593e-4226-afc9-3b3eee38aed6 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 514712 | 2025-07-26 09:07:19 AEST | 2025-07-26 13:51:58 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
303feee8-3384-4161-8ce9-3a6b701ff700 | c80d8369-70ac-49f8-9c60-2772c49f3ecd | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 656281 | 2025-07-26 06:53:59 AEST | 2025-07-26 13:53:03 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
4a1345fa-7714-4654-b442-71132e1deac6 | c80d8369-70ac-49f8-9c60-2772c49f3ecd | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 763009 | 2025-07-26 06:53:42 AEST | 2025-07-26 13:53:03 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
112bdf38-b1ad-46e2-bfe8-3964f9c55cd5 | c80d8369-70ac-49f8-9c60-2772c49f3ecd | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 672497 | 2025-07-26 06:53:53 AEST | 2025-07-26 13:53:03 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
fe3ba384-173b-47fd-9f1f-fb3d4ae671b7 | c80d8369-70ac-49f8-9c60-2772c49f3ecd | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 666130 | 2025-07-26 06:54:09 AEST | 2025-07-26 13:53:03 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
693314bc-b972-49a9-a14f-b9d6cf3379b3 | 42ad8481-6272-4e83-b518-0eab2a097b0b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 552385 | 2025-07-26 09:07:24 AEST | 2025-07-26 13:55:22 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cec94885-ac64-48b3-bdc2-a862246bf692 | 42ad8481-6272-4e83-b518-0eab2a097b0b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 443392 | 2025-07-26 09:07:26 AEST | 2025-07-26 13:55:22 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
d4b2a2fc-8193-4955-a9c7-5177a0955d27 | 28d370c1-4b94-4780-b4c2-0e46f4cfca8e | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 524721 | 2025-07-26 09:07:29 AEST | 2025-07-26 14:01:01 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6f25b978-8fc8-4f17-98f3-e13bb4f99ca1 | 28d370c1-4b94-4780-b4c2-0e46f4cfca8e | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 584850 | 2025-07-26 09:07:27 AEST | 2025-07-26 14:01:01 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
074b61a9-05b7-4ae4-981b-1e6555586a99 | 28d370c1-4b94-4780-b4c2-0e46f4cfca8e | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 542125 | 2025-07-26 09:07:31 AEST | 2025-07-26 14:01:01 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
21bbfbca-fdfd-40f1-ab0c-561e80e55632 | 28d370c1-4b94-4780-b4c2-0e46f4cfca8e | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 452248 | 2025-07-26 09:07:35 AEST | 2025-07-26 14:01:01 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
81326ae9-7f4a-4a1c-8ef9-a1bbc61efa3e | 28d370c1-4b94-4780-b4c2-0e46f4cfca8e | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 453041 | 2025-07-26 09:07:33 AEST | 2025-07-26 14:01:01 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b452cfd1-2084-4290-b84d-3c1c766a2c37 | fd08c06f-b0bc-47c3-94bd-c149fb1c4d0b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 471773 | 2025-07-27 07:15:28 AEST | 2025-07-27 10:53:05 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
facfe9e3-381e-4d93-9874-e2b698d320c5 | fd08c06f-b0bc-47c3-94bd-c149fb1c4d0b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 385526 | 2025-07-27 07:15:29 AEST | 2025-07-27 10:53:05 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c794d209-5fcd-4eb2-a441-014c182133ae | 30eb7ba0-2b7d-4916-b731-b77a54cbbe83 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 569478 | 2025-07-26 06:54:33 AEST | 2025-07-26 13:55:51 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
fbf4df60-c511-4ef2-ad84-7a2c73cfa184 | 30eb7ba0-2b7d-4916-b731-b77a54cbbe83 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 651218 | 2025-07-26 06:54:30 AEST | 2025-07-26 13:55:51 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
1c419270-dbd2-4513-b74e-1d79ba80e66f | 58762854-9a31-47b5-baa3-99d2033bf602 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 598954 | 2025-07-26 09:07:39 AEST | 2025-07-26 14:04:33 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cb4c14ff-4d60-4321-afe9-8509c7e21fbe | 58762854-9a31-47b5-baa3-99d2033bf602 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 499006 | 2025-07-26 09:07:37 AEST | 2025-07-26 14:04:33 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
ce61fa83-0af5-4997-8f84-6614256905b3 | 58762854-9a31-47b5-baa3-99d2033bf602 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 614466 | 2025-07-26 06:54:42 AEST | 2025-07-26 13:57:44 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
8025d18d-b1a2-4c64-b4f5-73c42397b5a8 | 58762854-9a31-47b5-baa3-99d2033bf602 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 524263 | 2025-07-26 06:54:35 AEST | 2025-07-26 13:57:44 AEST | [10 empty] | samsung | SM-S901E |  | 810 | 1080 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
12bdd1bd-47c2-4348-ae38-075513ec3bce | ccf0dc4f-4bdf-4f1c-b476-22b7b7a9bb2b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 495350 | 2025-07-27 07:15:31 AEST | 2025-07-27 10:56:36 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7de52eb8-bcc5-457e-a646-9c582b3ecf7f | ccf0dc4f-4bdf-4f1c-b476-22b7b7a9bb2b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 470371 | 2025-07-27 07:15:33 AEST | 2025-07-27 10:56:36 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a7075f26-8e10-4bde-812b-d30d71631175 | ccf0dc4f-4bdf-4f1c-b476-22b7b7a9bb2b | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 413848 | 2025-07-27 07:15:35 AEST | 2025-07-27 10:56:36 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
8d4349e4-3d57-46e6-8ea1-60e6712a3d26 | 10de8c3f-3daa-437a-8545-e6b0fa0ae7e4 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 585381 | 2025-07-26 06:54:49 AEST | 2025-07-26 13:59:16 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
a6267e5d-ced0-4de0-ac8d-bda88b2eaa57 | 10de8c3f-3daa-437a-8545-e6b0fa0ae7e4 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 599461 | 2025-07-26 06:54:46 AEST | 2025-07-26 13:59:16 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
50834895-acfd-40d9-84cf-bd0e2867de9f | b013d6e6-a2d0-403c-b4b3-a244c5c20ce5 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 790028 | 2025-07-26 09:05:59 AEST | 2025-07-26 12:42:24 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b75116f2-62fd-4061-9fde-d63418a80516 | b013d6e6-a2d0-403c-b4b3-a244c5c20ce5 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 717373 | 2025-07-26 09:06:05 AEST | 2025-07-26 12:42:24 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
02dafcc6-ddd9-47e0-86b8-b00c661f50ac | b013d6e6-a2d0-403c-b4b3-a244c5c20ce5 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 717380 | 2025-07-26 09:06:03 AEST | 2025-07-26 12:42:24 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a5036ff8-6729-4ed8-835b-a6d60ae6a391 | b013d6e6-a2d0-403c-b4b3-a244c5c20ce5 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 700336 | 2025-07-26 09:06:01 AEST | 2025-07-26 12:42:24 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c0e92b4b-3ce1-44ef-91b9-6ee6902e11e3 | db2b23b8-7585-40cf-9a5f-1927849f9255 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 770940 | 2025-07-26 09:06:10 AEST | 2025-07-26 12:46:21 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
08894690-add4-4226-8dce-b98ff4ae73ea | db2b23b8-7585-40cf-9a5f-1927849f9255 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 723086 | 2025-07-26 09:06:08 AEST | 2025-07-26 12:46:21 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
29859e54-aa9f-488d-9e9a-0cf0941d614d | db2b23b8-7585-40cf-9a5f-1927849f9255 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 676339 | 2025-07-26 09:06:12 AEST | 2025-07-26 12:46:21 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5e5fdae3-3d2f-4a70-99d9-03b16392c876 | 8601ee5d-c41e-42f7-8007-3578a3b0f042 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 728145 | 2025-07-26 09:06:17 AEST | 2025-07-26 12:49:10 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cc97bb52-451b-47bb-8c22-bd808872e046 | 8601ee5d-c41e-42f7-8007-3578a3b0f042 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 655673 | 2025-07-26 09:06:14 AEST | 2025-07-26 12:49:10 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c85e52d7-fa1a-4ce9-abb1-03c07fee87a6 | 8601ee5d-c41e-42f7-8007-3578a3b0f042 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 586393 | 2025-07-26 09:06:19 AEST | 2025-07-26 12:49:10 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b6a8e03f-e757-48e6-8198-79c8e0fa9794 | 8698e62b-b6e8-4d41-aeaa-49aee47bcbd9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 635929 | 2025-07-26 09:06:25 AEST | 2025-07-26 12:52:43 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
3b745c30-2da7-44a4-bea0-88c25f46d59a | 8698e62b-b6e8-4d41-aeaa-49aee47bcbd9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 649669 | 2025-07-26 09:06:23 AEST | 2025-07-26 12:52:43 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
62031d99-4df1-4764-97da-81d0d9f2508c | 8698e62b-b6e8-4d41-aeaa-49aee47bcbd9 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3217 | 118.5853 | POINT (118.58533510000095 -20.32165110000129) | 629497 | 2025-07-26 09:06:21 AEST | 2025-07-26 12:52:43 AEST | 3.4659 |  |  | 4 |  |  | -20.3217 | S | 118.5853 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1f8630da-d067-4562-b214-ab92e7b475ff | 45e1a202-ec6c-4f96-9967-dc09739ecf52 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 465020 | 2025-07-27 07:15:26 AEST | 2025-07-27 10:50:02 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
52c51ba5-e515-4c11-9408-32c7968e75fd | 45e1a202-ec6c-4f96-9967-dc09739ecf52 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 399421 | 2025-07-27 07:15:24 AEST | 2025-07-27 10:50:02 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e6ac11b4-9bae-42a4-b90d-a111d05dc4c1 | 0435f395-9584-44d0-a212-edd1b71b71e7 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 590238 | 2025-07-30 03:27:47 AEST | 2025-07-30 10:36:02 AEST |  |  |  | 2000 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
386fba4e-1692-47b9-b489-d26b15d0ba35 | 0435f395-9584-44d0-a212-edd1b71b71e7 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 619784 | 2025-07-30 03:28:00 AEST | 2025-07-30 10:36:02 AEST |  |  |  | 2000 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2bf6226d-214f-4d35-b9a9-87df01ec42c3 | 0435f395-9584-44d0-a212-edd1b71b71e7 | 6728cd27-078c-421a-b1f4-1acfc77f71f9 | 1 |  | -20.3151 | 118.5847 | POINT (118.58472222222221 -20.315106900001354) | 622515 | 2025-07-30 03:27:36 AEST | 2025-07-30 10:36:02 AEST |  |  |  | 2000 |  |  | -20.3151 | S | 118.5847 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
50b297bb-d31b-45e0-92a2-6a7d80d5682a | b91d8619-2ffb-4c20-8809-e57d14e6cdc0 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 827155 | 2025-07-27 06:58:38 AEST | 2025-07-27 14:09:06 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
90111df9-724b-4108-962e-df788c7c32e6 | b91d8619-2ffb-4c20-8809-e57d14e6cdc0 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | 0 | 0 | POINT (0.0 0.0) | 767427 | 2025-07-27 06:58:40 AEST | 2025-07-27 14:09:06 AEST | [10 empty] | samsung | SM-S901E |  | 1080 | 810 | Fulcrum Android 2506.1.1 (18768), Android 15, samsung, SM-S901E
7f4001d3-77fe-4db1-ac41-5ddb55e0baa9 | 6f2fa6df-4ab9-4b9f-8aa1-724595d71659 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 575403 | 2025-07-27 07:15:01 AEST | 2025-07-27 10:22:50 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1b89e0a5-a70a-4798-bb38-a8a753db8ae7 | 6f2fa6df-4ab9-4b9f-8aa1-724595d71659 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 476832 | 2025-07-27 07:14:57 AEST | 2025-07-27 10:22:50 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
26abfb80-1fa1-4640-84e0-a9177a4a8a77 | 6f2fa6df-4ab9-4b9f-8aa1-724595d71659 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 448806 | 2025-07-27 07:14:59 AEST | 2025-07-27 10:22:50 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
cbe78643-9d28-4905-91c2-141f4016e4ff | 6f2fa6df-4ab9-4b9f-8aa1-724595d71659 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 536199 | 2025-07-27 07:15:03 AEST | 2025-07-27 10:22:50 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b2d77ca2-c55c-44f9-87ee-bed383c24e97 | 3eeb6d62-9e00-44f4-9b6a-0b0e4539bd88 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 633887 | 2025-07-27 07:17:51 AEST | 2025-07-27 14:11:04 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e7936735-238d-49a7-bf47-a9ee6ae26e43 | 3eeb6d62-9e00-44f4-9b6a-0b0e4539bd88 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 627558 | 2025-07-27 07:17:58 AEST | 2025-07-27 14:11:04 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
20d23781-85ee-4873-afa8-39e938e4ecbd | f4b96f10-4ca8-4a14-8c09-4f48d8bb48ac | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 465358 | 2025-07-27 07:15:37 AEST | 2025-07-27 11:02:08 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f3321cd0-5cdd-42a2-b9e4-5d34eae2dea1 | f4b96f10-4ca8-4a14-8c09-4f48d8bb48ac | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 484963 | 2025-07-27 07:15:39 AEST | 2025-07-27 11:02:08 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a3c0cf9b-2f7d-4e33-90d7-6f2aa89de423 | b1c6be0f-a75a-40f7-957a-f8a1d020baac | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 676817 | 2025-07-27 07:18:03 AEST | 2025-07-27 14:12:32 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
5664954b-4216-4c5c-b013-a15635bfe4d0 | b1c6be0f-a75a-40f7-957a-f8a1d020baac | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 616114 | 2025-07-27 07:18:00 AEST | 2025-07-27 14:12:32 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
721a6368-0ee3-4a00-90c9-e7cec9557117 | bb814c00-8560-4524-8b35-cf6807aac3c4 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 666249 | 2025-07-27 07:18:05 AEST | 2025-07-27 14:14:59 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f6a1f104-ef88-46a6-a299-44025eeedcda | bb814c00-8560-4524-8b35-cf6807aac3c4 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 727084 | 2025-07-27 07:18:08 AEST | 2025-07-27 14:14:59 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6556226c-48aa-40f4-9f4c-103a3f8e98b4 | 65c23745-b085-4b2a-a7fb-afff57709387 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 371270 | 2025-07-27 07:15:41 AEST | 2025-07-27 11:05:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0d477d29-b929-4575-a20e-47644980100e | 65c23745-b085-4b2a-a7fb-afff57709387 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 367112 | 2025-07-27 07:15:42 AEST | 2025-07-27 11:05:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a6e0b2e4-db9b-49b2-9d6d-29bbe50390d4 | 217f48ed-f901-40bb-a5df-7768abf351b8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 642342 | 2025-07-27 07:14:51 AEST | 2025-07-27 10:19:28 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1d888be2-04a6-4241-927d-2910d4a99ff0 | 217f48ed-f901-40bb-a5df-7768abf351b8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 703116 | 2025-07-27 07:14:55 AEST | 2025-07-27 10:19:28 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
99063f92-60e7-47e4-976e-094afdc4f4af | 217f48ed-f901-40bb-a5df-7768abf351b8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 641896 | 2025-07-27 07:14:53 AEST | 2025-07-27 10:19:28 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7f5cf3fd-a759-4c42-889a-747c90e9399c | ccecdf3f-5227-420f-891c-4ec6bfa58963 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 688035 | 2025-07-27 07:18:12 AEST | 2025-07-27 14:16:22 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
0a2c5fcf-a01f-4320-ab05-4ef844dc3b4e | ccecdf3f-5227-420f-891c-4ec6bfa58963 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 624573 | 2025-07-27 07:18:10 AEST | 2025-07-27 14:16:22 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
6b872d0d-c1f5-41c3-9180-7db58933c914 | 7f1a03f0-777d-4ed1-af2e-da8af53b2ab5 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 612521 | 2025-07-27 07:14:49 AEST | 2025-07-27 10:12:21 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1c41c3f2-30a9-4f3f-957f-0d80a92909c2 | 7f1a03f0-777d-4ed1-af2e-da8af53b2ab5 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 603053 | 2025-07-27 07:14:45 AEST | 2025-07-27 10:12:21 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
da590e1a-b6fc-48d7-82d9-d6ca09b9638d | 30e83917-3a63-4839-b329-6b9aee33150d | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 620191 | 2025-07-27 07:18:15 AEST | 2025-07-27 14:18:32 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f9857c9d-a198-4b42-a9e2-c4456a13b939 | 30e83917-3a63-4839-b329-6b9aee33150d | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3667 | 118.6278 | POINT (118.6277552 -20.366723099997238) | 564948 | 2025-07-27 07:18:17 AEST | 2025-07-27 14:18:32 AEST | 5.2897 |  |  | 3000 |  |  | -20.3667 | S | 118.6278 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
afc7e22a-3764-4d46-be20-26c6ebc2bfbc | fe693e76-3162-4a19-aeca-956d3f3aa13e | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 581031 | 2025-07-27 07:14:40 AEST | 2025-07-27 10:06:14 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
72973e32-f780-4246-83b9-e54304c71dc6 | fe693e76-3162-4a19-aeca-956d3f3aa13e | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 476079 | 2025-07-27 07:14:42 AEST | 2025-07-27 10:06:14 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7b19c6ee-5672-4301-92aa-15aa8eb84188 | 5ed0e1ff-0b8d-4797-839d-3208ad26e6d9 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 615938 | 2025-07-27 07:14:15 AEST | 2025-07-27 09:55:55 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
231f51af-8a8c-43e2-8b09-22b1b41fe330 | 5ed0e1ff-0b8d-4797-839d-3208ad26e6d9 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 686749 | 2025-07-27 07:14:16 AEST | 2025-07-27 09:55:55 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
f10d8c19-826d-4a92-b774-fc872f1ad25d | 5ed0e1ff-0b8d-4797-839d-3208ad26e6d9 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 619964 | 2025-07-27 07:14:18 AEST | 2025-07-27 09:55:55 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
33794802-4e00-4f25-973d-403bfef0a6af | 5ed0e1ff-0b8d-4797-839d-3208ad26e6d9 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 668549 | 2025-07-27 07:14:20 AEST | 2025-07-27 09:55:55 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
e97294af-a50b-420a-8712-a5aef4725666 | d237f5e8-afd9-4956-9d04-35f5da7da5e8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 554383 | 2025-07-27 07:14:25 AEST | 2025-07-27 09:59:12 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
97b7b63e-ef3a-4f43-b3af-159695897554 | d237f5e8-afd9-4956-9d04-35f5da7da5e8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 494175 | 2025-07-27 07:14:23 AEST | 2025-07-27 09:59:12 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
94d329dc-31b3-46b6-a803-a4a538209f7c | d237f5e8-afd9-4956-9d04-35f5da7da5e8 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 541391 | 2025-07-27 07:14:22 AEST | 2025-07-27 09:59:12 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
160f4acb-3899-4c2f-ad22-61eda55d1b72 | f003acb6-94af-457c-9fda-6c3ac642fa41 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 515430 | 2025-07-27 07:14:37 AEST | 2025-07-27 10:03:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
94e5774b-e438-4817-9948-c5f89bddffc0 | f003acb6-94af-457c-9fda-6c3ac642fa41 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 679660 | 2025-07-27 07:14:39 AEST | 2025-07-27 10:03:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
7fb3401f-6f5d-4126-8fa2-cd9d3be8a483 | f003acb6-94af-457c-9fda-6c3ac642fa41 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 630840 | 2025-07-27 07:14:29 AEST | 2025-07-27 10:03:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
2ab891b7-1fb6-490c-b71a-ae809345d6bc | f003acb6-94af-457c-9fda-6c3ac642fa41 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 582538 | 2025-07-27 07:14:31 AEST | 2025-07-27 10:03:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
c424f3d0-e74f-4269-8526-33385068a11c | f003acb6-94af-457c-9fda-6c3ac642fa41 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 622395 | 2025-07-27 07:14:35 AEST | 2025-07-27 10:03:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 810 | 1080 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
dcd1ef1e-c993-4893-a97e-d9dbe7541c3d | f003acb6-94af-457c-9fda-6c3ac642fa41 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 615522 | 2025-07-27 07:14:27 AEST | 2025-07-27 10:03:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
a9e0ed59-53e5-413d-8b55-e558b20d93d3 | f003acb6-94af-457c-9fda-6c3ac642fa41 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 508284 | 2025-07-27 07:14:33 AEST | 2025-07-27 10:03:39 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
b6306faf-35ca-4a95-84f8-a75854dd65ba | 07542b54-89a3-4927-b6b3-dedf9585949f | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 568935 | 2025-07-27 07:14:12 AEST | 2025-07-27 09:50:19 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
1d57c757-a452-4f99-81ed-7c4abeb5f9a5 | 07542b54-89a3-4927-b6b3-dedf9585949f | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 476101 | 2025-07-27 07:14:11 AEST | 2025-07-27 09:50:19 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F
9548eb65-137f-4204-b8c9-43a267781b76 | 486d3faf-2261-4a46-aa8c-50d11de588e2 | 53caf531-3c9b-4c7c-b7fa-5144a6a794b3 | 1 |  | -20.3179 | 118.5774 | POINT (118.57741159999999 -20.317948100002432) | 517281 | 2025-07-27 07:14:05 AEST | 2025-07-27 09:46:07 AEST | 12.5941 |  |  | 4 |  |  | -20.3179 | S | 118.5774 | E | samsung | SM-G975F |  | 1080 | 810 | Fulcrum Android 2507.1.0 (19222), Android 12, samsung, SM-G975F